Copyright 2003 AIA
MASTERSPEC
12/03

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15145 - DOMESTIC WATER PIPING SPECIALTIES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following domestic water piping specialties:

Adjust list below to suit Project.

1. Vacuum breakers.

2. Backflow preventers.

3. Water pressure-reducing valves.

4. Balancing valves.

5. Temperature-actuated water mixing valves.

6. Strainers.

7. Outlet boxes.

8. Hose stations.

9. Hose bibbs.

10. Wall hydrants.

11. Ground hydrants.

12. Post hydrants.

13. Drain valves.

14. Water hammer arresters.

15. Air vents.

16. Trap-seal primer valves.

17. Trap-seal primer systems.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Meters and Gages" for thermometers, pressure gages, and flow meters in domestic water piping.

2. Division 15 Section "Domestic Water Piping" for water meters.

3. Division 15 Section "Medical Plumbing Fixtures" for thermostatic mixing valves for sitz baths, thermostatic mixing-valve assemblies for hydrotherapy equipment, and outlet boxes for dialysis equipment.

4. Division 15 Section "Emergency Plumbing Fixtures" for water tempering equipment.

5. Division 15 Section "Drinking Fountains and Water Coolers" for water filters for water coolers.

6. Division 15 Section "Water Filtration Equipment" for water filters in domestic water piping.

1.3 PERFORMANCE REQUIREMENTS

Coordinate this Article with Division 15 Section "Domestic Water Piping."

A. Minimum Working Pressure for Domestic Water Piping Specialties:  [125 psig (860 kPa)] <Insert pressure>, unless otherwise indicated.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

Retain paragraph below if retaining Part 2 "Trap-Seal Primer Systems" Article.

B. Shop Drawings:  Diagram power, signal, and control wiring.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

C. Field quality-control test reports.

D. Operation and Maintenance Data:  For domestic water piping specialties to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

Retain first paragraph below if retaining Part 2 "Trap-Seal Primer Systems" Article.

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. NSF Compliance:

1. Comply with NSF 14, "Plastics Piping Components and Related Materials," for plastic domestic water piping components.

2. Comply with NSF 61, "Drinking Water System Components - Health Effects; Sections 1 through 9."

PART 2 -  PRODUCTS

2.1 VACUUM BREAKERS

Copy and edit paragraph and subparagraphs below for each type of pipe-applied, atmospheric-type vacuum breaker required.  If only one type is required, drawing designation may be omitted.

Pipe-applied, atmospheric-type vacuum breakers in paragraph below are for moderate to high hazard and are available in NPS 1/4 to NPS 3 (DN 8 to DN 80).  They are not suitable for continuous pressure or protection from backflow.

A. Pipe-Applied, Atmospheric-Type Vacuum Breakers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Ames Co.

b. Cash Acme.

c. Conbraco Industries, Inc.

d. FEBCO; SPX Valves & Controls.

e. Rain Bird Corporation.

f. Toro Company (The); Irrigation Div.

g. Watts Industries, Inc.; Water Products Div.

h. Zurn Plumbing Products Group; Wilkins Div.

i. <Insert manufacturer's name.>

3. Standard:  ASSE 1001.

4. Size:  NPS 1/4 to NPS 3 (DN 8 to DN 80), as required to match connected piping.

5. Body:  Bronze.

6. Inlet and Outlet Connections:  Threaded.

7. Finish:  [Rough bronze] [Chrome plated].

Copy and edit paragraph and subparagraphs below for each type of hose-connection vacuum breaker required.  If only one type is required, drawing designation may be omitted.

Hose-connection vacuum breakers in paragraph below are for low hazard and are not suitable for continuous pressure.  Outlet size is garden-hose thread.

B. Hose-Connection Vacuum Breakers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Arrowhead Brass Products, Inc.

b. Cash Acme.

c. Conbraco Industries, Inc.

d. Legend Valve.

e. MIFAB, Inc.

f. Prier Products, Inc.

g. Watts Industries, Inc.; Water Products Div.

h. Woodford Manufacturing Company.

i. Zurn Plumbing Products Group; Light Commercial Operation.

j. Zurn Plumbing Products Group; Wilkins Div.

k. <Insert manufacturer's name.>

3. Standard:  ASSE 1011.

4. Body:  Bronze, nonremovable, with manual drain.

5. Outlet Connection:  Garden-hose threaded complying with ASME B1.20.7.

6. Finish:  [Chrome or nickel plated] [Rough bronze].

Copy and edit paragraph and subparagraphs below for each type of pressure vacuum breaker required.  If only one type is required, drawing designation may be omitted.

Pressure vacuum breakers in paragraph below are for moderate to high hazard and are available in NPS 1/2 to NPS 2 (DN 15 to DN 50).

C. Pressure Vacuum Breakers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Toro Company (The); Irrigation Div.

f. Watts Industries, Inc.; Water Products Div.

g. Zurn Plumbing Products Group; Wilkins Div.

h. <Insert manufacturer's name.>

4. Standard:  ASSE 1020.

5. Operation:  Continuous-pressure applications.

6. Pressure Loss:  [5 psig (35 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size:  <Insert NPS (DN).>

8. Design Flow Rate:  <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits:  <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate:  <Insert psig (kPa).>

11. Accessories:

a. Valves:  Ball type, on inlet and outlet.

Copy and edit paragraph and subparagraphs below for each type of laboratory-faucet vacuum breaker required.  If only one type is required, drawing designation may be omitted.

Laboratory-faucet vacuum breakers in paragraph below are for moderate to low hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

D. Laboratory-Faucet Vacuum Breakers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Conbraco Industries, Inc.

b. Watts Industries, Inc.; Water Products Div.

c. Woodford Manufacturing Company.

d. Zurn Plumbing Products Group; Wilkins Div.

e. <Insert manufacturer's name.>

3. Standard:  ASSE 1035.

4. Size:  NPS 1/4 or NPS 3/8 (DN 8 or DN 10) matching faucet size.

5. Body:  Bronze.

6. End Connections:  Threaded.

7. Finish:  Chrome plated.

Copy and edit paragraph and subparagraphs below for each type of spill-resistant vacuum breaker required.  If only one type is required, drawing designation may be omitted.

Spill-resistant vacuum breakers in paragraph below are for high hazard and are available in NPS 1/4 to NPS 1 (DN 8 to DN 25).

E. Spill-Resistant Vacuum Breakers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Conbraco Industries, Inc.

b. Watts Industries, Inc.; Water Products Div.

c. <Insert manufacturer's name.>

3. Standard:  ASSE 1056.

4. Operation:  Continuous-pressure applications.

5. Size:  [NPS 1/4 (DN 8)] [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

6. Accessories:

a. Valves:  Ball type, on inlet and outlet.

2.2 BACKFLOW PREVENTERS

Copy and edit paragraph and subparagraphs below for each type of intermediate atmospheric-vent backflow preventer required.  If only one type is required, drawing designation may be omitted.

Intermediate atmospheric-vent backflow preventers in paragraph below are for moderate hazard and are available in NPS 1/2 and NPS 3/4 (DN 15 and DN 20).

A. Intermediate Atmospheric-Vent Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cash Acme.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Honeywell Water Controls.

e. Legend Valve.

f. Watts Industries, Inc.; Water Products Div.

g. Zurn Plumbing Products Group; Wilkins Div.

h. <Insert manufacturer's name.>

3. Standard:  ASSE 1012.

4. Operation:  Continuous-pressure applications.

5. Size:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)].

6. Body:  Bronze.

7. End Connections:  [Union, solder] [Solder] joint.

8. Finish:  [Chrome plated] [Rough bronze].

Copy and edit paragraph and subparagraphs below for each type of reduced-pressure-principle backflow preventer required.  If only one type is required, drawing designation may be omitted.

Reduced-pressure-principle backflow preventers in paragraph below are for high hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

B. Reduced-Pressure-Principle Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Industries, Inc.; Water Products Div.

f. Zurn Plumbing Products Group; Wilkins Div.

g. <Insert manufacturer's name.>

4. Standard:  ASSE 1013.

5. Operation:  Continuous-pressure applications.

6. Pressure Loss:  [12 psig (83 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size:  <Insert NPS (DN).>

8. Design Flow Rate:  <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits:  <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

11. Body:  Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

12. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

13. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

14. Accessories:

a. Valves:  Ball type with threaded ends on inlet and outlet ofNPS 2 (DN 50) and smaller; outside screw and yoke gate-type with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

b. Air-Gap Fitting:  ASME A112.1.2, matching backflow-preventer connection.

Copy and edit paragraph and subparagraphs below for each type of double-check backflow-prevention assembly required.  If only one type is required, drawing designation may be omitted.

Double-check backflow-prevention assemblies in paragraph below are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

C. Double-Check Backflow-Prevention Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Industries, Inc.; Water Products Div.

f. Zurn Plumbing Products Group; Wilkins Div.

g. <Insert manufacturer's name.>

4. Standard:  ASSE 1015.

5. Operation:  Continuous-pressure applications, unless otherwise indicated.

6. Pressure Loss:  [5 psig (35 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size:  <Insert NPS (DN).>

8. Design Flow Rate:  <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits:  <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

11. Body:  Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

12. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

13. Configuration:  Designed for [horizontal, straight through] <Insert configuration> flow.

14. Accessories:

a. Valves:  Ball type with threaded ends on inlet and outlet ofNPS 2 (DN 50) and smaller; outside screw and yoke gate-type with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

Copy and edit paragraph and subparagraphs below for each type of beverage-dispensing-equipment backflow preventer required.  If only one type is required, drawing designation may be omitted.

Beverage-dispensing-equipment backflow preventers in paragraph below are for moderate hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

D. Beverage-Dispensing-Equipment Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Conbraco Industries, Inc.

b. Watts Industries, Inc.; Water Products Div.

c. Zurn Plumbing Products Group; Wilkins Div.

d. <Insert manufacturer's name.>

3. Standard:  ASSE 1022.

4. Operation:  Continuous-pressure applications.

5. Size:  NPS 1/4 or NPS 3/8 (DN 8 or DN 10).

6. Body:  Stainless steel.

7. End Connections:  Threaded.

Copy and edit paragraph and subparagraphs below for each type of dual-check-valve backflow preventer required.  If only one type is required, drawing designation may be omitted.

Dual-check-valve backflow preventers in paragraph below are for low hazard and are available in NPS 1/2 to NPS 1-1/4 (DN 15 to DN 32).

E. Dual-Check-Valve Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cash Acme.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Ford Meter Box Company, Inc. (The).

f. Honeywell Water Controls.

g. Legend Valve.

h. McDonald, A. Y. Mfg. Co.

i. Mueller Co.; Water Products Div.

j. Watts Industries, Inc.; Water Products Div.

k. Zurn Plumbing Products Group; Wilkins Div.

l. <Insert manufacturer's name.>

3. Standard:  ASSE 1024.

4. Operation:  Continuous-pressure applications.

5. Size:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)].

6. Body:  Bronze with union inlet.

Copy and edit paragraph and subparagraphs below for each type of carbonated-beverage-dispenser, dual-check-valve backflow preventer required.  If only one type is required, drawing designation may be omitted.

Carbonated-beverage-dispenser, dual-check-valve backflow preventers in paragraph below are for moderate hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

F. Carbonated-Beverage-Dispenser, Dual-Check-Valve Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cash Acme.

b. Lancer Corporation.

c. Watts Industries, Inc.; Water Products Div.

d. <Insert manufacturer's name.>

3. Standard:  ASSE 1032.

4. Operation:  Continuous-pressure applications.

5. Size:  NPS 1/4 or NPS 3/8 (DN 8 or DN 10).

6. Body:  Stainless steel.

7. End Connections:  Threaded.

Copy and edit paragraph and subparagraphs below for each type of reduced-pressure-detector, fire-protection backflow-preventer assembly required.  If only one type is required, drawing designation may be omitted.

Reduced-pressure-detector, fire-protection backflow-preventer assemblies in paragraph below are for high hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

G. Reduced-Pressure-Detector, Fire-Protection Backflow-Preventer Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Watts Industries, Inc.; Water Products Div.

e. Zurn Plumbing Products Group; Wilkins Div.

f. <Insert manufacturer's name.>

4. Standard:  ASSE 1047 and FMG approved or UL listed.

5. Operation:  Continuous-pressure applications.

6. Pressure Loss:  [12 psig (83 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size:  <Insert NPS (DN).>

8. Design Flow Rate:  <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits:  <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate:  <Insert psig (kPa).>

11. Body:  [Cast iron with interior lining complying with AWWA C550 or that is FDA approved] [Steel with interior lining complying with AWWA C550 or that is FDA approved] [Stainless steel].

12. End Connections:  Flanged.

13. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

14. Accessories:

a. Valves:  Outside screw and yoke gate-type with flanged ends on inlet and outlet.

b. Air-Gap Fitting:  ASME A112.1.2, matching backflow-preventer connection.

c. Bypass:  With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy and edit paragraph and subparagraphs below for each type of double-check, detector-assembly backflow preventer required.  If only one type is required, drawing designation may be omitted.

Double-check, detector-assembly backflow preventers in paragraph below are for low hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

H. Double-Check, Detector-Assembly Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Watts Industries, Inc.; Water Products Div.

e. Zurn Plumbing Products Group; Wilkins Div.

f. <Insert manufacturer's name.>

4. Standard:  ASSE 1048 and FMG approved or UL listed.

5. Operation:  Continuous-pressure applications.

6. Pressure Loss:  [5 psig (35 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size:  <Insert NPS (DN).>

8. Design Flow Rate:  <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits:  <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate:  <Insert psig (kPa).>

11. Body:  [Cast iron with interior lining complying with AWWA C550 or that is FDA approved] [Steel with interior lining complying with AWWA C550 or that is FDA approved] [Stainless steel].

12. End Connections:  Flanged.

13. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

14. Accessories:

a. Valves:  Outside screw and yoke gate-type with flanged ends on inlet and outlet.

b. Bypass:  With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy and edit paragraph and subparagraphs below for each type of hose-connection backflow preventer required.  If only one type is required, drawing designation may be omitted.

Hose-connection backflow preventers in paragraph below are for high hazard.  Outlet size is garden-hose thread.  Caution:  Availability is limited.

I. Hose-Connection Backflow Preventers <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Conbraco Industries, Inc.

b. Watts Industries, Inc.; Water Products Div.

c. Woodford Manufacturing Company.

d. <Insert manufacturer's name.>

3. Standard:  ASSE 1052.

4. Operation:  Up to 10-foot head of water (30-kPa) back pressure.

5. Inlet Size:  NPS 1/2 or NPS 3/4 (DN 15 or DN 20).

6. Outlet Size:  Garden-hose thread complying with ASME B1.20.7.

7. Capacity:  At least 3-gpm (0.19-L/s) flow.

Copy and edit paragraph and subparagraphs below for each type of backflow-preventer test kit required.  If only one type is required, drawing designation may be omitted.

Backflow-preventer test kits in paragraph below are suitable for pressure vacuum breakers, reduced-pressure-principle backflow preventers, double-check backflow-prevention assemblies, and double-check, detector-assembly backflow preventers.

J. Backflow-Preventer Test Kits <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Conbraco Industries, Inc.

b. FEBCO; SPX Valves & Controls.

c. Flomatic Corporation.

d. Watts Industries, Inc.; Water Products Div.

e. Zurn Plumbing Products Group; Wilkins Div.

f. <Insert manufacturer's name.>

4. Description:  Factory calibrated, with gages, fittings, hoses, and carrying case with test-procedure instructions.

2.3 WATER PRESSURE-REDUCING VALVES

Copy and edit paragraph and subparagraphs below for each type of water regulator required.  If only one type is required, drawing designation may be omitted.

Water regulators in paragraph below are available in NPS 1/2 to NPS 3 (DN 15 to DN 80).

A. Water Regulators <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cash Acme.

b. Conbraco Industries, Inc.

c. Honeywell Water Controls.

d. Watts Industries, Inc.; Water Products Div.

e. Zurn Plumbing Products Group; Wilkins Div.

f. <Insert manufacturer's name.>

3. Standard:  ASSE 1003.

4. Pressure Rating:  Initial working pressure of 150 psig (1035 kPa).

5. Size:  <Insert NPS (DN).>

6. Design Flow Rate:  <Insert gpm (L/s).>

7. Design Inlet Pressure:  <Insert psig (kPa).>

8. Design Outlet Pressure Setting:  <Insert psig (kPa).>

9. Body:  Bronze[ with chrome-plated finish] for NPS 2 (DN 50) and smaller; cast iron[ with interior lining complying with AWWA C550 or that is FDA approved] for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

10. Valves for Booster Heater Water Supply:  Include integral bypass.

11. End Connections:  Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

Copy and edit paragraph and subparagraphs below for each type of water control valve required.  If only one type is required, drawing designation may be omitted.

Water control valves in paragraph below are available in NPS 1-1/4 (DN 32) and larger.

B. Water Control Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. CLA-VAL Automatic Control Valves.

b. Flomatic Corporation.

c. OCV Control Valves.

d. Watts Industries, Inc.; Ames Fluid Control Systems.

e. Watts Industries, Inc.; Watts ACV.

f. Zurn Plumbing Products Group; Wilkins Div.

g. <Insert manufacturer's name.>

4. Description:  Pilot-operation, diaphragm-type, single-seated main water control valve.

5. Pressure Rating:  Initial working pressure of 150 psig (1035 kPa) minimum with AWWA C550 or FDA-approved, interior epoxy coating.  Include small pilot-control valve, restrictor device, specialty fittings, and sensor piping.

6. Main Valve Body:  Cast- or ductile-iron body with AWWA C550 or FDA-approved, interior epoxy coating; or stainless-steel body.

a. Size:  <Insert NPS (DN).>

b. Pattern:  [Angle] [Globe]-valve design.

c. Trim:  Stainless steel.

7. Design Flow:  <Insert gpm (L/s).>

8. Design Inlet Pressure:  <Insert psig (kPa).>

9. Design Outlet Pressure Setting:  <Insert psig (kPa).>

10. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

2.4 BALANCING VALVES

Copy and edit paragraph and subparagraphs below for each type of copper-alloy calibrated balancing valve required.  If only one type is required, drawing designation may be omitted.

A. Copper-Alloy Calibrated Balancing Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

To require a specific valve type (ball, globe, or Y-pattern globe) or a specific material (brass or bronze), verify its availability with manufacturer.

a. Armstrong International, Inc.

b. Flo Fab Inc.

c. ITT Industries; Bell & Gossett Div.

d. NIBCO INC.

e. TAC Americas.

f. Taco, Inc.

g. Watts Industries, Inc.; Water Products Div.

h. <Insert manufacturer's name.>

4. Type:  [Ball] [or] [Y-pattern globe] valve with two readout ports and memory setting indicator.

5. Body:  [Brass] [or] [bronze],

6. Size:  Same as connected piping, but not larger than NPS 2 (DN 50).

7. Accessories:  Meter hoses, fittings, valves, differential pressure meter, and carrying case.

Copy and edit paragraph and subparagraphs below for each type of cast-iron calibrated balancing valve required.  If only one type is required, drawing designation may be omitted.

B. Cast-Iron Calibrated Balancing Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Flo Fab Inc.

c. ITT Industries; Bell & Gossett Div.

d. NIBCO INC.

e. TAC Americas.

f. Watts Industries, Inc.; Water Products Div.

g. <Insert manufacturer's name.>

4. Type:  Adjustable with Y-pattern globe valve, two readout ports, and memory-setting indicator.

5. Size:  Same as connected piping, but not smaller than NPS 2-1/2 (DN 65).

C. Accessories:  Meter hoses, fittings, valves, differential pressure meter, and carrying case.

Copy and edit paragraph and subparagraphs below for each type of memory-stop balancing valve required.  If only one type is required, drawing designation may be omitted.

D. Memory-Stop Balancing Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Conbraco Industries, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Hammond Valve.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Red-White Valve Corp.

i. <Insert manufacturer's name.>

3. Standard:  MSS SP-110 for two-piece, copper-alloy ball valves.

4. Pressure Rating:  400-psig (2760-kPa) minimum CWP.

5. Size:  NPS 2 (DN 50) or smaller.

6. Body:  Copper alloy.

7. Port:  Standard or full port.

8. Ball:  Chrome-plated brass.

9. Seats and Seals:  Replaceable.

10. End Connections:  Solder joint or threaded.

11. Handle:  Vinyl-covered steel with memory-setting device.

2.5 TEMPERATURE-ACTUATED WATER MIXING VALVES

Copy and edit paragraph and subparagraphs below for each type of water-temperature limiting device required.  If only one type is required, drawing designation may be omitted.

Water-temperature limiting devices in paragraph below are not suitable for service as master thermostatic mixing valves.  Devices below are available in NPS 1/2 to NPS 1 (DN 15 to DN 25) and comply with ASSE 1016, ASSE 1017, or both; however, neither standard is adequate for them.  ASSE 1070, "Performance Requirements for Water Temperature Limiting Devices," is under development.

A. Water-Temperature Limiting Devices <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Cash Acme.

c. Conbraco Industries, Inc.

d. Honeywell Water Controls.

e. Legend Valve.

f. Leonard Valve Company.

g. Powers; a Watts Industries Co.

h. Symmons Industries, Inc.

i. Taco, Inc.

j. Watts Industries, Inc.; Water Products Div.

k. Zurn Plumbing Products Group; Wilkins Div.

l. <Insert manufacturer's name.>

4. Standard:  ASSE 1017.

5. Pressure Rating:  125 psig (860 kPa).

6. Type:  Thermostatically controlled water mixing valve.

7. Material:  Bronze body with corrosion-resistant interior components.

8. Connections:  Threaded[ union] inlets and outlet.

9. Accessories:  Check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

10. Tempered-Water Setting:  <Insert deg F (deg C).>

Delete first subparagraph below only if flow rate is indicated on Drawings.

11. Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

12. Valve Finish:  [Chrome plated] [Rough bronze].

Copy and edit paragraph and subparagraphs below for each type of primary, thermostatic, water mixing valve required.  If only one type is required, drawing designation may be omitted.

Primary, thermostatic, water mixing valves in paragraph below are available in NPS 3/4 to NPS 3 and maybe in NPS 4 (DN 20 to DN 80 and maybe in DN 100), but usually are NPS 2 (DN 50) or smaller.

B. Primary, Thermostatic, Water Mixing Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Lawler Manufacturing Company, Inc.

c. Leonard Valve Company.

d. Powers; a Watts Industries Co.

e. Symmons Industries, Inc.

f. <Insert manufacturer's name.>

4. Standard:  ASSE 1017.

5. Pressure Rating:  125 psig (860 kPa).

6. Type:  [Exposed-mounting] [Cabinet-type], thermostatically controlled water mixing valve.

7. Material:  Bronze body with corrosion-resistant interior components.

8. Connections:  Threaded[ union] inlets and outlet.

9. Accessories:  Manual temperature control, check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

10. Valve Pressure Rating:  125 psig (860 kPa) minimum, unless otherwise indicated.

11. Tempered-Water Setting:  <Insert deg F (deg C).>

Delete first subparagraph below only if flow rate is indicated on Drawings.

12. Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

13. Selected Valve Flow Rate at 45-psig (310-kPa) Pressure Drop:  <Insert gpm (L/s).>

14. Pressure Drop at Design Flow Rate:  <Insert psig (kPa).>

15. Valve Finish:  [Chrome plated] [Polished, chrome plated] [Rough bronze].

16. Piping Finish:  [Chrome plated] [Copper].

Retain subparagraph below if cabinet is required.

17. Cabinet:  Factory-fabricated, stainless steel, for [recessed] [surface] mounting and with hinged, stainless-steel door.

Copy and edit paragraph and subparagraphs below for each type of manifold, thermostatic, water-mixing-valve assembly required.  If only one type is required, drawing designation may be omitted.

Several manufacturers of thermostatic mixing valves promote single "high-low" valves to be used instead of manifold valve assemblies in paragraph below.  If single valves are required for high and low systems, specify them in "Primary, Thermostatic, Water Mixing Valves" Paragraph.

C. Manifold, Thermostatic, Water-Mixing-Valve Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Leonard Valve Company.

b. Powers; a Watts Industries Co.

c. Symmons Industries, Inc.

d. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, [cabinet-type] [exposed-mounting], thermostatically controlled, water-mixing-valve assembly in [two] [three]-valve parallel arrangement.

5. Large-Flow Parallel:  Thermostatic water mixing valve and downstream pressure regulator with pressure gages on inlet and outlet.

Retain first subparagraph below for three-valve assemblies.

6. Intermediate-Flow Parallel:  Thermostatic water mixing valve and downstream pressure regulator with pressure gages on inlet and outlet.

7. Small-Flow Parallel:  Thermostatic water mixing valve.

8. Thermostatic Mixing Valves:  Comply with ASSE 1017.  Include check stops on hot- and cold-water inlets and shutoff valve on outlet.

9. Water Regulator(s):  Comply with ASSE 1003.  Include pressure gage on inlet and outlet.

10. Component Pressure Ratings:  125 psig (860 kPa) minimum, unless otherwise indicated.

Retain first subparagraph below for cabinet-type assembly.

11. Cabinet:  Factory-fabricated, stainless steel, for [recessed] [surface] mounting and with hinged, stainless-steel door.

12. Selected Large Flow, Tempered Water Valve Size:  <Insert size.>

13. Tempered-Water Setting:  <Insert deg F (deg C).>

14. Unit Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

15. Unit Minimum Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

16. Selected Unit Flow Rate at 45-psig (310-kPa) Pressure Drop:  <Insert gpm (L/s).>

17. Unit Pressure Drop at Design Flow Rate:  <Insert psig (kPa).>

18. Unit Tempered-Water Outlet Size:  <Insert NPS (DN)> end connection.

19. Unit Hot- and Cold-Water Inlet Size:  <Insert NPS (DN)> end connections.

20. Thermostatic Mixing Valve and Water Regulator Finish:  [Chrome plated] [Polished, chrome plated] [Rough bronze].

21. Piping Finish:  [Chrome plated] [Copper].

Copy and edit paragraph and subparagraphs below for each type of photographic-process, thermostatic, water-mixing-valve assembly required.  If only one type is required, drawing designation may be omitted.

D. Photographic-Process, Thermostatic, Water-Mixing-Valve Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Lawler Manufacturing Company, Inc.

b. Leonard Valve Company.

c. Powers; a Watts Industries Co.

d. Symmons Industries, Inc.

e. <Insert manufacturer's name.>

3. Standard:  ASSE 1017, thermostatically controlled water mixing valve made for precise, process-water temperature control.

4. Pressure Rating:  125 psig (860 kPa) minimum, unless otherwise indicated.

5. Body:  Bronze with corrosion-resistant interior components.

6. Connections:  Threaded inlets and outlet.

7. Accessories:  Manual temperature control, check stops on hot- and cold-water supplies, thermometer, shutoff valve, and adjustable, temperature-control handle.

8. Cabinet:  Factory-fabricated, stainless steel, for surface mounting; with controls and thermometer mounted on front.

9. Tempered-Water Setting:  <Insert deg F (deg C).>

10. Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

11. Tempered-Water Outlet Size:  <Insert NPS (DN)> end connection.

12. Hot- and Cold-Water Inlet Size:  <Insert NPS (DN)> end connections.

Copy and edit paragraph and subparagraphs below for each type of individual-fixture, water tempering valve required.  If only one type is required, drawing designation may be omitted.

Individual-fixture, water tempering valves in paragraph below are not suitable for service as primary water tempering valves.  Valves below are available in NPS 3/4 (DN 20) and larger; however, devices in "Water-Temperature Limiting Devices" Paragraph should be used instead.

E. Individual-Fixture, Water Tempering Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cash Acme.

b. Conbraco Industries, Inc.

c. Honeywell Water Controls.

d. Lawler Manufacturing Company, Inc.

e. Leonard Valve Company.

f. Powers; a Watts Industries Co.

g. Watts Industries, Inc.; Water Products Div.

h. Zurn Plumbing Products Group; Wilkins Div.

i. <Insert manufacturer's name.>

3. Standard:  ASSE 1016, thermostatically controlled water tempering valve.

4. Pressure Rating:  125 psig (860 kPa) minimum, unless otherwise indicated.

5. Body:  Bronze body with corrosion-resistant interior components.

6. Temperature Control:  Adjustable.

7. Inlets and Outlet:  Threaded.

8. Finish:  Rough or chrome-plated bronze.

9. Tempered-Water Setting:  <Insert deg F (deg C).>

Retain subparagraph below only if required.

10. Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

Copy and edit paragraph and subparagraphs below for each type of primary water tempering valve required.  If only one type is required, drawing designation may be omitted.

Primary water tempering valves in paragraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

F. Primary Water Tempering Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Heat-Timer Corporation.

b. Holby Valve Co., Inc.

c. <Insert manufacturer's name.>

3. Standard:  ASSE 1017, thermostatically controlled tempering valve, listed as tempering valve.

4. Pressure Rating:  125 psig (860 kPa) minimum, unless otherwise indicated.

5. Body:  Bronze.

6. Temperature Control:  Manual.

7. Inlets and Outlet:  Threaded.

8. Selected Primary Water Tempering Valve Size:  <Insert size.>

9. Tempered-Water Setting:  <Insert deg F (deg C).>

10. Tempered-Water Design Flow Rate:  <Insert gpm (L/s).>

11. Pressure Drop at Design Flow Rate:  <Insert psig (kPa).>

12. Tempered-Water Outlet Size:  <Insert NPS (DN)> end connection.

13. Cold-Water Inlet Size:  <Insert NPS (DN)> end connection.

14. Hot-Water Inlet Size:  <Insert NPS (DN)> end connection.

15. Valve Finish:  [Rough bronze] <Insert finish>.

2.6 STRAINERS FOR DOMESTIC WATER PIPING

Copy and edit paragraph and subparagraphs below for each type of Y-pattern strainer required.  If only one type is required, drawing designation may be omitted.

A. Y-Pattern Strainers <Insert drawing designation if any>:

1. Pressure Rating:  125 psig (860 kPa) minimum, unless otherwise indicated.

2. Body:  Bronze for NPS 2 (DN 50) and smaller; cast iron[ with interior lining complying with AWWA C550 or FDA-approved, epoxy coating and] for NPS 2-1/2 (DN 65) and larger.

3. End Connections:  Threaded for NPS 2 (DN 50) and smaller;flanged for NPS 2-1/2 (DN 65) and larger.

4. Screen:  Stainless steel with round perforations, unless otherwise indicated.

If retaining more than one screen size, indicate screen size on Drawings.

5. Perforation Size:

a. StrainersNPS 2 (DN 50) and Smaller:  [0.020 inch (0.51 mm)] [0.033 inch (0.84 mm)] [0.062 inch (1.57 mm)] <Insert size>.

b. Strainers NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  [0.045 inch (1.14 mm)] [0.062 inch (1.57 mm)] [0.125 inch (3.18 mm)] <Insert size>.

c. Strainers NPS 5 (DN 125) and Larger:  [0.10 inch (2.54 mm)] [0.125 inch (3.18 mm)] [0.25 inch (6.35 mm)] <Insert size>.

6. Drain:  [Pipe plug] [Factory-installed, hose-end drain valve].

2.7 OUTLET BOXES

Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.

Copy and edit paragraph and subparagraphs below for each type of clothes washer outlet box required.  If only one type is required, drawing designation may be omitted.

A. Clothes Washer Outlet Boxes <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Acorn Engineering Company.

b. Guy Gray Manufacturing Co., Inc.

c. IPS Corporation.

d. LSP Products Group, Inc.

e. Oatey.

f. Plastic Oddities; a division of Diverse Corporate Technologies.

g. Symmons Industries, Inc.

h. Watts Industries, Inc.; Water Products Div.

i. Whitehall Manufacturing; a div. of Acorn Engineering Company.

j. Zurn Plumbing Products Group; Light Commercial Operation.

k. <Insert manufacturer's name.>

3. Mounting:  Recessed.

4. Material and Finish:  [Enameled-steel or epoxy-painted-steel] [Enameled-steel or epoxy-painted-steel or plastic] [Plastic] [Stainless-steel] box and faceplate.

5. Faucet:  Combination, valved fitting or separate hot- and cold-water, valved fittings complying with ASME A112.18.1.  Include garden-hose thread complying with ASME B1.20.7 on outlets.

6. Supply Shutoff Fittings:  NPS 1/2 (DN 15) gate, globe, or ball valves and NPS 1/2 (DN 15) copper, water tubing.

7. Drain:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] standpipe and P-trap for direct waste connection to drainage piping.

Retain one or both subparagraphs below if required.  Hoses are usually included with clothes washers.

8. Inlet Hoses:  Two 60-inch- (1500-mm-) long, rubber household clothes washer inlet hoses with female, garden-hose-thread couplings.  Include rubber washers.

9. Drain Hose:  One 48-inch- (1200-mm-) long, rubber household clothes washer drain hose with hooked end.

Copy and edit paragraph and subparagraphs below for each type of icemaker outlet box required.  If only one type is required, drawing designation may be omitted.

B. Icemaker Outlet Boxes <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Acorn Engineering Company.

b. IPS Corporation.

c. LSP Products Group, Inc.

d. Oatey.

e. Plastic Oddities; a division of Diverse Corporate Technologies.

f. <Insert manufacturer's name.>

3. Mounting:  Recessed.

4. Material and Finish:  [Enameled-steel or epoxy-painted-steel] [Enameled-steel or epoxy-painted-steel or plastic] [Plastic] [Stainless-steel] box and faceplate.

5. Faucet:  Valved fitting complying with ASME A112.18.1.  Include NPS 1/2 (DN 15) or smaller copper tube outlet.

6. Supply Shutoff Fitting:  NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

2.8 HOSE STATIONS

Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.  Revise this Article for required features.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

To require a specific type of hose station, verify its availability with manufacturer.

1. ARCHON Industries, Inc.

2. Armstrong International, Inc.

3. Cooney Brothers, Inc.

4. DynaFluid Ltd.

5. Leonard Valve Company.

6. Strahman Valves, Inc.

7. T & S Brass and Bronze Works, Inc.

8. <Insert manufacturer's name.>

Copy and edit paragraph and subparagraphs below for each type of single-temperature-water hose station required.  If only one type is required, drawing designation may be omitted.

C. Single-Temperature-Water Hose Stations <Insert drawing designation if any>:

1. Standard:  ASME A112.18.1.

2. Cabinet:  Stainless-steel enclosure with exposed valve handle, hose connection, and hose rack.  Include thermometer in front.

3. Hose-Rack Material:  Stainless steel.

4. Body Material:  Bronze[ with stainless-steel wetted parts].

5. Body Finish:  Rough bronze[, chrome plated].

6. Mounting:  [Wall, with reinforcement] [Floor, with stainless-steel pedestal].

7. Supply Fitting:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valve and check valve and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing.  Omit check valve if check stop is included with fitting.

8. Hose:  Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert length> long.

9. Nozzle:  With hand squeeze on-off control.

10. Vacuum Breaker:  Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052; and garden-hose thread complying with ASME B1.20.7 on outlet.

Copy and edit paragraph and subparagraphs below for each type of hot- and cold-water hose station required.  If only one type is required, drawing designation may be omitted.

D. Hot- and Cold-Water Hose Stations <Insert drawing designation if any>:

1. Standard:  ASME A112.18.1.

2. Type Faucet:  [Blending] [Thermostatic mixing] valve.

3. Cabinet:  Stainless-steel enclosure with exposed valve handles, hose connection, and hose rack.  Include thermometer in front.

4. Hose-Rack Material:  Stainless steel.

5. Body Material:  Bronze[ with stainless-steel wetted parts].

6. Body Finish:  Rough bronze[ or chrome plate].

7. Mounting:  [Wall, with reinforcement] [Floor, with stainless-steel pedestal].

8. Supply Fittings:  Two [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valves and check valves and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing.  Omit check valves if check stops are included with fitting.

9. Hose:  Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert length> long.

10. Nozzle:  With hand squeeze on-off control.

11. Vacuum Breaker:  Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052; and garden-hose thread complying with ASME B1.20.7 on outlet.

Copy and edit paragraph and subparagraphs below for each type of cold-water and steam hose station required.  If only one type is required, drawing designation may be omitted.

E. Cold-Water and Steam Hose Stations <Insert drawing designation if any>:

1. Standard:  ASME A112.18.1.

2. Type Faucet:  [Blending] [Thermostatic mixing] valve.

3. Cabinet:  Stainless-steel enclosure with exposed valve handles, hose connection, and hose rack.  Include thermometer in front.

4. Hose-Rack Material:  Stainless steel.

5. Body Material:  Bronze [with stainless-steel wetted parts].

6. Body Finish:  Rough bronze [or chrome plate].

7. Mounting:  [Wall, with reinforcement] [Floor, with stainless-steel pedestal].

8. Supply Fittings:  Two [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valves and check valves and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing.  Omit check valves if check stops are included with fitting.

9. Hose:  Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert length> long.

10. Nozzle:  With hand squeeze on-off control.

11. Vacuum Breaker:  Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052; and garden-hose thread complying with ASME B1.20.7 on outlet.

2.9 HOSE BIBBS

Copy and edit paragraph and subparagraphs below for each type of hose bibb required.  If only one type is required, drawing designation may be omitted.

A. Hose Bibbs <Insert drawing designation if any>:

1. Standard:  ASME A112.18.1 for sediment faucets.

2. Body Material:  Bronze.

3. Seat:  Bronze, replaceable.

4. Supply Connections:  NPS 1/2 or NPS 3/4 (DN 15 or DN 20) threaded or solder-joint inlet.

5. Outlet Connection:  Garden-hose thread complying with ASME B1.20.7.

6. Pressure Rating:  125 psig (860 kPa).

7. Vacuum Breaker:  Integral[ or field-installation,] nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011.

8. Finish for Equipment Rooms:  Rough bronze, or chrome or nickel plated.

9. Finish for Service Areas:  [Rough bronze] [Chrome or nickel plated].

10. Finish for Finished Rooms:  Chrome or nickel plated.

11. Operation for Equipment Rooms:  Wheel handle or operating key.

12. Operation for Service Areas:  [Wheel handle] [Operating key].

13. Operation for Finished Rooms:  [Wheel handle] [Operating key].

14. Include operating key with each operating-key hose bibb.

15. Include[ integral] wall flange with each chrome- or nickel-plated hose bibb.

2.10 WALL HYDRANTS

Wall hydrants without integral vacuum breakers or backflow preventers are available but not recommended.

Copy and edit paragraph and subparagraphs below for each type of nonfreeze wall hydrant required.  If only one type is required, drawing designation may be omitted.

A. Nonfreeze Wall Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company.

b. MIFAB, Inc.

c. Prier Products, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Woodford Manufacturing Company.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

3. Standard:  ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

4. Pressure Rating:  125 psig (860 kPa).

5. Operation:  Loose key.

6. Casing and Operating Rod:  Of length required to match wall thickness.  Include wall clamp.

7. Inlet:  NPS 3/4 or NPS 1 (DN 20 or DN 25).

8. Outlet:  Concealed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

9. Box:  Deep, flush mounting with cover.

10. Box and Cover Finish:  [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain last three subparagraphs above for concealed-outlet-type wall hydrants or first two subparagraphs below for exposed-outlet-type wall hydrants.

11. Outlet:  Exposed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

12. Nozzle and Wall-Plate Finish:  [Polished nickel bronze] [Rough bronze] <Insert finish>.

13. Operating Keys(s):  [One] [Two] with each wall hydrant.

Copy and edit paragraph and subparagraphs below for each type of nonfreeze, hot- and cold-water wall hydrant required.  If only one type is required, drawing designation may be omitted.

B. Nonfreeze, Hot- and Cold-Water Wall Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company.

b. Prier Products, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Woodford Manufacturing Company.

g. Zurn Plumbing Products Group; Specification Drainage Operation.

h. <Insert manufacturer's name.>

3. Standard:  ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

4. Pressure Rating:  125 psig (860 kPa).

5. Operation:  Loose key.

6. Casings and Operating Rods:  Of length required to match wall thickness.  Include wall clamps.

7. Inlets:  NPS 3/4 or NPS 1 (DN 20 or DN 25).

8. Outlet:  Concealed.

9. Box:  Deep, flush mounting with cover.

10. Box and Cover Finish:  [Polished nickel bronze] [Chrome plated] <Insert finish>.

11. Vacuum Breaker:  Nonremovable, manual-drain-type, hose-connection [vacuum breaker complying with ASSE 1011] [or] [backflow preventer complying with ASSE 1052] and with garden-hose thread complying with ASME B1.20.7 on outlet.

12. Operating Keys(s):  [One] [Two] with each wall hydrant.

Copy and edit paragraph and subparagraphs below for each type of moderate-climate wall hydrant required.  If only one type is required, drawing designation may be omitted.

C. Moderate-Climate Wall Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company.

b. MIFAB, Inc.

c. Prier Products, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Woodford Manufacturing Company.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

3. Standard:  ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

4. Pressure Rating:  125 psig (860 kPa).

5. Operation:  Loose key.

6. Inlet:  NPS 3/4 or NPS 1 (DN 20 or DN 25).

7. Outlet:  Concealed, with integral vacuum breaker or nonremovable hose-connection [vacuum breaker complying with ASSE 1011] [or] [backflow preventer complying with ASSE 1052]; and garden-hose thread complying with ASME B1.20.7.

8. Box:  Deep, flush mounting with cover.

9. Box and Cover Finish:  [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain last three subparagraphs above for concealed-outlet-type wall hydrants or first two subparagraphs below for exposed-outlet-type wall hydrants.

10. Outlet:  Exposed, with integral vacuum breaker or nonremovable hose-connection [vacuum breaker complying with ASSE 1011] [or] [backflow preventer complying with ASSE 1052]; and garden-hose thread complying with ASME B1.20.7.

11. Nozzle and Wall-Plate Finish:  [Polished nickel bronze] [Rough bronze] <Insert finish>.

12. Operating Keys(s):  [One] [Two] with each wall hydrant.

Copy and edit paragraph and subparagraphs below for each type of vacuum breaker wall hydrant required.  If only one type is required, drawing designation may be omitted.

D. Vacuum Breaker Wall Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Arrowhead Brass Products, Inc.

b. Mansfield Plumbing Products LLC.

c. McDonald, A. Y. Mfg. Co.

d. Prier Products, Inc.

e. Smith, Jay. R. Mfg. Co.; Division of Smith Industries, Inc.

f. Watts Industries, Inc.; Water Products Div.

g. Woodford Manufacturing Company.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. <Insert manufacturer's name.>

3. Standard:  ASSE 1019, Type A or Type B.

4. Type:  Freeze-resistant, automatic draining with integral air-inlet valve.

Retain only Type B in first subparagraph below if hose will remain attached.

5. Classification:  [Type A, for automatic draining with hose removed or ]Type B, for automatic draining with hose removed or with hose attached and nozzle closed.

6. Pressure Rating:  125 psig (860 kPa).

7. Operation:  [Loose key] [Loose key or wheel handle] [Wheel handle].

8. Casing and Operating Rod:  Of length required to match wall thickness.  Include wall clamp.

9. Inlet:  NPS 1/2 or NPS 3/4 (DN 15 or DN 20).

10. Outlet:  Exposed with garden-hose thread complying with ASME B1.20.7.

2.11 GROUND HYDRANTS

Retain this Article only if ground hydrants are required and are not specified in Division 2 Section "Water Distribution."  Vacuum breakers are ineffective on this type of hydrant.  If ground hydrants are used, a backflow preventer in supply piping is recommended.

Copy and edit paragraph and subparagraphs below for each type of nonfreeze ground hydrant required.  If only one type is required, drawing designation may be omitted.

A. Nonfreeze Ground Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company.

b. MIFAB, Inc.

c. Murdock, Inc.

d. Prier Products, Inc.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Tyler Pipe; Wade Div.

g. Watts Drainage Products Inc.

h. Woodford Manufacturing Company.

i. Zurn Plumbing Products Group; Light Commercial Operation.

j. Zurn Plumbing Products Group; Specification Drainage Operation.

k. <Insert manufacturer's name.>

3. Standard:  ASME A112.21.3M.

4. Type:  Nonfreeze, concealed-outlet ground hydrant with box.

5. Operation:  Loose key.

6. Casing and Operating Rod:  Of at least length required for burial of valve below frost line.

7. Inlet:  NPS 3/4 (DN 20).

8. Outlet:  Garden-hose thread complying with ASME B1.20.7.

9. Drain:  Designed with hole to drain into ground when shut off.

10. Box:  [Standard] [Deep] pattern with cover.

11. Box and Cover Finish:  [Rough] [Polished nickel] <Insert finish> bronze.

12. Operating Key(s):  [One] [Two] with each ground hydrant.

Vacuum breaker in subparagraph below will be ineffectual because of location at ground level.  If required, include a deep box.

13. Vacuum Breaker:  ASSE 1011.

2.12 POST HYDRANTS

Retain this Article only if post hydrants are required and are not specified in Division 2 Section "Water Distribution."

Copy and edit paragraph and subparagraphs below for each type of nonfreeze, draining-type post hydrant required.  If only one type is required, drawing designation may be omitted.

Hydrants in paragraph below are not recommended.  Nonfreeze, nondraining-type post hydrants or freeze-resistant sanitary yard hydrants are preferred.

A. Nonfreeze, Draining-Type Post Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. MIFAB, Inc.

b. Prier Products, Inc.

c. Simmons Manufacturing Co.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Woodford Manufacturing Company.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

3. Standard:  ASME A112.21.3M.

4. Type:  Nonfreeze, exposed-outlet post hydrant.

5. Operation:  Loose key.

6. Casing and Operating Rod:  Of at least length required for burial of valve below frost line.

7. Casing:  Bronze with casing guard.

8. Inlet:  NPS 3/4 (DN 20).

9. Outlet:  Garden-hose thread complying with ASME B1.20.7.

10. Drain:  Designed with hole to drain into ground when shut off.

11. Vacuum Breaker:  Nonremovable, drainable, hose-connection [vacuum breaker complying with ASSE 1011] [or] [backflow preventer complying with ASSE 1052]; and garden-hose thread complying with ASME B1.20.7 on outlet.

12. Operating Key(s):  [One] [Two] with each loose-key-operation wall hydrant.

Copy and edit paragraph and subparagraphs below for each type of nonfreeze, nondraining-type post hydrant required.  If only one type is required, drawing designation may be omitted.

B. Nonfreeze, Nondraining-Type Post Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Murdock, Inc.

b. <Insert manufacturer's name.>

3. Operation:  Lever-piston operating mechanism and nondraining water-storage reservoir, designed without drain

4. Length:  As required for burial of valve below frost line.

5. Inlet:  NPS 1 (DN 25) threaded.

6. Outlet:  [NPS 1 (DN 25) outlet and coupling plug for 1-inch (25-mm) hose] [NPS 1 by NPS 3/4 (DN 25 by DN 20) adapter with nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011; and garden-hose thread complying with ASME B1.20.7 on outlet] [or] [NPS 1 by NPS 3/4 (DN 25 by DN 20) adapter with nonremovable, drainable, hose-connection backflow preventer complying with ASSE 1052; and garden-hose thread complying with ASME B1.20.7 on outlet].

Copy and edit paragraph and subparagraphs below for each type of freeze-resistant sanitary yard hydrant required.  If only one type is required, drawing designation may be omitted.

C. Freeze-Resistant Sanitary Yard Hydrants <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Hoeptner Products.

b. <Insert manufacturer's name.>

3. Standard:  ASSE 1057, Type 5 for nondraining hydrants.

4. Operation:  Wheel handle.

5. Head:  Copper alloy, with pail hook.

6. Inlet:  NPS 3/4-inch (DN 20) threaded inlet and inlet nozzle, galvanized-steel riser, and venturi.

7. Canister:  [Plastic] [Zinc-plated steel] with atmospheric-vent device.

8. Vacuum Breaker:  Removable hose-connection backflow preventer complying with ASSE 1052 with garden-hose thread complying with ASME B1.20.7 on outlet for field installation.

2.13 DRAIN VALVES

Copy and edit paragraph and subparagraphs below for each type of ball-valve-type, hose-end drain valve required.  If only one type is required, drawing designation may be omitted.

A. Ball-Valve-Type, Hose-End Drain Valves <Insert drawing designation if any>:

1. Standard:  MSS SP-110 for standard-port, two-piece ball valves.

2. Pressure Rating:  400-psig (2760-kPa) minimum CWP.

3. Size:  NPS 3/4 (DN 20).

4. Body:  Copper alloy.

5. Ball:  Chrome-plated brass.

6. Seats and Seals:  Replaceable.

7. Handle:  Vinyl-covered steel.

8. Inlet:  Threaded or solder joint.

9. Outlet:  Threaded, short nipple with garden-hose thread complying with ASME B1.20.7 and cap with brass chain.

Copy and edit paragraph and subparagraphs below for each type of gate-valve-type, hose-end drain valve required.  If only one type is required, drawing designation may be omitted.

B. Gate-Valve-Type, Hose-End Drain Valves <Insert drawing designation if any>:

1. Standard:  MSS SP-80 for gate valves.

2. Pressure Rating:  Class 125.

3. Size:  NPS 3/4 (DN 20).

4. Body:  ASTM B 62 bronze.

5. Inlet:  NPS 3/4 (DN 20) threaded or solder joint.

6. Outlet:  Garden-hose thread complying with ASME B1.20.7 and cap with brass chain.

Copy and edit paragraph and subparagraphs below for each type of stop-and-waste drain valve required.  If only one type is required, drawing designation may be omitted.

C. Stop-and-Waste Drain Valves <Insert drawing designation if any>:

1. Standard:  MSS SP-110 for ball valves or MSS SP-80 for gate valves.

2. Pressure Rating:  200-psig (1380-kPa) minimum CWP or Class 125.

3. Size:  NPS 3/4 (DN 20).

4. Body:  Copper alloy or ASTM B 62 bronze.

5. Drain:  NPS 1/8 (DN 6) side outlet with cap.

2.14 WATER HAMMER ARRESTERS

Copy and edit paragraph and subparagraphs below for each type of water hammer arrester required.  If only one type is required, drawing designation may be omitted.

A. Water Hammer Arresters <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

To require a specific type of water hammer arrester, verify its availability with manufacturer.

a. AMTROL, Inc.

b. Josam Company.

c. MIFAB, Inc.

d. PPP Inc.

e. Sioux Chief Manufacturing Company, Inc.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. Tyler Pipe; Wade Div.

h. Watts Drainage Products Inc.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name>.

3. Standard:  ASSE 1010 or PDI-WH 201.

4. Type:  [Metal bellows] [Copper tube with piston].

5. Size:  ASSE 1010, Sizes AA and A through F or PDI-WH 201, Sizes A through F.

2.15 AIR VENTS

Copy and edit paragraph and subparagraphs below for each type of bolted-construction automatic air vent required.  If only one type is required, drawing designation may be omitted.

A. Bolted-Construction Automatic Air Vents <Insert drawing designation if any>:

1. Body:  Bronze.

2. Pressure Rating:  125-psig (860-kPa) minimum pressure rating at 140 deg F (60 deg C).

3. Float:  Replaceable, corrosion-resistant metal.

4. Mechanism and Seat:  Stainless steel.

5. Size:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] minimum inlet.

6. Inlet and Vent Outlet End Connections:  Threaded.

Copy and edit paragraph and subparagraphs below for each type of welded-construction automatic air vent required.  If only one type is required, drawing designation may be omitted.

B. Welded-Construction Automatic Air Vents <Insert drawing designation if any>:

1. Body:  Stainless steel.

2. Pressure Rating:  150-psig (1035-kPa) minimum pressure rating.

3. Float:  Replaceable, corrosion-resistant metal.

4. Mechanism and Seat:  Stainless steel.

5. Size:  NPS 3/8 (DN 10) minimum inlet.

6. Inlet and Vent Outlet End Connections:  Threaded.

2.16 TRAP-SEAL PRIMER VALVES

Copy and edit paragraph and subparagraphs below for each type of supply-type, trap-seal primer valve required.  If only one type is required, drawing designation may be omitted.

A. Supply-Type, Trap-Seal Primer Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. MIFAB, Inc.

b. PPP Inc.

c. Sioux Chief Manufacturing Company, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Watts Industries, Inc.; Water Products Div.

f. <Insert manufacturer.>

3. Standard:  ASSE 1018.

4. Pressure Rating:  125 psig (860 kPa) minimum.

5. Body:  Bronze.

6. Inlet and Outlet Connections:  NPS 1/2 (DN 15) threaded, union, or solder joint.

7. Gravity Drain Outlet Connection:  NPS 1/2 (DN 15) threaded or solder joint.

8. Finish:  Chrome plated, or rough bronze for units used with pipe or tube that is not chrome finished.

Copy and edit paragraph and subparagraphs below for each type of drainage-type, trap-seal primer valve required.  If only one type is required, drawing designation may be omitted.

B. Drainage-Type, Trap-Seal Primer Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

b. <Insert manufacturer.>

3. Standard:  ASSE 1044, lavatory P-trap with NPS 3/8 (DN 10) minimum, trap makeup connection.

4. Size:  NPS 1-1/4 (DN 32) minimum.

5. Material:  Chrome-plated, cast brass.

2.17 TRAP-SEAL PRIMER SYSTEMS

Copy and edit paragraph and subparagraphs below for each type of trap-seal primer system required.  If only one type is required, drawing designation may be omitted.

A. Trap-Seal Primer Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. PPP Inc.

b. <Insert manufacturer.>

4. Standard:  ASSE 1044,

5. Piping:  NPS 3/4, ASTM B 88, Type L (DN 20, ASTM B 88M, Type B); copper, water tubing.

6. Cabinet:  [Recessed] [Surface]-mounting steel box with stainless-steel cover.

7. Electric Controls:  24-hour timer, solenoid valve, and manual switch for 120-V ac power.

8. Vacuum Breaker:  ASSE 1001.

9. Number Outlets:  [Four] [Six] [Eight] <Insert number>.

10. Size Outlets:  [NPS 1/2 (DN 15)] [NPS 5/8 (DN 18)].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Refer to Division 15 Section "Basic Mechanical Materials and Methods" for piping joining materials, joint construction, and basic installation requirements.

Revise remaining paragraphs and subparagraphs in this Article to include specific installation requirements.

B. Install backflow preventers in each water supply to mechanical equipment and systems and to other equipment and water systems that may be sources of contamination.  Comply with authorities having jurisdiction.

1. Locate backflow preventers in same room as connected equipment or system.

2. Install drain for backflow preventers with atmospheric-vent drain connection with air-gap fitting, fixed air-gap fitting, or equivalent positive pipe separation of at least two pipe diameters in drain piping and pipe to floor drain.  Locate air-gap device attached to or under backflow preventer.  Simple air breaks are not acceptable for this application.

3. Do not install bypass piping around backflow preventers.

C. Install water regulators with inlet and outlet shutoff valves[ and bypass with memory-stop balancing valve].  Install pressure gages on inlet and outlet.

D. Install water control valves with inlet and outlet shutoff valves[ and bypass with globe valve].  Install pressure gages on inlet and outlet.

E. Install balancing valves in locations where they can easily be adjusted.

F. Install temperature-actuated water mixing valves with check stops or shutoff valves on inlets and with shutoff valve on outlet.

1. Install thermometers and water regulators if specified.

2. Install cabinet-type units recessed in or surface mounted on wall as specified.

G. Install Y-pattern strainers for water on supply side of each [control valve,] [water pressure-reducing valve,] [solenoid valve,] [and pump].

H. Install outlet boxes recessed in wall.  Install 2-by-4-inch (38-by-89-mm) fire-retardant-treated-wood blocking wall reinforcement between studs.  Fire-retardant-treated-wood blocking is specified in Division 6 Section "Rough Carpentry."

I. Install hose stations with check stops or shutoff valves on inlets and with thermometer on outlet.

1. Install shutoff valve on outlet if specified.

2. Install cabinet-type units recessed in or surface mounted on wall as specified.  Install 2-by-4-inch (38-by-89-mm) fire-retardant-treated-wood blocking wall reinforcement between studs.  Fire-retardant-treated-wood blocking is specified in Division 6 Section "Rough Carpentry."

J. Install ground hydrants with [1 cu. yd. (0.75 cu. m)] <Insert dimension> of crushed gravel around drain hole.  Set ground hydrants with box flush with grade.

K. Install draining-type post hydrants with [1 cu. yd. (0.75 cu. m)] <Insert dimension> of crushed gravel around drain hole.  Set post hydrants in concrete paving or in [1 cu. ft. (0.03 cu. m)] <Insert dimension> of concrete block at grade.

L. Install nonfreeze, nondraining-type post hydrants set in concrete or pavement.

M. Install freeze-resistant yard hydrants with riser pipe set in concrete or pavement.  Do not encase canister in concrete.

Water hammer arresters in first paragraph below are best shown on water risers and details.  Specifying number, size, and location here is difficult.

N. Install water hammer arresters in water piping according to PDI-WH 201.

O. Install air vents at high points of water piping.[ Install drain piping and discharge onto floor drain.]

P. Install supply-type, trap-seal primer valves with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting.  Adjust valve for proper flow.

Q. Install drainage-type, trap-seal primer valves as lavatory trap with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting.

R. Install trap-seal primer systems with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting.  Adjust system for proper flow.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping and specialties.

Retain both paragraphs below if retaining Part 2 "Trap-Seal Primer Systems" Article.

B. Ground equipment according to Division 16 Section "Grounding and Bonding."

C. Connect wiring according to Division 16 Section "Conductors and Cables."

3.3 LABELING AND IDENTIFYING

A. Equipment Nameplates and Signs:  Install engraved plastic-laminate equipment nameplate or sign on or near each of the following:

Coordinate list below with products retained in Part 2.

1. Pressure vacuum breakers.

2. Intermediate atmospheric-vent backflow preventers.

3. Reduced-pressure-principle backflow preventers.

4. Double-check backflow-prevention assemblies.

5. Carbonated-beverage-machine backflow preventers.

6. Dual-check-valve backflow preventers.

7. Reduced-pressure-detector, fire-protection backflow-preventer assemblies.

8. Double-check, detector-assembly backflow preventers.

9. Water pressure-reducing valves.

10. Calibrated balancing valves.

11. Primary, thermostatic, water mixing valves.

12. Manifold, thermostatic, water-mixing-valve assemblies.

13. Photographic-process, thermostatic, water-mixing-valve assemblies.

14. Primary water tempering valves.

15. Outlet boxes.

16. Hose stations.

17. Supply-type, trap-seal primer valves.

18. Trap-seal primer systems.

B. Distinguish among multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations, in addition to identifying unit.  Nameplates and signs are specified in Division 15 Section "Mechanical Identification."

3.4 FIELD QUALITY CONTROL

A. Perform the following tests and prepare test reports:

1. Test each [pressure vacuum breaker] [reduced-pressure-principle backflow preventer] [double-check backflow-prevention assembly] [and] [double-check, detector-assembly backflow preventer] <Insert type> according to authorities having jurisdiction and the device's reference standard.

B. Remove and replace malfunctioning domestic water piping specialties and retest as specified above.

3.5 ADJUSTING

A. Set field-adjustable pressure set points of water pressure-reducing valves.

B. Set field-adjustable flow set points of balancing valves.

C. Set field-adjustable temperature set points of temperature-actuated water mixing valves.

END OF SECTION 15145

DOMESTIC WATER PIPING SPECIALTIES
15145 - 1

