Copyright 2005 AIA
MASTERSPEC Full Length
03/05 (R 03/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15192 - FACILITY FUEL-OIL PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [fuel-oil] [fuel-oil and diesel-fuel-oil] [diesel-fuel-oil] distribution systems and the following:

1. Pipes, tubes, and fittings.

2. Piping and tubing joining materials.

3. Piping specialties.

4. Valves.

5. Vertical, steel, fuel-oil ASTs.

6. Horizontal, steel, fuel-oil ASTs.

7. Containment-dike, steel, fuel-oil ASTs.

8. Insulated, steel, fuel-oil ASTs.

9. Concrete-vaulted, steel, fuel-oil ASTs.

10. Steel, fuel-oil USTs with STI-P3.

11. Composite, steel, fuel-oil USTs.

12. Jacketed, steel, fuel-oil USTs.

13. FRP fuel-oil USTs.

14. Fuel-oil AST accessories.

15. Fuel-oil UST accessories.

16. Fuel-oil storage tank piping specialties.

17. Fuel-oil storage tank pumps.

18. Fuel-transfer pumps.

19. Fuel maintenance system.

20. Liquid-level gage system.

21. Leak-detection and monitoring system.

22. Mechanical sleeve seals.

23. Grout.

24. Concrete bases.

1.3 DEFINITIONS

Retain definitions remaining after this Section has been edited.

A. AST:  Aboveground storage tank.

B. Exposed, Interior Installations:  Exposed to view indoors.  Examples include finished occupied spaces and mechanical equipment rooms.

C. Exposed, Exterior Installations:  Exposed to view outdoors or subject to outdoor ambient temperatures and weather conditions.  Examples include rooftop locations.

D. Finished Spaces:  Spaces other than mechanical and electrical equipment rooms, furred spaces, pipe and duct shafts, unheated spaces immediately below roof, spaces above ceilings, unexcavated spaces, crawlspaces, and tunnels.

Abbreviation in first paragraph below is generic name for "Viton."

E. FPM:  Vinylidene fluoride-hexafluoropropylene copolymer rubber.

F. FRP:  Glass-fiber-reinforced plastic.

G. UST:  Underground storage tank.

1.4 PERFORMANCE REQUIREMENTS

A. Maximum Operating-Pressure Ratings:  3-psig (21-kPa) fuel-oil supply pressure at oil-fired appliances.

Retain first paragraph below if Contractor is required to assume responsibility for design.

B. Delegated Design:  Design restraint and anchors for fuel-oil piping, ASTs, and equipment, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  Factory-installed support attachments for AST shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include construction details, material descriptions, and dimensions of individual components and profiles.  Also include, where applicable, rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

1. Piping specialties.

2. Valves:  Include pressure rating, capacity, settings, and electrical connection data of selected models.

3. Each type and size of fuel-oil storage tank.  Indicate dimensions, weights, loads, components, and location and size of each field connection.

4. Fuel-oil storage tank accessories.

5. Fuel-oil storage tank piping specialties.

6. Fuel-oil storage tank pumps.

7. Fuel-oil transfer pumps.

8. Fuel maintenance system.

9. Liquid-level gage system.

10. Leak-detection and monitoring system.

B. Shop Drawings:  For facility fuel-oil piping layout.  Include plans, piping layout and elevations, sections, and details for fabrication of pipe anchors, hangers, supports for multiple pipes, alignment guides, expansion joints and loops, and attachments of the same to building structure.  Detail location of anchors, alignment guides, and expansion joints and loops.

1. Shop Drawing Scale:  [1/4 inch per foot (1:50)] <Insert scale>.

2. For fuel-oil storage tanks and pumps, include details of supports and anchors.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

C. Delegated-Design Submittal:  For fuel-oil piping and equipment indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of anchors and seismic restraints.

2. Design Calculations:  Calculate requirements for selecting seismic restraints.

3. Detail fabrication and assembly of pipe anchors, hangers, supports for multiple pipes, and attachments of the same to building structure.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Plans and details, drawn to scale, on which fuel-oil piping is shown and coordinated with other installations, using input from installers of the items involved.

E. Site Survey:  Plans, drawn to scale, on which fuel-oil piping and tanks are shown and coordinated with other services and utilities.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" for delegated design.

F. Qualification Data:  For qualified professional engineer.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Sections specifying supports and seismic controls.  See SEI/ASCE 7 for certification requirements for equipment and components.

G. Seismic Qualification Certificates:  For ASTs, accessories, and components, from manufacturer.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if retaining procedures for brazing certification in "Quality Assurance" Article.

H. Brazing certificates.

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

I. Welding certificates.

J. Field quality-control reports.

K. Operation and Maintenance Data:  For fuel-oil equipment and accessories to include in emergency, operation, and maintenance manuals.

L. Warranty:  Sample of special warranty.

1.6 QUALITY ASSURANCE

Retain "Brazing certificates" Paragraph in "Submittals" Article if retaining first paragraph below.

A. Brazing:  Qualify processes and operators according to ASME Boiler and Pressure Vessel Code:  Section IX.

Retain one or both of first two paragraphs below for welding supports.  Retain first paragraph for welded piping supports; retain second for welded steel pipe joints.  Also retain "Welding certificates" Paragraph in "Submittals" Article.

B. Steel Support Welding Qualifications:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

C. Pipe Welding Qualifications:  Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

E. Comply with ASME B31.9, "Building Services Piping," for fuel-oil piping materials, installation, testing, and inspecting.

F. Comply with requirements of the EPA and of state and local authorities having jurisdiction.  Include recording of fuel-oil storage tanks and monitoring of tanks and piping.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Lift and support fuel-oil storage tanks only at designated lifting or supporting points, as shown on Shop Drawings.  Do not move or lift tanks unless empty.

B. Deliver pipes and tubes with factory-applied end caps.  Maintain end caps through shipping, storage, and handling to prevent pipe end damage and to prevent entrance of dirt, debris, and moisture.

C. Store pipes and tubes with protective PE coating to avoid damaging the coating and to protect from direct sunlight.

D. Store PE pipes and valves protected from direct sunlight.

1.8 PROJECT CONDITIONS

Retain this article if interruption of existing fuel-oil service is required.

A. Interruption of Existing Fuel-Oil Service:  Do not interrupt fuel-oil service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary fuel-oil supply according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of fuel-oil service.

2. Do not proceed with interruption of fuel-oil service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.9 COORDINATION

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

1.10 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of fuel-oil storage tanks and flexible, double-containment piping and related equipment that fail in materials or workmanship within specified warranty period.

1. Storage Tanks:

a. Failures include, but are not limited to, the following when used for storage of fuel oil at temperatures not exceeding [150 deg F (66 deg C)] <Insert temperature>:

1) Structural failures including cracking, breakup, and collapse.

Retain first subparagraph below for steel tanks.

2) Corrosion failure including external and internal corrosion of steel tanks.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

b. Warranty Period:  [30] <Insert number> years from date of Substantial Completion.

2. Flexible, Double-Containment Piping and Related Equipment:

a. Failures due to defective materials or workmanship for materials installed together, including piping, dispenser sumps, entry boots, and sump mounting adapters.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

b. Warranty Period:  [10] [30] <Insert number> years from date of Substantial Completion.

1.11 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Drive Belt:  [One] <Insert number> for each belt-driven pump.

PART 2 -  PRODUCTS

2.1 PIPES, TUBES, AND FITTINGS

This article includes examples of materials listed in NFPA 30, "Flammable and Combustible Liquids Code."  Coordinate piping materials in this article with piping schedules in Part 3.  See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

A. See Part 3 piping schedule articles for where pipes, tubes, fittings, and joining materials are applied in various services.

B. Steel Pipe:  ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

1. Malleable-Iron Threaded Fittings:  ASME B16.3, Class 150, standard pattern.

2. Wrought-Steel Welding Fittings:  ASTM A 234/A 234M, for butt and socket welding.

3. Unions:  ASME B16.39, Class 150, malleable iron with brass-to-iron seat, ground joint, and threaded ends.

4. Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, minimum Class 150, including bolts, nuts, and gaskets of the following material group, end connections, and facings:

a. Material Group:  1.1.

b. End Connections:  Threaded or butt welding to match pipe.

c. Lapped Face:  Not permitted underground.

d. Gasket Materials:  Asbestos free, ASME B16.20 metallic, or ASME B16.21 nonmetallic, gaskets compatible with fuel oil.

e. Bolts and Nuts:  ASME B18.2.1, cadmium-plated steel.

Retain subparagraph below for underground steel pipe.  Cathodic protection may be required in addition to protective coating.  Coordinate with requirements in Division 13 Section "Cathodic Protection."

5. Protective Coating for Underground Piping:  Factory-applied, three-layer coating of epoxy, adhesive, and PE.

a. Joint Cover Kits:  Epoxy paint, adhesive, and heat-shrink PE sleeves.

C. Drawn-Temper Copper Tube:  Comply with [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)].

1. Copper Fittings:  ASME B16.22, wrought copper, streamlined pattern.

2. Bronze Flanges and Flanged Fittings:  ASME B16.24, Class 150.

a. Gasket Material:  Asbestos free, ASME B16.20, metallic, or ASME B16.21 nonmetallic, gaskets compatible with fuel oil.

b. Bolts and Nuts:  ASME B18.2.1, cadmium-plated steel.

D. Annealed-Temper Copper Tube:  Comply with [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)].

1. Copper Fittings:  ASME B16.22, wrought copper, streamlined pattern.

Verify acceptability of fittings in subparagraph below with authorities having jurisdiction before retaining.

2. Flare Fittings:  Comply with ASME B16.26 and SAE J513.

a. Copper fittings with long nuts.

b. Metal-to-metal compression seal without gasket.

c. Dryseal threads complying with ASME B1.20.3.

2.2 DOUBLE-CONTAINMENT PIPE AND FITTINGS

A. Flexible, Double-Containment Piping:  Comply with UL 971.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Environ Products, Inc.

b. OPW.

c. <Insert manufacturer's name>.

2. Pipe Materials:  PVDF complying with ASTM D 3222 for carrier pipe with mechanical couplings to seal carrier, and PE pipe complying with ASTM D 4976 for containment piping.

3. [Fiberglass] [PE] sumps.

4. Watertight sump entry boots, pipe adapters with test ports and tubes, coaxial fittings, and couplings.

5. Minimum Operating Pressure Rating:  10 psig (69 kPa).

6. Plastic to Steel Pipe Transition Fittings:  Factory-fabricated fittings with plastic end matching or compatible with carrier piping, and steel pipe end complying with ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

Retain subparagraph below if double-containment piping will have cable leak-detection system installed in annular space.

7. Include design and fabrication of double-containment pipe and fitting assemblies with provision for field installation of cable leak-detection system in annular space between carrier and containment piping.

B. Rigid, Double-Containment Piping:  Comply with UL 971.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Ameron International; Fiberglass Pipe Group.

b. Conley Corporation.

c. Perma-Pipe, Inc.

d. Smith Fibercast.

e. <Insert manufacturer's name>.

2. RTRP:  ASTM D 2996 or ASTM D 2997 carrier and containment piping and mechanical couplings to seal carrier and containment piping or individually bonded joints.

a. Minimum Operating-Pressure Rating for RTRP NPS 2 and NPS 3 (DN 50 and DN 80):  150 psig (1035 kPa).

b. Minimum Operating-Pressure Rating for RTRP NPS 4 and NPS 6 (DN 100 and DN 150):  125 psig (860 kPa).  Compliance with UL 971 is not required for NPS 6 (DN 150) and larger piping.

c. Fittings:  RTRF complying with ASTM D 2996 or ASTM D 2997, and made by RTRP manufacturer; watertight sump entry boots, termination, or other end fittings.

Retain subparagraph below if double-containment piping will have cable leak-detection system installed in annular space.

3. Include design and fabrication of double-containment pipe and fitting assemblies with provision for field installation of cable leak-detection system in annular space between carrier and containment piping.

2.3 PIPING SPECIALTIES

A. Flexible Connectors:  Comply with UL 567.

1. Metallic Connectors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) American Flexible Hose Co., Inc.

2) Flexicraft Industries.

3) FLEX-ING, Inc.

4) Hose Master, Inc.

5) Metraflex Company (The).

6) Proco Products, Inc.

7) Tru-Flex Metal Hose Corp.

8) Unaflex.

9) <Insert manufacturer's name>.

Flexible connectors in first subparagraph below are listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction, but there is no UL-applicable standard.

b. Listed and labeled for aboveground and underground applications by an NRTL acceptable to authorities having jurisdiction.

c. Stainless-steel bellows with woven, flexible, bronze or stainless-steel, wire-reinforcing protective jacket.

d. Minimum Operating Pressure:  150 psig (1035 kPa).

e. End Connections:  Socket, flanged, or threaded end to match connected piping.

f. Maximum Length:  30 inches (762 mm).

Items in first two subparagraphs below are optional features.

g. Swivel end, 50-psig (345-kPa) maximum operating pressure.

h. Factory-furnished anode.

2. Nonmetallic Connectors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) American Flexible Hose Co., Inc.

2) Flexicraft Industries.

3) FLEX-ING, Inc.

4) Hose Master, Inc.

5) Metraflex Company (The).

6) Tru-Flex Metal Hose Corp.

7) <Insert manufacturer's name>.

b. Listed and labeled for underground applications by an NRTL acceptable to authorities having jurisdiction.

c. PFTE bellows with woven, flexible, bronze or stainless-steel, wire-reinforcing protective jacket.

d. Minimum Operating Pressure:  150 psig (1035 kPa).

e. End Connections:  Socket, flanged, or threaded end to match connected piping.

f. Maximum Length:  30 inches (762 mm).

Items in two subparagraphs below are optional features.

g. Swivel end, 50-psig (345-kPa) maximum operating pressure.

h. Factory-furnished anode.

Retain one or more of first three paragraphs below.  If retaining more than one type of strainer, indicate location of each type on Drawings.

B. Y-Pattern Strainers:

1. Body:  ASTM A 126, Class B, cast iron with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for NPS 2 (DN 50) and smaller; flanged ends for NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  [60] [80]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating:  125 psig (860 kPa).

C. Basket Strainers:

1. Body:  ASTM A 126, Class B, high-tensile cast iron with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for NPS 2 (DN 50) and smaller; flanged ends for NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  [60] [80]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating:  125 psig (860 kPa).

D. T-Pattern Strainers:

1. Body:  Ductile or malleable iron with removable access coupling and end cap for strainer maintenance.

2. End Connections:  Grooved ends.

3. Strainer Screen:  [60] [80]-mesh startup strainer, and perforated stainless-steel basket with 57 percent free area.

4. CWP Rating:  750 psig (5170 kPa).

E. Manual Air Vents:

1. Body:  Bronze.

2. Internal Parts:  Nonferrous.

3. Operator:  Screwdriver or thumbscrew.

4. Inlet Connection:  NPS 1/2 (DN 15).

5. Discharge Connection:  NPS 1/8 (DN 6).

6. CWP Rating:  150 psig (1035 kPa).

7. Maximum Operating Temperature:  225 deg F (107 deg C).

2.4 JOINING MATERIALS

A. Joint Compound and Tape:  Suitable for fuel oil.

B. Welding Filler Metals:  Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

C. Brazing Filler Metals:  Alloy with melting point greater than 1000 deg F (540 deg C) complying with AWS A5.8/A5.8M.  Brazing alloys containing more than 0.05 percent phosphorus are prohibited.

D. Bonding Adhesive for Fiberglass Piping:  As recommended by fiberglass piping manufacturer.

2.5 MANUAL FUEL-OIL SHUTOFF VALVES

Coordinate valve materials in this article with the valve schedule in Part 3.  See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

Shutoff valves for fuel-oil service must comply with one or more standards.  Revise this article if compliance with specific standards apply.  If locking devices are required, verify that they are available from listed manufacturers.

A. See valve schedule in Part 3 for where each valve type is applied in various services.

B. General Requirements for Metallic Valves, NPS 2 (DN 50) and Smaller for Liquid Service:  Comply with UL 842.

1. CWP Rating:  [125 psig (860 kPa)] <Insert pressure>.

2. Threaded Ends:  Comply with ASME B1.20.1.

3. Dryseal Threads on Flare Ends:  Comply with ASME B1.20.3.

4. Tamperproof Feature:  Locking feature for valves indicated in the valve schedule.

5. Service Mark:  Initials "WOG" shall be permanently marked on valve body.

C. General Requirements for Metallic Valves, NPS 2-1/2 (DN 65) and Larger:  Comply with UL 842.

1. CWP Rating:  [125 psig (860 kPa)] <Insert pressure>.

2. Flanged Ends:  Comply with ASME B16.5 for steel flanges.

3. Tamperproof Feature:  Locking feature for valves indicated in the valve schedule.

4. Service Mark:  Initials "WOG" shall be permanently marked on valve body.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves have a reduced port but one fewer leak path.

D. One-Piece, Bronze Ball Valve with Bronze Trim:  MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body:  Bronze, complying with ASTM B 584.

3. Ball:  Chrome-plated brass.

4. Stem:  Bronze; blowout proof.

5. Seats:  Reinforced TFE; blowout proof.

6. Packing:  Separate packnut with adjustable-stem packing threaded ends.

7. Ends:  Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating:  600 psig (4140 kPa).

9. Service Mark:  Initials "WOG" shall be permanently marked on valve body.

Where pressure drop is a concern, use full-port ball valves.  For corrosive or high-temperature applications, use stainless-steel trim ball valves.

E. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:  MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body:  Bronze, complying with ASTM B 584.

3. Ball:  Chrome-plated bronze.

4. Stem:  Bronze; blowout proof.

5. Seats:  Reinforced TFE; blowout proof.

6. Packing:  Threaded-body packnut design with adjustable-stem packing.

7. Ends:  Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating:  600 psig (4140 kPa).

9. Service Mark:  Initials "WOG" shall be permanently marked on valve body.

F. Two-Piece, Regular-Port Bronze Ball Valves with Bronze Trim:  MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body:  Bronze, complying with ASTM B 584.

3. Ball:  Chrome-plated bronze.

4. Stem:  Bronze; blowout proof.

5. Seats:  Reinforced TFE.

6. Packing:  Threaded-body packnut design with adjustable-stem packing.

7. Ends:  Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating:  600 psig (4140 kPa).

9. Service Mark:  Initials "WOG" shall be permanently marked on valve body.

2.6 SPECIALTY VALVES

A. Pressure Relief Valves:  Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anderson Greenwood; Division of Tyco Flow Control.

b. Fulflo Specialties, Inc.

c. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

d. <Insert manufacturer's name>.

2. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

3. Body:  Brass, bronze, or cast steel.

4. Springs:  Stainless steel, interchangeable.

5. Seat and Seal:  Nitrile rubber.

6. Orifice:  Stainless steel, interchangeable.

7. Factory-Applied Finish:  Baked enamel.

8. Maximum Inlet Pressure:  [150 psig (1035 kPa)] <Insert pressure>.

9. Relief Pressure Setting:  [60 psig (414 kPa)] <Insert pressure>.

B. Oil Safety Valves:  Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anderson Greenwood; Division of Tyco Flow Control.

b. Suntec Industries Incorporated.

c. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

d. <Insert manufacturer's name>.

2. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

3. Body:  Brass, bronze, or cast steel.

4. Springs:  Stainless steel.

5. Seat and Diaphragm:  Nitrile rubber.

6. Orifice:  Stainless steel, interchangeable.

7. Factory-Applied Finish:  Baked enamel.

8. Manual override port.

9. Maximum Inlet Pressure:  [60 psig (414 kPa)] <Insert pressure>.

10. Maximum Outlet Pressure:  [3 psig (21 kPa)] <Insert pressure>.

Retain first paragraph below for piping terminations under fuel dispenser that will close in case of mechanical damage or fire.

C. Emergency Shutoff Valves:  Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Ameron International; Fiberglass Pipe Group.

b. Conley Corporation.

c. EMCO Wheaton; a Gardner Denver Company.

d. Environ Products, Inc.

e. OPW.

f. <Insert manufacturer's name>.

2. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

3. [Single] [Double] poppet valve.

4. Body:  ASTM A 126, cast iron.

5. Disk:  FPM.

6. Poppet Spring:  Stainless steel.

7. Stem:  Plated brass.

8. O-Ring:  FPM.

9. Packing Nut:  PTFE-coated brass.

10. Fusible link to close valve at 165 deg F (74 deg C).

11. Thermal relief to vent line pressure buildup due to fire.

12. Air test port.

13. Maximum Operating Pressure:  0.5 psig (3.45 kPa).

Retain paragraph below for diesel-fuel-oil dispenser piping.

D. Mechanical Leak Detector:  Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. FE Petro, Inc.

b. Red Jacket Pumps; a division of Veeder-Root.

c. <Insert manufacturer's name>.

3. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

4. Body:  ASTM A 126, cast iron.

5. O-Rings:  Elastomeric compatible with fuel oil.

6. Piston and Stem Seals:  PTFE.

7. Stem and Spring:  Stainless steel.

8. Piston Cylinder:  Burnished brass.

9. Indicated Leak Rate:  Maximum 3 gph (3 mL/s) at 10 psig (69 kPa).

10. Leak Indication:  Reduced flow.

2.7 VERTICAL, STEEL, FUEL-OIL AST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Adamson Global Technology Corporation.

3. Brown Tank.

4. Buffalo Tank Company, Inc.

5. Cardinal Tank Corp.

6. Clawson Tank Company.

7. Containment Solutions, Inc.

8. Hall Tank Co.

9. Highland Tank & Manufacturing Company, Inc.

10. Modern Welding Company, Inc.

11. Palmer Manufacturing & Tank Inc.

12. Steel Tank & Fabricating Co., Inc.

13. Watco Tanks, Inc.

14. We-Mac Manufacturing, Inc.

15. <Insert manufacturer's name>.

Retain one of first two paragraphs below.  Double-wall tanks are recommended.

C. Description:  UL 142, single-wall, vertical, steel tank.

D. Description:  UL 142[ and STI F921], double-wall, vertical, steel tank; with primary- and secondary-containment walls and interstitial space.

E. Construction:  Fabricated with welded, carbon steel suitable for operation at atmospheric pressure and for storing fuel oil with specific gravity up to 1.1 and maintained temperature up to 150 deg F (66 deg C).

If Project has more than one type or configuration of vertical, steel, fuel-oil AST, delete paragraph below and schedule tanks on Drawings.

F. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.8 HORIZONTAL, STEEL, FUEL-OIL AST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Adamson Global Technology Corporation.

3. Brown Tank.

4. Buffalo Tank Company, Inc.

5. Cardinal Tank Corp.

6. Clawson Tank Company.

7. Containment Solutions, Inc.

8. Hall Tank Co.

9. Highland Tank & Manufacturing Company, Inc.

10. Modern Welding Company, Inc.

11. Palmer Manufacturing & Tank Inc.

12. Safe-T-Tank Corp.

13. Steel Tank & Fabricating Co., Inc.

14. Watco Tanks, Inc.

15. We-Mac Manufacturing, Inc.

16. <Insert manufacturer's name>.

Retain one of first two paragraphs below.  Double-wall tanks are recommended.

C. Description:  UL 142, single-wall, horizontal, steel tank.

D. Description:  UL 142[ and STI F921], double-wall, horizontal, steel tank; with primary- and secondary-containment walls and interstitial space.

E. Construction:  Fabricated with welded, carbon steel; suitable for operation at atmospheric pressure and for storing fuel oil with specific gravity up to 1.1 and with maintained temperature up to 150 deg F (66 deg C).

Retain one of first two paragraphs below.

F. Supports:  Manufacturer's standard structural steel welded to tank.

G. Supports:  Manufacturer's standard type[ and number], steel or cast-iron cradles, for field installation.

1. Number of Supports:  <Insert number>.

Concrete or steel supports for off-the-ground mounting must be specified or detailed on Drawings.

If Project has more than one type or configuration of horizontal, steel, fuel-oil AST, delete paragraph below and schedule tanks on Drawings.

H. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.9 CONTAINMENT-DIKE, STEEL, FUEL-OIL AST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Areo Power Unitized Fueler Inc.

2. Buffalo Tank Company, Inc.

3. Cardinal Tank Corp.

4. Clawson Tank Company.

5. Containment Solutions, Inc.

6. Hall Tank Co.

7. Highland Tank & Manufacturing Company, Inc.

8. Modern Welding Company, Inc.

9. Palmer Manufacturing & Tank Inc.

10. Safe-T-Tank Corp.

11. Watco Tanks, Inc.

12. We-Mac Manufacturing, Inc.

13. <Insert manufacturer's name>.

C. Description:  UL 142 and STI F911, single-wall, horizontal, steel tank; with [open or enclosed] [enclosed], secondary-containment dike with capacity greater than tank capacity.

D. Construction:  Fabricated with welded, carbon steel; suitable for operation at atmospheric pressure and for storing fuel oil with specific gravity up to 1.1 and with maintained temperature up to 150 deg F (66 deg C).

If Project has more than one type or configuration of containment-dike, steel, fuel-oil AST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.10 INSULATED, STEEL, FUEL-OIL AST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Adamson Global Technology Corporation.

3. Areo Power Unitized Fueler Inc.

4. Brown Tank.

5. Containment Solutions, Inc.

6. ConVault, Inc.

7. Hamilton Tanks.

8. Highland Tank & Manufacturing Company, Inc.

9. Modern Welding Company, Inc.

10. Palmer Manufacturing & Tank Inc.

11. Steel Tank & Fabricating Co., Inc.

12. We-Mac Manufacturing, Inc.

13. <Insert manufacturer's name>.

C. Description:  [UL 142 and UL 2085] [UL 142, UL 2085, and STI F941], thermally insulated and fire-resistant, double-wall, horizontal, steel tank; with primary- and secondary-containment walls and insulation and with interstitial space.

D. Construction:  Fabricated with welded, carbon steel and insulation; suitable for operation at atmospheric pressure and for storing fuel oil with specific gravity up to 1.1 and with test temperature according to UL 2085.

If Project has more than one type or configuration of insulated, steel, fuel-oil AST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.11 CONCRETE-VAULTED, STEEL, FUEL-OIL AST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cardinal Tank Corp.

2. ConVault, Inc.

3. Earthsafe Systems, Inc.

4. EcoVault, Inc.

5. <Insert manufacturer's name>.

C. Description:  [UL 142 and UL 2085] [UL 142, UL 2085, and STI F941]; thermally insulated, fire-resistant and protected, double-wall, horizontal, steel tank; with primary- and secondary-containment walls and insulation and with interstitial space.

D. Construction:  Fabricated with welded, carbon steel and insulation and encased in concrete that will protect from bullets; suitable for operation at atmospheric pressure and for storing fuel oil with specific gravity up to 1.1 and with test temperature according to UL 2085.

If Project has more than one type or configuration of concrete-vaulted, steel, fuel-oil AST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.12 STEEL, FUEL-OIL UST WITH STI-P3

This article specifies USTs with the STI-P3 corrosion-protection system.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Adamson Global Technology Corporation.

3. Brown Tank.

4. Clawson Tank Company.

5. Containment Solutions, Inc.

6. Hall Tank Co.

7. Hamilton Tanks.

8. Highland Tank & Manufacturing Company, Inc.

9. Kennedy Tank and Manufacturing Company, Inc.

10. Lannon Tank Corporation.

11. Modern Welding Company, Inc.

12. Palmer Manufacturing & Tank Inc.

13. Service Welding & Machine Co., Inc.

14. Steel Tank & Fabricating Co., Inc.

15. Watco Tanks, Inc.

16. We-Mac Manufacturing, Inc.

17. <Insert manufacturer's name>.

C. Description:  UL 58 and STI P3, double-wall, horizontal, steel tank; with cathodic protection and electrical isolation.

1. Containment Method:  STI-P3, [Type I, with primary and secondary walls in contact] [Type II, with interstitial space].

D. Construction:  Fabricated with welded steel; suitable for operation at atmospheric pressure and for storing liquids with specific gravity up to 1.1; fabricated for the following loads:

1. Depth of Bury:  3 feet (1 m) from top of tank to finished surface.

2. External Hydrostatic Pressure:  To withstand general buckling with safety factor of 2:1 if hole is fully flooded.

3. Surface Loads:  AASHTO's "Specifications for Highway Bridges," H-20 axle loads of 32,000 lb (14 515 kg).

E. Corrosion-Protection System:  Protect tank and factory-installed piping by engineered and installed corrosion-protection system according to STI P3, with means of monitoring cathodic protection.

If Project has more than one type or configuration of steel, fuel-oil UST with STI-P3, delete paragraph below and schedule tanks on Drawings.

F. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.13 COMPOSITE, STEEL, FUEL-OIL UST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Adamson Global Technology Corporation.

3. Brown Tank.

4. Clawson Tank Company.

5. Containment Solutions, Inc.

6. Hall Tank Co.

7. Hamilton Tanks.

8. Modern Welding Company, Inc.

9. Palmer Manufacturing & Tank Inc.

10. Watco Tanks, Inc.

11. We-Mac Manufacturing, Inc.

12. <Insert manufacturer's name>.

C. Description:  UL 58, double-wall, horizontal, composite tank; with coating complying with UL 1746 and STI F894.

1. Containment Method:  STI F894, [Type I, with primary and secondary walls in contact] [Type II, with interstitial space].

D. Construction:  Fabricated with welded steel and factory coating according to UL 1746 and STI F894; suitable for operation at atmospheric pressure and for storing liquids with specific gravity up to 1.1; fabricated for the following loads:

1. Depth of Bury:  3 feet (1 m) from top of tank to finished surface.

2. External Hydrostatic Pressure:  To withstand general buckling with safety factor of 2:1 if hole is fully flooded.

3. Surface Loads:  AASHTO's "Specifications for Highway Bridges," H-20 axle loads of 32,000 lb (14 515 kg).

If Project has more than one type or configuration of composite, steel, fuel-oil UST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.14 JACKETED, STEEL, FUEL-OIL UST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ace Tank & Equipment Company.

2. Cardinal Tank Corp.

3. Clawson Tank Company.

4. Hamilton Tanks.

5. Highland Tank & Manufacturing Company, Inc.

6. Kennedy Tank and Manufacturing Company, Inc.

7. Lannon Tank Corporation.

8. Palmer Manufacturing & Tank Inc.

9. Service Welding & Machine Co., Inc.

10. <Insert manufacturer's name>.

C. Description:  Jacketed, horizontal, steel tank; complying with UL 58, and with plastic or fiberglass jacket and corrosion-protection system according to UL 1746[ and STI F922].

D. Construction:  Tank fabricated with welded carbon steel, and jacket fabricated with plastic or fiberglass and vacuum-sealed interstitial space; suitable for operation at atmospheric pressure and with integral leak-detection device.  Tank fabricated for the following loads:

1. Depth of Bury:  3 feet (1 m) from top of tank to finished surface.

2. External Hydrostatic Pressure:  To withstand general buckling with safety factor of 2:1 if hole is fully flooded.

3. Surface Loads:  AASHTO's "Specifications for Highway Bridges," H-20 axle loads of 32,000 lb (14 515 kg).

If Project has more than one type or configuration of jacketed, steel, fuel-oil UST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.15 FRP FUEL-OIL UST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Containment Solutions, Inc.

2. Xerxes Corporation.

3. <Insert manufacturer's name>.

C. Description:  Horizontal, FRP UST; UL 1316, double wall, with interstitial space[ and integral, hydrostatic, leak-detection and monitoring system].

D. Construction:  Fabricated with fiberglass-reinforced polyester resins; suitable for operation at atmospheric pressure; fabricated for the following loads:

1. Depth of Bury:  3 feet (1 m) from top of tank to finished surface.

2. External Hydrostatic Pressure:  To withstand general buckling with safety factor of 2:1 if hole is fully flooded.

3. Surface Loads:  AASHTO's "Specifications for Highway Bridges," H-20 axle loads of 32,000 lb (14 515 kg).

If Project has more than one type or configuration of FRP fuel-oil UST, delete paragraph below and schedule tanks on Drawings.

E. Capacities and Characteristics:

1. Capacity:  <Insert gal. (L)>.

2. Diameter:  <Insert feet (m)>.

3. Length:  <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line:  <Insert NPS (DN)>.

b. Vent Line:  <Insert NPS (DN)>.

c. Outlet:  <Insert NPS (DN)>.

d. Return:  <Insert NPS (DN)>.

e. Gage:  <Insert NPS (DN)>.

5. Manholes:

a. Number Required:  <Insert number>.

b. Diameter:  <Insert inches (mm)>.

6. Fuel-Oil Grade Number:  <Insert number>.

2.16 SHOP PAINTING OF AST

Retain this article only for AST with steel exterior surface.

Retain first paragraph below if field painting AST.

A. Apply manufacturer's standard prime coat to exterior steel surface of AST[ and supports].

Retain remainder of this article if shop painting AST.

B. Prepare exterior steel surface of AST[ and tank supports].

Retain first option in first paragraph below for "Commercial Blast Cleaning";  retain second option for "Near-White Blast Cleaning."

C. Shop Cleaning:  After fabrication, blast clean according to [SSPC-SP 6/NACE No. 3] [SSPC-SP 10/NACE No. 2].

D. After cleaning, remove dust or residue from cleaned surfaces.

E. If surface develops rust before prime coat is applied, repeat surface preparation.

F. Apply manufacturer's standard prime coat to shop-cleaned, dry surface same day as surface preparation.

G. Apply manufacturer's standard two-component, epoxy finish coats.

2.17 FUEL-OIL AST ACCESSORIES

Retain this article for ASTs.  Show fittings and accessories on plans, details, and piping schematics.

Retain one of first two paragraphs below.  Retain first paragraph for horizontal tanks and some vertical tanks; retain second paragraph for vertical tanks.

A. Tank Manholes:  22-inch- (560-mm-) minimum diameter; bolted, flanged, and gasketed; centered on top of tank.

B. Tank Manholes:  22-inch- (560-mm-) minimum diameter; bolted, flanged, and gasketed; on top and at side of tank.

Retain one of first two paragraphs below.  Retain first paragraph for horizontal tanks; retain second for vertical tanks.

C. Threaded pipe connection fittings on top of tank, for fill, supply, return, vent, sounding, and gaging.  Include cast-iron plugs for shipping.

D. Threaded pipe connection fittings on top or sides of tank as indicated, for fill, supply, return, vent, sounding, and gaging.  Include cast-iron plugs for shipping.

E. Striker Plates:  Inside tank, on bottom below fill, vent, sounding, gage, and other tube openings.

F. Lifting Lugs:  For handling and installation.

Retain one of first two paragraphs below.  Retain first paragraph for horizontal tanks and some vertical tanks; retain second paragraph for vertical tanks.

G. Ladders:  Carbon-steel ladder inside tank, anchored to top and bottom, and located as indicated.  Include reinforcement of tank at bottom of ladder.

H. Ladders:  Carbon-steel ladder outside tank, anchored to top and side wall.  Comply with requirements in Division 5 Section "Metal Fabrications" for exterior steel ladder.

1. Cage:  Include welded steel cage around ladders for tanks [20 feet (6 m)] <Insert dimension> high or higher.

I. Supply Tube:  Extension of supply piping fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

J. Sounding and Gage Tubes:  Extension of fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

2.18 FUEL-OIL UST ACCESSORIES

Retain this article for USTs.  Show fittings and accessories on plans, details, and piping schematics.

A. Tank Manholes:  22-inch- (560-mm-) minimum diameter; bolted, flanged, and gasketed, with extension collar; for access to inside of tank.

Retain first paragraph below for steel tanks.

B. Steel Tank Masonry Supports:  Two [6-by-6-by-3/8-inch (150-by-150-by-10-mm)] <Insert dimensions> steel angles, [72 inches (1800 mm)] <Insert dimension> long, located longitudinally on tank on each side of manholes and continuously welded in place.

C. Threaded pipe connection fittings on top of tank for fill, supply, return, vent, sounding, and gaging, in locations and of sizes indicated.  Include cast-iron plugs for shipping.

D. Striker Plates:  Inside tank, on bottom below fill, vent, sounding, gage, and other tube openings.

E. Lifting Lugs:  For handling and installation.

F. Ladders:  Carbon-steel ladder inside tank, anchored to top and bottom.  Include reinforcement of tank at bottom of ladder.

G. Supply Tube:  Extension of supply piping fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

H. Sounding and Gage Tubes:  Extension of fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

I. Containment Sumps:  [Fiberglass] [PE] with sump base, add-on extension pieces as required, sump top, lid, and gasket-seal joints.  Include sump entry boots for pipe penetrations through sidewalls.

J. Sump Entry Boots:  Two-part pipe fitting for field assembly and of size required to fit over pipe.  Include gaskets shaped to fit sump sidewall, sleeves, seals, and clamps as required for liquid-tight pipe penetrations.

K. Anchor Straps:  Storage tank manufacturer's standard anchoring system, with straps, strap-insulating material, cables and turnbuckles, of strength at least one and one-half times maximum uplift force of empty tank without backfill in place.

L. Filter Mat:  Geotextile woven or spun filter fabric, in 1 or more layers, for minimum total weight of [3 oz./sq. yd. (101.7 g/sq. m)] <Insert dimension>.

M. Overfill Prevention Valves:  Factory fabricated or shop or field assembled from manufacturer's standard components.  Include drop tube, cap, fill nozzle adaptor, check valve mechanism or other devices, and vent if required to restrict flow at 95 percent of tank capacity and to provide complete shutoff of filling at [98] [99] <Insert other> percent of tank capacity.

2.19 FUEL-OIL STORAGE TANK PIPING SPECIALTIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. EBW, Inc.

2. Environ Products, Inc.

3. Morrison Bros. Co.

4. OPW.

5. Preferred Utilities Manufacturing Corporation.

6. Universal Valve Company.

7. <Insert manufacturer's name>.

Show fuel-oil tank specialty fittings on plans, details, and piping schematics.

B. Fitting Materials:  Cast iron, malleable iron, brass, or corrosion-resistant metal; suitable for fuel-oil service.

1. Surface, Flush-Mounted Fittings:  Waterproof and suitable for truck traffic.

2. Aboveground-Mounted Fittings:  Weatherproof.

Retain one of first three paragraphs below.

C. Spill-Containment Fill Boxes:  Flush mounting, with drainage feature to drain oil into tank, threaded fill-pipe connection, and wrench operation.

D. Fill Boxes:  Flush mounting, with threaded fill-pipe connection and wrench operation.

E. Locking Fill Boxes:  Flush mounting, with locking-type inner fill cap for standard padlock and threaded fill-pipe connection.

F. Supply and Sounding Drop Tubes:  Fuel-oil supply piping or fitting, inside tank, terminating 6 inches (150 mm) above bottom of tank, and with end cut at a 45-degree angle (1:1 slope).

G. Pipe Adapters and Extensions:  Compatible with piping and fittings.

H. Suction Strainers and Check Valves:  Bronze or corrosion-resistant metal components.

I. Foot Valves and Antisiphon Valves:  Poppet-type, bronze or corrosion-resistant metal components.

J. Weatherproof Vent Cap:  Cast- or malleable-iron increaser fitting with corrosion-resistant wire screen, with free area at least equal to cross-sectional area of connecting pipe and threaded-end connection.

K. Metal Manholes:  [22-inch- (560-mm-)] <Insert dimension> minimum diameter frame and cover.  Furnish manhole units of adequate size for access to fittings if size is not indicated.

L. Monitoring Well Caps:  Locking pipe plug and manhole.

M. <Insert required fittings here>.

2.20 SUBMERSIBLE FUEL-OIL PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. FE Petro, Inc.

2. Red Jacket Pumps; a division of Veeder-Root.

3. <Insert manufacturer's name>.

C. Description:  Comply with UL 79, UL 87, and UL 343.

1. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

2. Impeller:  Turbine.

3. Housing and Volute:  Cast iron.

4. Bearings:  Bronze, self-lubricating.

5. Seals:  Mechanical.

6. Shaft:  Polished steel.

7. Suspension Piping:  Telescoping to accommodate tank diameter and depth of bury.

8. Base:  Steel.

9. Pressure Relief:  Built in.

10. Discharge Check Valve:  Built in.

11. Drive:  Direct, close coupled.

D. Controls:  Pump controller panel complying with UL 353 and UL 508C and with interlock and terminals for connections to [fuel-oil-burning equipment] [diesel-driven fire pumps] [diesel-driven emergency generators] [and] [diesel-fuel-oil dispenser].

Select desired control features from subparagraphs below.

1. Run pumps to maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

2. Run pumps on seven-day schedule.

3. Stage pumps on pressure at a common supply manifold.

4. Alternate pumps to equalize run time.

5. Alarm motor failure.

6. Manual reset dry-run protection.  Stop pumps if fuel level falls below pump suction.

7. Deenergize and alarm pump locked rotor condition.

8. Alarm open circuit, high and low voltage.

9. Indicating lights for power on, run, and off normal conditions.

10. Interface with automatic control system is specified in Division 15 Section "HVAC Instrumentation and Controls" to control and indicate the following:

a. Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

b. Operating status.

c. Alarm off-normal status.

Default motor characteristics are specified in Division 15 Section "Motors."

E. Motor:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Thermal-Overload Protection:  Motor-winding temperature sensor.

3. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

If Project has more than one submersible fuel-oil pump, delete paragraph below and schedule pumps on Drawings.

F. Capacities and Characteristics:

1. Number of Stages:  <Insert number>.

2. Capacity:  <Insert gph (L/s)>.

3. Discharge Pressure:  <Insert psig (kPa)>.

4. Outlet Size:  <Insert NPS (DN)>.

5. Motor Speed:  <Insert rpm>.

6. Motor Horsepower:  <Insert value>.

7. Electrical Characteristics:

a. Volts:  [120] [208] [240] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.21 SIMPLEX FUEL-OIL TRANSFER PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Retain one of two subparagraphs and lists below.  Retain second subparagraph and list when pumps are required by authorities having jurisdiction to be listed and labeled by an NRTL.

1. Fuel-Oil Transfer Pumps:

a. DESMI INC./Rotan Pumps.

b. Haight Pumps; Division of Baker Mfg.

c. Preferred Utilities Manufacturing Corporation.

d. Suntec Industries Incorporated.

e. Tuthill Corporation; Tuthill Pump Div.

f. Viking Pump Inc.; a Unit of IDEX Corporation.

g. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

h. <Insert manufacturer's name>.

2. NRTL-Listed, Fuel-Oil Transfer Pumps:

a. Tuthill Corporation; Tuthill Pump Div.

b. Viking Pump Inc.; a Unit of IDEX Corporation.

c. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

d. <Insert manufacturer's name>.

C. Description:  Comply with UL 343, and HI M109.

1. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

2. Type:  Positive-displacement, rotary type.

3. Impeller:  [Steel gear with crescent] [Carbon vane].

4. Housing:  Cast-iron foot mounted.

5. Bearings:  Bronze, self-lubricating.

6. Shaft:  Polished steel.

7. Seals:  Mechanical.

8. Base:  Steel.

9. Pressure Relief:  Built in.

10. Discharge Check Valve:  Built in.

Some manufacturers provide close-coupled pumps in first paragraph below only in certain size ranges.

D. Drive:  [V-belt with guard; gear reducer; or direct, close coupled] [V-belt with guard] [Gear reducer] [Direct, close coupled].

E. Controls:

Select desired control features from subparagraphs below.

1. Run pump to maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

2. Run pump on seven-day schedule.

3. Alarm motor failure.

4. Manual reset dry-run protection.  Stop pump if fuel level falls below pump suction.

5. Deenergize and alarm pump locked rotor condition.

6. Alarm open circuit, high and low voltage.

7. Indicating lights for power on, run, and off normal conditions.

8. Interface with automatic control system is specified in Division 15 Section "HVAC Instrumentation and Controls" to control and indicate the following:

a. Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

b. Operating status.

c. Alarm off-normal status.

Default motor characteristics are specified in Division 15 Section "Motors."

F. Motor:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

If Project has more than one simplex fuel-oil transfer pump, delete paragraph below and schedule pumps on Drawings.

G. Capacities and Characteristics:

1. Number of Stages:  <Insert number>.

2. Capacity:  <Insert gph (L/s)>.

3. Inlet Vacuum:  <Insert inches Hg (kPa)>.

4. Discharge Pressure:  <Insert psig (kPa)>.

5. Inlet and Outlet Size:  <Insert NPS (DN)>.

6. Motor Speed:  <Insert rpm>.

7. Motor Horsepower:  <Insert value>.

8. Electrical Characteristics:

a. Volts:  [120] [208] [240] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.22 [DUPLEX] [TRIPLEX] FUEL-OIL TRANSFER PUMP SETS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Alyan Pump Company.

2. Hydronic Modules Corporation.

3. Preferred Utilities Manufacturing Corporation.

4. Smith-Koch, Inc.

5. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

6. <Insert manufacturer's name>.

C. Description:  Comply with HI M109.

1. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

2. Type:  Positive-displacement, rotary type.

3. Impeller:  [Steel gear with crescent] [Carbon vane].

4. Housing:  Cast-iron foot mounted.

5. Bearings:  Bronze, self-lubricating.

6. Shaft:  Polished steel.

7. Seals:  Mechanical.

8. Base:  Steel.

9. Pressure Relief:  Built in.

10. Discharge Check Valve:  Built in.

Some manufacturers provide close-coupled pumps in first paragraph below only in certain size ranges.

D. Drive:  [V-belt with guard, gear reducer, or direct close coupled] [V-belt with guard] [Gear reducer] [Direct close coupled].

E. Controls:

Select desired control features from subparagraphs below.

1. Run pumps to maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

2. Run pumps on seven-day schedule.

3. Stage pumps on pressure at a common supply manifold.

4. Alternate pumps to equalize run time.

5. Alarm motor failure.

6. Manual reset dry-run protection.  Stop pumps if fuel level falls below pump suction.

7. Deenergize and alarm pump locked rotor condition.

8. Alarm open circuit, high and low voltage.

9. Indicating lights for power on, run, and off normal conditions.

10. Interface with automatic control system is specified in Division 15 Section "HVAC Instrumentation and Controls" to control and indicate the following:

a. Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

b. Operating status.

c. Alarm off-normal status.

Default motor characteristics are specified in Division 15 Section "Motors."

F. Motor:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

G. Piping Furnished with Pumps:  Steel with ferrous fittings and threaded or welded joints.

H. Strainers Furnished with Pumps:  Duplex, basket type with corrosion-resistant-metal-screen baskets.

If Project has more than one duplex or triplex fuel-oil transfer pump set, delete paragraph below and schedule pump sets on Drawings.

I. Capacities and Characteristics:

1. Number of Stages:  <Insert number>.

2. Capacity (Each Pump):  <Insert gph (L/s)>.

3. Inlet Vacuum:  <Insert inches Hg (kPa)>.

4. Discharge Pressure:  <Insert psig (kPa)>.

5. Inlet and Outlet Size:  <Insert NPS (DN)>.

6. Motor Speed:  <Insert rpm>.

7. Motor Horsepower (Each Pump):  <Insert value>.

8. Electrical Characteristics (Pump Set):

a. Volts:  [120] [208] [240] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.23 FUEL MAINTENANCE SYSTEM

Retain this article for fuel systems that serve diesel-engine-driven equipment.  Authorities having jurisdiction may require this system for healthcare facilities.  Fuel maintenance system circulates fuel oil from storage tanks through filters and back to storage tanks to remove particulates, biogrowth, and moisture that accumulates as the fuel ages.  Fuel maintenance program may be implemented by using fuel oil before it begins to deteriorate (approximately one month), by periodic replacement of fuel oil, or by filtering the fuel and adding stabilizers.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Fuel Technologies, International, LLC.

2. <Insert manufacturer's name>.

C. Description:  Factory fabricated and wired fuel maintenance system for fuel-oil filtration; with enclosure, filter, fuel-oil pump, and controls; FMG approved, listed, and labeled by an NRTL acceptable to authorities having jurisdiction.

1. Enclosure:  NEMA 250, Type 3R, painted steel containing pumps, filters, accessories, and controls.  Hinged door on the front of enclosure.

2. Pump:  Comply with HI M109, steel-gear-with-crescent, positive-displacement, direct- coupled, rotary-type.

3. Materials:  Cast-iron housing; bronze bearings; steel shaft; mechanical seals; and built-in, pressure relief bypass valve.

Default motor characteristics are specified in Division 15 Section "Motors."

4. Motor:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

b. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

5. Piping:  Steel with malleable-iron fittings and threaded joints or wrought-steel fittings and welded joints.

6. Multistage Filter:  Spin-on, replaceable types.

a. Stage 1:  100-mesh strainer.

b. Stage 2:  Centrifuge to separate particulates and water from oil.

c. Stage 3:  Coalescing water and particulate filter.

d. Stage 4:  30-micron particulate removal.

e. Stage 5:  10-micron particulate removal.

f. Stage 6:  Minimum 99.5 percent water removal with see-through bowl and water-sensor probe.

g. Stage 7:  [1.5] [3]-micron particulate removal.

Retain first subparagraph below for multiple fuel-oil storage tanks.

7. Multiple-Tank Manifolds:

a. Manifold fabricated of Schedule 80, black steel pipe and threaded nipples for [two] [three] [four] tanks.

b. Solenoid valves for supply and return piping to each tank.

c. Strainers for each tank supply connection.

8. Programmable Logic Controller:

a. Alarm on maximum 15-in. Hg (51-kPa) vacuum at pump suction indicating plugged filter.

b. Alarm on high water level in filter.

c. Alarm leak in enclosure.

d. Touch screen; with minimum 2-line, 20-character, backlit, LCD display.

e. Controller strip heater with thermostat.

9. Interface with automatic control system is specified in Division 15 Section "HVAC Instrumentation and Controls" to control and indicate the following:

a. Start/stop system when required by schedule.

b. Operating status.

c. Alarm off-normal status.

If Project has more than one fuel maintenance system, delete paragraph below and schedule systems on Drawings.

D. Capacities and Characteristics:

1. Capacity (Each Pump):  [3 gpm (0.19 L/s)] [8 gpm (0.50 L/s)] [24 gpm (1.5 L/s)] <Insert value>.

If maximum suction lift exceeds 15 feet (4.6 m), delete pumps from this equipment and specify a submersible pump in storage tank(s).  Control submersible pump(s) with fuel-oil maintenance system.

2. Maximum Suction Lift:  [15 feet (4.6 m)] <Insert value>.

3. Inlet and Outlet Size:  <Insert NPS (DN)>.

4. Motor Horsepower (Each Pump):  <Insert value>.

5. Electrical Characteristics (Pump Set):

a. Volts:  [120] [208] [240] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.24 LIQUID-LEVEL GAGE SYSTEM

Retain this article if liquid-level gage system is not specified in "Leak-Detection and Monitoring System" Article.  Delete this article if liquid-level gage system is included in the leak-detection and monitoring system.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Caldwell Systems Corporation.

2. Clawson Tank Company.

3. EBW, Inc.

4. Highland Tank & Manufacturing Company, Inc.

5. INCON, Inc.

6. King Engineering Corp.

7. Krueger Sentry Gauge.

8. Pneumercator Inc.

9. Preferred Utilities Manufacturing Corporation.

10. Rochester Gauges, Inc.

11. Tuthill Corporation; Tuthill Transfer Systems; Sotera Systems.

12. Uehling Instrument Company.

13. Venture Measurement Company, LLC.

14. <Insert manufacturer's name>.

C. Description:  Calibrated, liquid-level gage system complying with [UL 180 with floats] [UL 1238 with probes] or other sensors and remote annunciator panel.

Alarms specified in first paragraph below may be used as part of leak-detection system.

D. Annunciator Panel:  With visual and audible, high-tank-level and low-tank-level alarms, fuel indicator with registration in gallons (liters), and overfill alarm.  Include gage volume range that covers fuel-oil storage capacity.

E. Controls:  Electrical, operating on [120] <Insert voltage>-V ac.

2.25 LEAK-DETECTION AND MONITORING SYSTEM

Retain one of two paragraphs in this article.

A. Cable and Sensor System:  Comply with UL 1238.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Caldwell Systems Corporation.

b. Containment Solutions, Inc.

c. EBW, Inc.

d. Gems Sensors Inc.

e. Highland Tank & Manufacturing Company, Inc.

f. INCON, Inc.

g. In-Situ, Inc.

h. MSA; Instrument Div.

i. Perma-Pipe, Inc.

j. Pneumercator Inc.

k. Raychem Corp; Tyco Electronics Corporation.

l. Tuthill Corporation; Tuthill Transfer Systems; Sotera Systems.

m. Veeder-Root; a Danaher Corporation Company.

n. <Insert manufacturer's name>.

Visual and audible alarms in "Liquid-Level Gage System" Article may be used as part of leak-detection system.

3. Calibrated, leak-detection and monitoring system with probes and other sensors and remote alarm panel for fuel-oil storage tanks and fuel-oil piping.

4. Include fittings and devices required for testing.

5. Controls:  Electrical, operating on [120] <Insert voltage>-V ac.

Retain three subparagraphs below for an optional feature that replaces system described in "Liquid-Level Gage System" Article.

6. Calibrated, liquid-level gage complying with [UL 180 with floats] [UL 1238 with probes] or other sensors and remote annunciator panel.

7. Remote Annunciator Panel:  With visual and audible, high-tank-level and low-tank-level alarms, fuel indicator with registration in gallons (liters), and overfill alarm.  Include gage volume range that covers fuel-oil storage capacity.

8. Controls:  Electrical, operating on [120] <Insert voltage>-V ac.

B. Hydrostatic System:  Comply with UL 1238.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Caldwell Systems Corporation.

b. Containment Solutions, Inc.

c. EBW, Inc.

d. Gems Sensors Inc.

e. Highland Tank & Manufacturing Company, Inc.

f. INCON, Inc.

g. In-Situ, Inc.

h. MSA; Instrument Div.

i. Perma-Pipe, Inc.

j. Pneumercator Inc.

k. Raychem Corp; Tyco Electronics Corporation.

l. Tuthill Corporation; Tuthill Transfer Systems; Sotera Systems.

m. Veeder-Root; a Danaher Corporation Company.

n. <Insert manufacturer's name>.

Visual and audible alarms in "Liquid-Level Gage System" Article may be used as part of leak-detection system.

3. Calibrated, leak-detection and monitoring system with brine antifreeze solution, reservoir sensor, and electronic control panel to monitor leaks in inner and outer tank walls.

4. Include fittings and devices required for testing.

5. Controls:  Electrical, operating on [120] <Insert voltage>-V ac.

Retain three subparagraphs below for an optional feature that replaces system described in "Liquid-Level Gage System" Article.

6. Calibrated, liquid-level gage complying with [UL 180 with floats] [UL 1238 with probes] or other sensors and remote annunciator panel.

7. Remote Annunciator Panel:  With visual and audible, high-tank-level and low-tank-level alarms, fuel indicator with registration in gallons (liters), and overfill alarm.  Include gage volume range that covers fuel-oil storage capacity.

8. Controls:  Electrical, operating on [120] <Insert voltage>-V ac.

2.26 FUEL OIL

Second option in first paragraph below is grade typically used for fuel-oil-burning equipment.

A. Fuel Oil:  ASTM D 396, Grade [No. 1] [No. 2].

Last option in paragraph below is typically used for automotive or other diesel engines.

B. Diesel Fuel Oil:  ASTM D 975, Grade [Low Sulfur] [No. 1-D, special-purpose] [No. 2-D, general-purpose], high volatility.

2.27 SLEEVES

Retain this article for penetrations through exterior walls.

A. Steel Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.

B. Cast-Iron Pipe Sleeves:  Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop unless otherwise indicated.

2.28 MECHANICAL SLEEVE SEALS

Retain this article for penetrations through exterior walls.

A. Description:  Modular sealing element unit, designed for field assembly, to fill annular space between pipe and sleeve.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Advance Products & Systems, Inc.

b. Calpico Inc.

c. Metraflex Company (The).

d. Pipeline Seal and Insulator, Inc.

e. <Insert manufacturer's name>.

2. Sealing Elements:  [EPDM] [NBR] <Insert other> interlocking links shaped to fit surface of pipe.  Include type and number required for pipe material and size of pipe and sleeve.

3. Pressure Plates:  [Plastic] [Carbon steel] [Stainless steel].

4. Connecting Bolts and Nuts:  [Carbon steel with corrosion-resistant coating] [Stainless steel] of length required to secure pressure plates to sealing elements.  Include one nut and bolt for each sealing element.

2.29 ESCUTCHEONS

A. General Requirements for Escutcheons:  Manufactured wall and ceiling escutcheons and floor plates, with ID to fit around pipe or tube and with OD that completely covers opening.

Retain escutcheons in seven paragraphs below to coordinate with selections in "Indoor Piping Installation" Article.

B. One-Piece, Deep-Pattern Escutcheons:  Deep-drawn brass with polished chrome-plated finish.

C. One-Piece, Cast-Brass Escutcheons:  With set screw.

1. Finish:  [Polished chrome-plated] [Rough brass] [Polished chrome-plated or rough brass].

D. Split-Casting, Cast-Brass Escutcheons:  With concealed hinge and set screw.

1. Finish:  [Polished chrome-plated] [Rough brass] [Polished chrome-plated or rough brass].

E. One-Piece, Stamped-Steel Escutcheons:  With [set screw] [spring clips] [set screw or spring clips] and chrome-plated finish.

F. Split-Plate, Stamped-Steel Escutcheons:  With [concealed] [exposed-rivet] hinge, [set screw] [spring clips] [set screw or spring clips], and chrome-plated finish.

G. One-Piece, Floor-Plate Escutcheons:  Cast-iron floor plate.

H. Split-Casting, Floor-Plate Escutcheons:  Cast brass with concealed hinge and set screw.

2.30 GROUT

A. Description:  ASTM C 1107, Grade B, nonshrink and nonmetallic, dry hydraulic-cement grout.

1. Characteristics:  Posthardening, volume adjusting, nonstaining, noncorrosive, nongaseous, and recommended for interior and exterior applications.

2. Design Mix:  5000-psi (34.5-MPa), 28-day compressive strength.

3. Packaging:  Premixed and factory packaged.

2.31 LABELING AND IDENTIFYING

A. Detectable Warning Tape:  Acid- and alkali-resistant, PE film warning tape manufactured for marking and identifying underground utilities, a minimum of 6 inches (152 mm) wide and 4 mils (0.1 mm) thick, continuously inscribed with a description of utility, with metallic core encased in a protective jacket for corrosion protection, detectable by metal detector when tape is buried up to 30 inches (762 mm) deep; colored yellow.

2.32 CONCRETE MANHOLES

A. Precast Concrete Manhole Sections:  ASTM C 478 (ASTM C 478M), base and concentric-cone sections with integral ladder or steps.

B. Cast-Iron Frame and Cover:  Heavy-duty, water-resistant, cast-iron manhole frame, gasket, and bolted cover; [24-inch- (609-mm-)] <Insert dimension> diameter, inside opening dimension; [8-inch (203-mm)] <Insert dimension> frame riser height.

2.33 SOURCE QUALITY CONTROL

Coordinate standards for tests in this article with those referenced in Part 2 fuel-oil storage tank articles.  Do not include STI tests if tanks are not STI type.

A. Pressure test and inspect fuel-oil storage tanks, after fabrication and before shipment, according to ASME and the following:

Retain one or more of seven subparagraphs below.

1. [Vertical] [Vertical or Horizontal] [Horizontal], Single-Wall Steel ASTs:  UL 142.

2. [Vertical] [Vertical or Horizontal] [Horizontal], Double-Wall Steel ASTs:  UL 142, STI F921, and STI R931.

3. Horizontal, Containment-Dike, Steel ASTs:  UL 142 and STI F911.

4. Horizontal, [Concrete-Vaulted] [Concrete-Vaulted and Insulated] [Insulated], Steel ASTs:  UL 142 and UL 2085.

5. Horizontal, Steel USTs with the STI-P3 Corrosion-Protection System:  UL 58 and STI P3.

6. [Composite] [Composite and Jacketed] [Jacketed], Steel USTs:  UL 58.

7. FRP USTs:  UL 1316.

B. Affix standards organization's code stamp.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for fuel-oil piping system to verify actual locations of piping connections before equipment installation.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 EARTHWORK

A. Comply with requirements in Division 2 Section "Earthwork" for excavating, trenching, and backfilling.

3.3 PREPARATION

Retain first paragraph below for renovations and additions.

A. Close equipment shutoff valves before turning off fuel oil to premises or piping section.

B. Comply with NFPA 30 and NFPA 31 requirements for prevention of accidental ignition.

3.4 OUTDOOR PIPING INSTALLATION

NFPA 30 requires a minimum of 18 inches (457 mm) of compacted backfill, 8 inches (203 mm) under asphalt 2 inches (51 mm) thick, or 4 inches (102 mm) under 4 inches (102 mm) of reinforced concrete in areas subject to vehicle traffic; 6 inches (152 mm) of compacted backfill in areas without traffic.  Greater depth is required as recommended by pipe and equipment manufacturers where frost conditions may occur.

A. Install underground fuel-oil piping buried at least [18 inches (457 mm)] <Insert dimension> below finished grade.  Comply with requirements in Division 2 Section "Earthwork" for excavating, trenching, and backfilling.

1. If fuel-oil piping is installed with less than [12 inches (305 mm)] <Insert dimension> of cover to finished grade, install in containment piping.

B. Steel Piping with Protective Coating:

1. Apply joint cover kits to pipe after joining, to cover, seal, and protect joints.

Retain one of two subparagraphs below.  Verify acceptability of repaired coating systems with authorities having jurisdiction.

2. Repair damage to PE coating on pipe as recommended in writing by protective coating manufacturer.  Review protective coating damage with Architect prior to repair.

3. Replace pipe having damaged PE coating with new pipe.

C. Install double-containment, fuel-oil pipe at a minimum slope of 1 percent downward toward fuel-oil storage tank sump.

D. Install vent pipe at a minimum slope of 2 percent downward toward fuel-oil storage tank sump.

E. Assemble and install entry boots for pipe penetrations through sump sidewalls for liquid-tight joints.

F. Install metal pipes and tubes, fittings, valves, and flexible connectors at piping connections to AST and UST.

G. Install fittings for changes in direction in rigid pipe.

H. Install system components with pressure rating equal to or greater than system operating pressure.

I. Aboveground, Exterior-Wall Pipe Penetrations:  Seal penetrations using steel pipe sleeves and mechanical sleeve seals.  Install sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

J. Underground, Exterior-Wall Pipe Penetrations:  Install cast-iron "wall pipes" for sleeves.  Seal pipe penetrations using mechanical sleeve seals.  Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

K. Mechanical Sleeve Seal Installation:  Position pipe in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between pipe and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

L. Install pressure gage on suction[ and discharge] from each pump.  Pressure gages are specified in Division 15 Section "Meters and Gages."

3.5 INDOOR PIPING INSTALLATION

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Arrange for pipe spaces, chases, slots, sleeves, and openings in building structure during progress of construction, to allow for mechanical installations.

C. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

D. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

E. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

F. Install piping free of sags and bends.

G. Install fittings for changes in direction and branch connections.

H. Install escutcheons for penetrations of walls, ceilings, and floors.

Coordinate applications in "New Piping" and "Existing Piping" subparagraphs below with escutcheons specified in Part 2.

1. New Piping:

a. Piping with Fitting or Sleeve Protruding from Wall:  One-piece, deep-pattern type.

Retain one of first two subparagraphs below.

b. Piping at Wall and Floor Penetrations in Finished Spaces:  One-piece, cast-brass type with polished chrome-plated finish.

c. Piping at Wall and Floor Penetrations in Finished Spaces:  One-piece, stamped-steel type.

Retain one of first two subparagraphs below.

d. Piping at Ceiling Penetrations in Finished Spaces:  [One-piece] [Split-casting] [One-piece or split-casting], cast-brass type with polished chrome-plated finish.

e. Piping at Ceiling Penetrations in Finished Spaces:  [One-piece, stamped-steel type] [Split-plate, stamped-steel type with concealed hinge] [One-piece, stamped-steel type or split-plate, stamped-steel type with concealed hinge] and set screw.

Retain one of first two subparagraphs below.

f. Piping in Unfinished Service Spaces:  One-piece, cast-brass type with [polished chrome-plated] [rough-brass] finish.

g. Piping in Unfinished Service Spaces:  One-piece, stamped-steel type with [set screw] [spring clips] [set screw or spring clips].

Retain one of first two subparagraphs below.

h. Piping in Equipment Rooms:  One-piece, cast-brass type.

i. Piping in Equipment Rooms:  One-piece, stamped-steel type with [set screw] [spring clips] [set screw or spring clips].

j. Piping at Floor Penetrations in Equipment Rooms:  One-piece, floor-plate type.

2. Existing Piping:

Retain one of first two subparagraphs below.

a. Piping at Wall and Floor Penetrations in Finished Spaces:  Split-casting, cast-brass type with chrome-plated finish.

b. Piping at Wall and Floor Penetrations in Finished Spaces:  Split-plate, stamped-steel type with concealed hinge and spring clips.

Retain one of first two subparagraphs below.

c. Piping at Ceiling Penetrations in Finished Spaces:  Split-casting, cast-brass type with chrome-plated finish.

d. Piping at Ceiling Penetrations in Finished Spaces:  Split-plate, stamped-steel type with concealed hinge and set screw.

Retain one of first two subparagraphs below.

e. Piping in Unfinished Service Spaces:  Split-casting, cast-brass type with [polished chrome-plated] [rough-brass] finish.

f. Piping in Unfinished Service Spaces:  Split-plate, stamped-steel type with [concealed] [exposed-rivet] [concealed or exposed-rivet] hinge and set screw or spring clips.

Retain one of first two subparagraphs below.

g. Piping in Equipment Rooms:  Split-casting, cast-brass type.

h. Piping in Equipment Rooms:  Split-plate, stamped-steel type with set screw or spring clips.

i. Piping at Floor Penetrations in Equipment Rooms:  Split-casting, floor-plate type.

I. Fire-Barrier Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations.  Seal pipe penetrations with firestop materials.  Comply with requirements in Division 7 Section "Through-Penetration Firestop Systems."

J. Verify final equipment locations for roughing-in.

K. Comply with requirements for equipment specifications in Division 15 Sections for roughing-in requirements.

L. Conceal pipe installations in walls, pipe spaces, or utility spaces; above ceilings; below grade or floors; and in floor channels unless indicated to be exposed to view.

M. Prohibited Locations:

1. Do not install fuel-oil piping in or through circulating air ducts, clothes or trash chutes, chimneys or gas vents (flues), ventilating ducts, or dumbwaiter or elevator shafts.

2. Do not install fuel-oil piping in solid walls or partitions.

N. Use eccentric reducer fittings to make reductions in pipe sizes.  Install fittings with level side down.

O. Connect branch piping from top or side of horizontal piping.

P. Install unions in pipes NPS 2 (DN 50) and smaller at final connection to each piece of equipment and elsewhere as indicated.  Unions are not required on flanged devices.

Q. Do not use fuel-oil piping as grounding electrode.

R. Install [Y-pattern] [basket] [T-pattern] strainer on inlet side of fuel-oil pump.

3.6 VALVE INSTALLATION

A. Install manual fuel-oil shutoff valves on branch connections to fuel-oil appliance.

B. Install valves in accessible locations.

C. Protect valves from physical damage.

D. Install metal tag attached with metal chain indicating fuel-oil piping systems.

E. Identify valves as specified in Division 15 Section "Mechanical Identification."

F. Install oil safety valves at inlet of each oil-fired appliance.

G. Install pressure relief valves in distribution piping between the supply and return lines.

H. Install one-piece, bronze ball valve with hose end connection at low points in fuel-oil piping.

I. Install manual air vents at high points in fuel-oil piping.

Retain paragraph below for systems with fuel-oil or diesel-fuel-oil dispensers.

J. Install emergency shutoff valves at dispensers.

3.7 PIPING JOINT CONSTRUCTION

A. Ream ends of pipes and tubes and remove burrs.

B. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

C. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

D. Welded Joints:  Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators according to "Quality Assurance" Article.

1. Bevel plain ends of steel pipe.

2. Patch factory-applied protective coating as recommended by manufacturer at field welds and where damage to coating occurs during construction.

E. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter.

F. Flanged Joints:  Install gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.

G. Flared Joints:  Comply with SAE J513.  Tighten finger tight, then use wrench according to fitting manufacturer's written recommendations.  Do not overtighten.

H. Fiberglass-Bonded Joints:  Prepare pipe ends and fittings, apply adhesive, and join according to pipe manufacturer's written instructions.

3.8 FUEL-OIL AST INSTALLATION

A. Install tank bases and supports.

B. Connect piping and vent fittings.

C. Install ground connections.

D. Install tank leak-detection and monitoring devices.

E. Install steel ASTs according to STI R912.

F. Install insulated and concrete-vaulted, steel ASTs according to STI R942.

G. Fill storage tanks with fuel oil.

3.9 FUEL-OIL UST INSTALLATION

Coordinate this article with Drawings.

A. Excavate to sufficient depth for a minimum of 3 feet (1 m) of earth cover from top of tank to finished grade.  Allow for cast-in-place, concrete-ballast base plus 6 inches (150 mm) of sand or pea gravel between ballast base and tank.  Extend excavation at least 12 inches (300 mm) around perimeter of tank.

B. Set tie-down eyelets for hold-down straps in concrete-ballast base and tie to reinforcing steel.

C. Place 6 inches (152 mm) of clean sand or pea gravel on top of concrete-ballast base.

D. Set tank on fill materials and install hold-down straps.

E. Connect piping.

F. Install tank leak-detection and monitoring devices.

G. Install containment sumps.

H. Backfill excavation with clean sand or pea gravel in 12-inch (305-mm) lifts and tamp backfill lift to consolidate.

I. Install filter mat between top of backfill material and earth fill.

J. Install steel USTs with the STI-P3 corrosion-protection system according to STI R821 and STI R891.  Protect anodes during tank placement and backfilling operations.

K. Install composite, steel USTs according to STI R913 and STI R891.

L. Install jacketed, steel USTs according to STI R923 and STI R891.

M. Install FRP USTs with FRP hold-down straps, manhole extensions, and manhole risers.

N. Fill storage tanks with fuel oil.

3.10 HANGER AND SUPPORT INSTALLATION

A. Pipe hanger and support and equipment support materials and installation requirements are specified in Division 15 Section "Hangers and Supports."

Maximum spans below are from MSS SP-69 (water service).

B. Install hangers for horizontal steel piping with the following maximum spacing and minimum rod sizes:

1. NPS 1-1/4 (DN 32) and Smaller:  Maximum span, 84 inches (2130 mm); minimum rod size, 3/8 inch (10 mm).

2. NPS 1-1/2 (DN 40):  Maximum span, 108 inches (2740 mm); minimum rod size, 3/8 inch (10 mm).

3. NPS 2 (DN 50):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

4. NPS 2-1/2 (DN 65):  Maximum span, 11 feet (3.4 m); minimum rod size, 1/2 inch (13 mm).

5. NPS 3 (DN 80):  Maximum span, 12 feet (3.7 m); minimum rod size, 1/2 inch (13 mm).

6. NPS 4 (DN 100):  Maximum span, 13 feet (4 m); minimum rod size, 5/8 inch (16 mm).

C. Support vertical steel pipe at each floor and at spacing not greater than 15 feet (4.5 m).

D. Install hangers for horizontal, drawn-temper copper tubing with the following maximum spacing and minimum rod sizes:

1. NPS 3/4 (DN 20) and Smaller:  Maximum span, 60 inches (1524 mm); minimum rod size, 3/8 inch (10 mm).

2. NPS 1 (DN 25):  Maximum span, 72 inches (1830 mm); minimum rod size, 3/8 inch (10 mm).

3. NPS 1-1/4 (DN 32):  Maximum span, 84 inches (2130 mm); minimum rod size, 3/8 inch (10 mm).

4. NPS 1-1/2 and NPS 2 (DN 40 and DN 50):  Maximum span, 96 inches (2440 mm); minimum rod size, 3/8 inch (10 mm).

5. NPS 2-1/2 (DN 65):  Maximum span, 108 inches (2740 mm); minimum rod size, 1/2 inch (13 mm).

6. NPS 3 (DN 80):  Maximum span, 10 feet (3 m); minimum rod size, 1/2 inch (13 mm).

7. NPS 4 (DN 100):  Maximum span, 11 feet (3.4 m); minimum rod size, 5/8 inch (16 mm).

E. Support vertical copper tube at each floor and at spacing not greater than 10 feet (3 m).

3.11 FUEL-OIL PUMP INSTALLATION

A. Submersible Pumps:

1. Suspend pumps from supply piping and anchored to bottom of tank.

B. Transfer Pumps:

1. Install pumps with access space for periodic maintenance including removal of motors, impellers, and accessories.

2. Set pumps on and anchor to concrete base.

C. Install two-piece, full-port ball valves at suction and discharge of pumps.

D. Install mechanical leak-detector valves at pump discharge.

Duplex or triplex pumps are furnished with strainers.

E. Install [Y-pattern] [basket] [T-pattern] strainer on inlet side of simplex fuel-oil pumps.

Duplex or triplex pumps are furnished with check valves.

F. Install check valve on discharge of simplex fuel-oil pumps.

G. Install suction piping with minimum fittings and change of direction.

H. Install vacuum and pressure gage, upstream and downstream respectively, at each pump to measure the differential pressure across the pump.  Pressure gages are specified in Division 15 Section "Meters and Gages."

3.12 FUEL MAINTENANCE SYSTEM INSTALLATION

Retain this article for fuel maintenance system.

A. Install suction line, with foot valve, at one end of storage tank, 1 inch (25 mm) from the bottom of tank.

B. Install return line at the opposite end of storage tank from suction line.

3.13 LIQUID-LEVEL GAGE SYSTEM INSTALLATION

A. Install liquid-level gage system.  Locate panel inside building where indicated.

3.14 LEAK-DETECTION AND MONITORING SYSTEM INSTALLATION

Coordinate this article with fuel-oil storage tank and piping.

A. Install leak-detection and monitoring system.  Install alarm panel inside building where indicated.

1. Double-Wall, Fuel-Oil Storage Tanks:  [Install probes] [Install probes or use factory-installed integral probes] [Use factory-installed integral probes] in interstitial space.

System in first subparagraph below requires extensive description here or layout and details on Drawings.

2. Single-Wall, Fuel-Oil Storage Tanks:  Install probes as indicated.

Float-type probes in tank containment sumps and at piping low points, if required, are the most often used.  Cable sensors are also available.

3. Double-Containment, Fuel-Oil Piping:  Install leak-detection sensor [probes in fuel-oil storage tank containment sumps and at low points in piping] [cable probes in interstitial space of double-containment piping].

Retain subparagraph below for liquid-level gage that is part of leak-detection and monitoring system.

4. Install liquid-level gage.

3.15 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Install piping adjacent to equipment to allow service and maintenance.

B. Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment having threaded pipe connection.

C. Install flanges, in piping NPS 2-1/2 (DN 65) and larger, adjacent to flanged valves and at final connection to each piece of equipment having flanged pipe connection.

D. Connect piping to equipment with ball valve and union.  Install union between valve and equipment.

E. Install flexible piping connectors at final connection to burners or oil-fired appliances that must be moved for maintenance access.

3.16 LABELING AND IDENTIFYING

Retain one of first two paragraphs below.

A. Nameplates, pipe identification, and signs are specified in Division 15 Section "Mechanical Identification."

B. Equipment Nameplates and Signs:  Install engraved plastic-laminate equipment nameplates and signs on or near each service regulator, service meter, and earthquake valve.

1. Text:  In addition to identifying unit, distinguish between multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations.

Coordinate dimensions in paragraph below with depth of bury for fuel-oil piping.

C. Install detectable warning tape directly above fuel-oil piping, [12 inches (304 mm)] <Insert dimension> below finished grade, except [6 inches (152 mm)] <Insert dimension> below subgrade under pavements and slabs.  Terminate tracer wire in an accessible area, and identify as "tracer wire" for future use with plastic-laminate sign.

1. Piping:  Over underground fuel-oil distribution piping.

2. Fuel-Oil Storage Tanks:  Over edges of each UST.

3.17 FIELD PAINTING OF AST

Retain this article only for AST with steel exterior surface.

Retain first paragraph below if shop painting AST.

A. Prepare and touch up damaged exterior surface of AST[ and supports] as specified in "Shop Painting of AST" Article.

Retain remainder of this article if field painting AST.

B. Prepare exterior steel surface of AST[ and tank supports].

Retain first option in first paragraph below for "Commercial Blast Cleaning"; retain second option for "Near-White Blast Cleaning."

C. Field Cleaning:  After fabrication, blast clean according to [SSPC-SP 6/NACE No. 3] [SSPC-SP 10/NACE No. 2].

D. After cleaning, remove dust or residue from cleaned surfaces.

E. If surfaces develop rust before prime coat is applied, repeat surface preparation.

F. Prepare surface of AST[ and supports] and apply painting systems according to specifications in Division 9 Section "High-Performance Coatings" for [severe] [moderate] [mild] environment [high-gloss] [semigloss] finish for ferrous metal.

3.18 FIELD PAINTING OF ABOVEGROUND PIPING

Division 9 Sections specify paint products for various surfaces (e.g., ferrous and nonferrous metals).  For HVAC items to be field painted, choose among various application methods and coating systems (number of prime and finish coatings and coating thicknesses).  Coordinate these requirements with Architect to ensure that appropriate painting requirements are retained in these Division 9 Sections.

A. Comply with requirements in Division 9 painting Sections for painting interior and exterior fuel-oil piping.

B. Paint exposed, exterior metal piping, valves, and piping specialties, except components with factory-applied paint or protective coating.

1. Alkyd System:  MPI EXT 5.1D.

a. Prime Coat:  Alkyd anticorrosive metal primer.

For a Premium Grade system, "MPI Manual" requires intermediate coat; delete intermediate coat for a Custom Grade system.

b. Intermediate Coat:  Exterior alkyd enamel matching topcoat.

c. Topcoat:  Exterior alkyd enamel [(flat)] [(semigloss)] [(gloss)].

d. Color:  [Gray] <Insert color>.

C. Paint exposed, interior metal piping, valves, and piping specialties, except components with factory-applied paint or protective coating.

Retain one of two painting systems below or include both for Contractor option.

1. Latex Over Alkyd Primer System:  MPI INT 5.1Q.

a. Prime Coat:  [Alkyd anticorrosive] [Quick-drying alkyd] metal primer.

For a Premium Grade system, "MPI Manual" requires intermediate coat; delete intermediate coat for a Custom Grade system.

b. Intermediate Coat:  Interior latex matching topcoat.

c. Topcoat:  Interior latex [(flat)] [(low sheen)] [(eggshell)] [(satin)] [(semigloss)] [(gloss)].

d. Color:  [Gray] <Insert color>.

2. Alkyd System:  MPI INT 5.1E.

a. Prime Coat:  [Alkyd anticorrosive] [Quick-drying alkyd] metal primer.

For a Premium Grade system, "MPI Manual" requires intermediate coat; delete intermediate coat for a Custom Grade system.

b. Intermediate Coat:  Interior alkyd matching topcoat.

c. Topcoat:  Interior alkyd [(flat)] [(eggshell)] [(semigloss)] [(gloss)].

d. Color:  [Gray] <Insert color>.

D. Damage and Touchup:  Repair marred and damaged factory-applied finishes with materials and by procedures to match original factory finish.

3.19 CONCRETE BASES

Coordinate concrete work in this article with Division 3 Section "Cast-in-Place Concrete" or "Cast-in-Place Concrete (Limited Applications)."

A. Concrete Bases:  Anchor equipment to concrete base according to equipment manufacturer's written instructions and according to seismic codes at Project.

1. Construct concrete bases of dimensions indicated, but not less than 4 inches (100 mm) larger in both directions than supported unit.

2. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on [18-inch (457-mm)] <Insert dimension> centers around the full perimeter of the base.

3. Install epoxy-coated anchor bolts for supported equipment that extend through concrete base, and anchor into structural concrete floor.

4. Place and secure anchorage devices.  Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

6. Use [3000-psig (20.7-MPa)] <Insert dimension>, 28-day, compressive-strength concrete and reinforcement as specified in [Division 3 Section "Cast-in-Place Concrete."] [Division 3 Section "Cast-in-Place Concrete (Limited Applications)."]

3.20 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

Tank and pipe test pressures in this article are required by NFPA 31.  Verify requirements with authorities having jurisdiction.

Retain first subparagraph below if storage tanks do not bear the ASME code stamp as required in "Source Quality Control" Article.

1. Tanks:  Minimum hydrostatic or compressed-air test pressures for fuel-oil storage tanks that have not been factory tested and do not bear the ASME code stamp or a listing mark acceptable to authorities having jurisdiction:

a. Single-Wall Tanks:  Minimum 3 psig (20.7 kPa) and maximum 5 psig (34.5 kPa).

b. Double-Wall Tanks:

1) Inner Tanks:  Minimum 3 psig (20.7 kPa) and maximum 5 psig (34.5 kPa).

2) Interstitial Space:  Minimum 3 psig (20.7 kPa) and maximum 5 psig (34.5 kPa), or 5.3-in. Hg (18-kPa) vacuum.

c. Where vertical height of fill and vent pipes is such that the static head imposed on the bottom of the tank is greater than 10 psig (69 kPa), hydrostatically test the tank and fill and vent pipes to a pressure equal to the static head thus imposed.

d. Maintain the test pressure for one hour.

2. Piping:  Minimum hydrostatic or pneumatic test-pressures measured at highest point in system:

a. Fuel-Oil Distribution Piping:  Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [30] <Insert time> minutes.

b. Fuel-Oil, Double-Containment Piping:

1) Carrier Pipe:  Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [30] <Insert time> minutes.

2) Containment Conduit:  Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [60] <Insert time> minutes.

c. Suction Piping:  Minimum 20-in. Hg (68 kPa) for minimum [30] <Insert time> minutes.

d. Isolate storage tanks if test pressure in piping will cause pressure in storage tanks to exceed 10 psig (69 kPa).

3. Inspect and test fuel-oil piping according to NFPA 31, "Tests of Piping" Paragraph; and according to requirements of authorities having jurisdiction.

4. Test liquid-level gage for accuracy by manually measuring fuel-oil levels at not less than [three] [four] [five] <Insert number or describe procedure> different depths while filling tank and checking against gage indication.

5. Test leak-detection and monitoring system for accuracy by manually operating sensors and checking against alarm panel indication.

6. Start fuel-oil transfer pumps to verify for proper operation of pump and check for leaks.

7. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

8. Bleed air from fuel-oil piping using manual air vents.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

D. Fuel-oil piping and equipment will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

3.21 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain [liquid-level gage systems] [leak-detection and monitoring systems] [fuel-oil pumps] <Insert other>.

3.22 OUTDOOR PIPING SCHEDULE

Retain and revise applicable piping applications.  Coordinate with materials specified in Part 2.  Retain multiple materials for Contractor's option.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Underground fuel-oil piping shall be[ one of] the following.  Size indicated is carrier-pipe size.

Flexible, double-containment piping systems are available in NPS 3/4 to NPS 3 (DN 20 to DN 80).  Rigid, double-containment piping is not limited in size.

1. Flexible, double-containment piping.

2. Rigid, double-containment piping.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.  Fill and vent piping are not generally filled with fuel oil; therefore, they are not usually required to be double contained.  Verify this installation practice with authorities having jurisdiction.

B. Underground fuel-oil-tank fill and vent piping shall be[ one of] the following:

1. [NPS 2 (DN 50)] <Insert pipe size> and Smaller:  Steel pipe, steel or malleable-iron threaded fittings, and threaded joints.  Coat pipe and fittings with protective coating for steel piping.

2. [NPS 2-1/2 (DN 65)] <Insert pipe size> and Larger:  Steel pipe, steel welding fittings, and welded joints.  Coat pipe and fittings with protective coating for steel piping.

Indicate extent of containment conduit on Drawings.  Containment conduit is required for piping with insufficient depth of bury.

C. Containment Conduit:  Steel pipe with wrought-steel fittings and welded joints.  Coat pipe and fittings with protective coating for steel piping.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

D. Aboveground fuel-oil piping shall be[ one of] the following:

Because fill and vent piping do not generally contain fuel oil, double-containment piping is usually not required.  Verify requirements with authorities having jurisdiction.

1. [NPS 2 (DN 50)] <Insert pipe size> and Smaller:  Steel pipe, steel or malleable-iron threaded fittings, and threaded joints.

2. [NPS 2-1/2 (DN 65)] <Insert pipe size> and Larger:  Steel pipe, steel welding fittings, and welded joints.

Practical size limit for copper is NPS 4 (DN 100) because joints are difficult to heat evenly for brazing.  ASME B31.9 requires that copper tubing not be used at ASTs that are placed behind a dike because piping may fail during a fire.

3. [Annealed] [Drawn]-temper copper tube with wrought-copper fittings and brazed joints.

3.23 INDOOR PIPING SCHEDULE

Retain and revise applicable piping applications.  Coordinate with materials specified in Part 2.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

A. Aboveground fuel-oil piping shall be[ one of] the following:

1. [NPS 1/2 (DN 15)] <Insert pipe size> and Smaller:  [Steel pipe, steel or malleable-iron threaded fittings, and threaded joints] [Annealed-temper copper pipe, wrought copper fittings, and brazed or flared joints].

2. [NPS 5/8 to NPS 2 (DN 18 to DN 50)] <Insert pipe size>:  [Steel pipe, steel or malleable-iron threaded fittings, and threaded joints] [Drawn temper copper pipe, wrought copper fittings, and brazed joints].

Practical size limit for copper is NPS 4 (DN 100) because joints are difficult to heat evenly for brazing.

3. [NPS 2-1/2 (DN 65)] <Insert pipe size> and Larger: [Steel pipe, steel fittings, and welded or flanged joints] [Drawn temper copper pipe, wrought copper fittings, and brazed or flanged joints].

4. Steel pipe with malleable-iron fittings and threaded joints.

5. Steel pipe with wrought-steel fittings and welded joints.

Practical size limit for copper is NPS 4 (DN 100) because joints are difficult to heat evenly for brazing.

6. Annealed-temper copper tube, brass fittings, and flared joints.

7. Drawn-temper copper tubing, copper fittings, and brazed joints.

3.24 ABOVEGROUND MANUAL FUEL-OIL SHUTOFF VALVE SCHEDULE

Retain and revise applicable piping applications.  Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Distribution piping valves for pipe NPS 2 (DN 50) and smaller shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Distribution piping valves for pipe NPS 2-1/2 (DN 65) and larger shall be[ one of] the following:

1. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

2. Bronze, [nonlubricated] [lubricated] plug valve.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

C. Valves in branch piping for single appliance shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

END OF SECTION 15192

FACILITY FUEL-OIL PIPING
15192 - 1

