Copyright 2002 AIA
MASTERSPEC Full Length
12/02 (R06/06)

Copyright 2002 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15485 - ELECTRIC WATER HEATERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following electric water heaters:

Adjust list below to suit Project.

1. Household, small-capacity electric water heaters.

2. Household, storage electric water heaters.

3. Household, collector-to-tank, solar-electric water heaters.

4. Household, collector-to-tank, heat-exchanger-coil, solar-electric water heaters.

5. Flow-control, instantaneous electric water heaters.

6. Thermostat-control, instantaneous electric water heaters.

7. Light-commercial electric water heaters.

8. Commercial electric booster heaters.

9. Commercial, storage electric water heaters.

10. Compression tanks.

11. Water heater accessories.

1.3 SUBMITTALS

A. Product Data:  For each type and size of water heater indicated.  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. LEED Submittal:

1. Product Data for Prerequisite EA 2:  Documentation indicating that units comply with ASHRAE/IESNA 90.1-2004, Section 7 - "Service Water Heating."

C. Shop Drawings:  Diagram power, signal, and control wiring.

Retain paragraph below only for commercial and instantaneous electric water heaters and if certificates are required.

D. Product Certificates:  For each type of [commercial] [and] [instantaneous] electric water heater, signed by product manufacturer.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

E. Manufacturer Seismic Qualification Certification:  Submit certification that commercial water heaters, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

F. Source quality-control test reports.

G. Field quality-control test reports.

H. Operation and Maintenance Data:  For electric water heaters to include in emergency, operation, and maintenance manuals.

I. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain same type of electric water heaters through one source from a single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of electric water heaters and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EA 2 requires that water heaters comply with ASHRAE/IESNA 90.1-2004, including equipment efficiency indicated in table titled "Performance Requirements for Water Heating Equipment."

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004.

E. ASME Compliance:  Where indicated, fabricate and label commercial water heater storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

F. Comply with NSF 61, "Drinking Water System Components - Health Effects; Sections 1 through 9," for all components that will be in contact with potable water.

1.5 COORDINATION

A. Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of electric water heaters that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures including storage tank and supports.

b. Faulty operation of controls.

c. Deterioration of metals, metal finishes, and other materials beyond normal use.

Verify available warranties for units and components and insert numbers below.

2. Warranty Period(s):  From date of Substantial Completion:

a. Household Electric Water Heaters:

1) Storage Tank:  [Five] [Six] [10] <Insert number> years.

2) Controls and Other Components:  [Two] [Three] <Insert number> years.

b. Instantaneous Electric Water Heaters:  [One] [Two] [Five] <Insert number> year(s).

c. Light-Commercial Electric Water Heaters:

1) Storage Tank:  [Three] [Five] <Insert number> years.

2) Controls and Other Components:  [Two] [Three] <Insert number> years.

d. Commercial Electric Water Heaters:

1) Storage Tank:  [Three] [Five] <Insert number> years.

2) Controls and Other Components:  [Three] [Five] <Insert number> years.

e. Compression Tanks:  [One] <Insert number> year(s).

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 HOUSEHOLD ELECTRIC WATER HEATERS

Refer to the table for household electric water heaters at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Household, Small-Capacity Electric Water Heaters:  Comply with UL 174.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bradford White Corporation.

c. Controlled Energy Corporation.

d. Electric Heater Company (The); Hubbell Heaters Division.

e. GSW Water Heating Company.

f. In-Sink-Erator Div.; Emerson Electric Co.

g. Lochinvar Corporation.

h. Rheem Water Heater Div.; Rheem Manufacturing Company.

i. Ruud Water Heater Div.; Rheem Manufacturing Company.

j. Smith, A. O. Water Products Company.

k. <Insert manufacturer's name.>

Household, small-capacity electric water heaters are limited to between 1- and 5-gal. (3.8- and 18.9-L) capacity.  Verify availability if option in first subparagraph below is required.

2. Storage-Tank Construction:  Corrosion-resistant metal[ or steel with corrosion-resistant coating].

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Drain Valve:  ASSE 1005, if tank has drain outlet.  Provide hose-end drain valve in piping for water heaters without drain outlet.  Hose-end drain valves are specified in Division 15 Section "Plumbing Specialties."

Option in first subparagraph below is not applicable if applying for LEED certification.

b. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

c. Jacket:  Steel with enameled finish.

d. Heating Element:  Electric, screw-in immersion type.

e. Temperature Control:  Adjustable thermostat.

f. Safety Control:  High-temperature-limit cutoff device or system.

g. Power Supply Cord:  24 to 72 inches (610 to 1830 mm) with plug.

h. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 for combination temperature and pressure relief valves.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

If more than one household electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Heating Element:

Household, small-capacity electric water heaters have only one electrical heating element.

1) Number:  One.

2) Power Demand:  <Insert kilowatt.>

d. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

e. Electrical Characteristics:

1) Total Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] <Insert value>.

3) Phases:  Single.

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

B. Household, [Standard] [Tabletop], Storage Electric Water Heaters:  Comply with UL 174.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bradford White Corporation.

c. Electric Heater Company (The); Hubbell Heaters Division.

d. GSW Water Heating Company.

e. Heat Transfer Products, Inc.

f. HESco Industries, Inc.

g. Lochinvar Corporation.

h. Maytag Corp.; Water Heating Appliances Div.

i. Rheem Water Heater Div.; Rheem Manufacturing Company.

j. Ruud Water Heater Div.; Rheem Manufacturing Company.

k. Smith, A. O. Water Products Company.

l. State Industries, Inc.

m. Vaughn Manufacturing Corporation.

n. <Insert manufacturer's name.>

Household, storage electric water heaters are limited to between 6- and 120-gal. (22.7- and 454-L) capacity.

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

1) Standard:  Cylindrical shape.

2) Tabletop:  Rectangular shape, with flat-top work surface and raised back.

f. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

g. Heating Elements:  Two; electric, screw-in immersion type with 12 kW or less total, and wired for nonsimultaneous operation, unless otherwise indicated.

h. Temperature Control:  Adjustable thermostat for each element.

i. Safety Control:  High-temperature-limit cutoff device or system.

j. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 for combination temperature and pressure relief valves.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

If more than one household electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Jacket:  [Cylindrical] [Tabletop, rectangular] shape.

d. Heating Elements:

1) Number:  Two.

2) Power Demand Each:  <Insert kilowatt.>

e. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

f. Electrical Characteristics:

1) Total Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

C. Household, Collector-to-Tank, Solar-Electric Water Heaters:  Comply with UL 174 with piping and electrical connections for UL 1279 solar collector system.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bradford White Corporation.

c. Rheem Water Heater Div.; Rheem Manufacturing Company.

d. Ruud Water Heater Div.; Rheem Manufacturing Company.

e. <Insert manufacturer's name.>

Household, collector-to-tank solar-electric water heaters are limited to 120-gal. (454-L) capacity.

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Sensor electrical connections and tank stud for sensor.

b. Anode Rod:  Replaceable magnesium.

c. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

d. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

e. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

f. Jacket:  Steel with enameled finish.

g. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

h. Heating Element:  One; electric, screw-in immersion type with 6 kW or less.

i. Temperature Control:  Adjustable thermostat for each element.

j. Safety Control:  High-temperature-limit cutoff device or system.

k. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 for combination temperature and pressure relief valves.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

If more than one household electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Heating Element:

1) Number:  One.

2) Power Demand:  <Insert kilowatt.>

d. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

e. Electrical Characteristics:

1) Total Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

D. Household, Collector-to-Tank, Heat-Exchanger-Coil, Solar-Electric Water Heaters:  Comply with UL 174 with integral coil-type heat exchanger.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alternate Energy Technologies, LLC.

b. Electric Heater Company (The); Hubbell Heaters Division.

c. Therma-Flow/Everhot.

d. Vaughn Manufacturing Corporation.

e. <Insert manufacturer's name.>

Household, collector-to-tank, heat-exchanger-coil, solar-electric water heaters are limited to 120-gal. (454-L) capacity.

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

g. Heat Exchanger:  Corrosion-resistant-metal immersion coil.

h. Heating Element:  One; electric, screw-in immersion type with 6 kW or less.

i. Temperature Control:  Adjustable thermostat for each element.

j. Safety Control:  High-temperature-limit cutoff device or system.

k. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 for combination temperature and pressure relief valves.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

If more than one household electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Heating Element:

1) Number:  One.

2) Power Demand:  <Insert kilowatt.>

d. Heat-Exchanger Coil Surface:  <Insert sq. ft. (sq. m).>

e. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

f. Electrical Characteristics:

1) Total Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

2.3 INSTANTANEOUS ELECTRIC WATER HEATERS

Refer to the tables for commercial and instantaneous electric water heaters at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Flow-Control, Instantaneous Electric Water Heaters:  Comply with UL 499 for tankless electric (water heater) heating appliance.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Chronomite Laboratories, Inc.

b. Controlled Energy Corporation.

c. Eemax, Inc.

d. Hot Aqua, Inc.

e. IMI Waterheating, Ltd.

f. Stiebel Eltron, Inc.

g. <Insert manufacturer's name.>

2. Construction:  Copper piping or tubing complying with NSF 61 barrier materials for potable water, without storage capacity.

a. Connections:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  [150 psig (1035 kPa)] <Insert psig (kPa)>.

c. Heating Element:  Resistance heating system.

d. Temperature Control:  Flow-control fitting.

e. Safety Control:  High-temperature-limit cutoff device or system.

f. Jacket:  Aluminum or steel with enameled finish or plastic.

3. Support:  Bracket for wall mounting.

If more than one instantaneous electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Temperature Control:  Flow-control fitting.

1) Flow-Control Fitting:  <Insert gpm (L/s).>

2) Water Temperature Rise:  <Insert deg F (deg C).>

b. Electrical Characteristics:

1) Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] [277] [480] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

B. Thermostat-Control, Instantaneous Electric Water Heaters:  Comply with UL 499 for tankless electric (water heater) heating appliance.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Chronomite Laboratories, Inc.

b. IMI Waterheating, Ltd.

c. Keltech, Inc.

d. Niagara Industries, Inc.

e. <Insert manufacturer's name.>

2. Construction:  Copper piping or tubing complying with NSF 61 barrier materials for potable water, without storage capacity.

a. Connections:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  [150 psig (1035 kPa)] <Insert psig (kPa)>.

c. Heating Element:  Resistance heating system.

d. Temperature Control:  Thermostat.

e. Safety Control:  High-temperature-limit cutoff device or system.

f. Jacket:  Aluminum or steel with enameled finish or plastic.

3. Support:  Bracket for wall mounting.

If more than one instantaneous electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

4. Capacity and Characteristics:

a. Temperature Control:  Adjustable thermostat.

1) Flow Rate:  <Insert gpm (L/s) minimum.>

2) Temperature Setting:  <Insert deg F (deg C).>

b. Electrical Characteristics:

1) Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] [277] [480] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

2.4 LIGHT-COMMERCIAL ELECTRIC WATER HEATERS

Refer to the table for commercial and instantaneous electric water heaters at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Description:  Comply with UL 174 for household, storage electric water heaters.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bradford White Corporation.

c. Electric Heater Company (The); Hubbell Heaters Division.

d. GSW Water Heating Company.

e. Heat Transfer Products, Inc.

f. Lochinvar Corporation.

g. Rheem Water Heater Div.; Rheem Manufacturing Company.

h. Ruud Water Heater Div.; Rheem Manufacturing Company.

i. Smith, A. O. Water Products Company.

j. State Industries, Inc.

k. <Insert manufacturer's name.>

Light-commercial electric water heaters are limited to 120-gal. (454-L) maximum capacity.

2. Storage-Tank Construction:  Steel, vertical arrangement.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

Heating elements in first subparagraph below are limited to 12 kW total maximum.

g. Heating Elements:  Two; electric, screw-in immersion type; wired for simultaneous operation, unless otherwise indicated.

h. Temperature Control:  Adjustable thermostat for each element.

i. Safety Control:  High-temperature-limit cutoff device or system.

j. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 for combination temperature and pressure relief valves.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

Retain subparagraph below only if required.

4. Special Requirements:  NSF 5 construction with legs for off-floor installation.

If more than one light-commercial electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

5. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Heating Elements:  <Insert kilowatt> each.

d. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert deg F (deg C)>.

e. Electrical Characteristics:

1) Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] [277] [480] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

2.5 COMMERCIAL ELECTRIC WATER HEATERS

Refer to the table for commercial and instantaneous electric water heaters at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

Water heaters in first paragraph and subparagraphs below are for at least 180 deg F (82 deg C) hot-water supply to dishwashers.

A. Commercial Electric Booster Heaters:  Comply with UL 1453 requirements for booster-type water heaters.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Bradford White Corporation.

b. Coates Heater Co.

c. Electric Heater Company (The); Hubbell Heaters Division.

d. Hatco Corporation.

e. Lochinvar Corporation.

f. Rheem Water Heater Div.; Rheem Manufacturing Company.

g. Ruud Water Heater Div.; Rheem Manufacturing Company.

h. Smith, A. O. Water Products Company.

i. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [Corrosion-resistant metal] [Corrosion-resistant metal or steel] [Steel].

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

c. Insulation:  Comply with ASHRAE/IESNA 90.1.

d. Jacket:  Rectangular shaped, with stainless-steel front panel, unless otherwise indicated.

e. Heating Elements:  Electric, screw-in or bolt-on immersion type arranged in multiples of three.

1) Option:  Booster heaters with 9 kW or less total may have 2 or 3 elements.

2) Staging:  Input not exceeding [18 kW] <Insert kW> per step.

f. Temperature Control:  Adjustable thermostat, to setting of at least 180 deg F (82 deg C).

g. Safety Controls:  High-temperature-limit and low-water cutoff devices or systems.

h. Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3, combination temperature and pressure relief valve.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

i. Gages:  Combination temperature and pressure type or separate thermometer and pressure gage.

4. Special Requirements:  NSF 5 construction with [brackets for undercounter] [legs for floor] installation.

If more than one commercial electric water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule water heaters on Drawings.

5. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [40 deg F (22 deg C)] [50 deg F (28 deg C)] [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [140 deg F (60 deg C)] [180 deg F (82 deg C)] <Insert deg F (deg C)>.

d. Number of Heating Elements:  [Two] [Three] [Six] [Nine] <Insert number>.

1) Number of Stages:  [One] [Two] [Three] [Four] <Insert number>.

2) Kilowatt per Stage:  <Insert kilowatt.>

e. Electrical Characteristics:

1) Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] [277] [480] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

B. Commercial, Storage Electric Water Heaters:  Comply with UL 1453 requirements for storage-tank-type water heaters.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bock Water Heaters, Inc.

c. Bradford White Corporation.

d. Cemline Corporation.

e. Electric Heater Company (The); Hubbell Heaters Division.

f. GSW Water Heating Company.

g. HESco Industries, Inc.

h. Lochinvar Corporation.

i. Precision Boilers.

j. PVI Industries, LLC.

k. RECO USA.

l. Rheem Water Heater Div.; Rheem Manufacturing Company.

m. Ruud Water Heater Div.; Rheem Manufacturing Company.

n. Smith, A. O. Water Products Company.

o. State Industries, Inc.

p. Vaughn Manufacturing Corporation.

q. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [ASME] [Non-ASME]-code, steel [horizontal] [vertical] arrangement.

a. Tappings:  Factory fabricated of materials compatible with tank and piping connections.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Pressure Rating:  [150 psig (1035 kPa)] <Insert psig (kPa)>.

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

c. Insulation:  Comply with ASHRAE/IESNA 90.1.

d. Jacket:  Steel with enameled finish.

e. Heating Elements:  Electric, screw-in or bolt-on immersion type arranged in multiples of three.

1) Staging:  Input not exceeding [18 kW] <Insert kW> per step.

f. Temperature Control:  Adjustable thermostat.

g. Safety Controls:  High-temperature-limit and low-water cutoff devices or systems.

h. Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Special Requirements:  NSF 5 construction.

5. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one commercial electric water heater is required on Project, delete subparagraphs and associated subparagraphs below and schedule water heaters on Drawings.

6. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [40 deg F (22 deg C)] [50 deg F (28 deg C)] [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [140 deg F (60 deg C)] [180 deg F (82 deg C)] <Insert deg F (deg C)>.

d. Number of Heating Elements:  [Two] [Three] [Six] [Nine] <Insert number>.

1) Number of Stages:  [One] [Two] [Three] [Four] <Insert number>.

2) Kilowatt per Stage:  <Insert kilowatt.>

e. Electrical Characteristics:

1) Power Demand:  <Insert kilowatt.>

2) Volts:  [120] [240] [277] [480] <Insert value>.

3) Phases:  [Single] [Three].

4) Hertz:  60.

5) Full-Load Amperes:  <Insert value.>

6) Minimum Circuit Ampacity:  <Insert value.>

7) Maximum Overcurrent Protection:  <Insert value.>

2.6 COMPRESSION TANKS

Retain this Article only if small, non-ASME-code, diaphragm tanks with a capacity of 25 gal. (95 L) or less are required.  Small tanks are usually available with 150-psig (1035-kPa) working-pressure rating.  Large tanks are usually available with 100-psig (690-kPa) working-pressure rating.  A multiple small-tank arrangement may be used to match system pressure and volume requirements.  Other compression tanks are specified in Division 15 Section "Potable-Water Storage Tanks."

A. Description:  Steel pressure-rated tank constructed with welded joints and factory-installed butyl-rubber diaphragm.  Include air precharge to minimum system-operating pressure at tank.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AMTROL Inc.

b. Armstrong Pumps, Inc.

c. Flexcon Industries.

d. Honeywell Sparco.

e. Myers, F. E.; Pentair Pump Group (The).

f. Smith, A. O.; Aqua-Air Div.

g. State Industries, Inc.

h. Taco, Inc.

i. Watts Regulator Co.

j. Wessels Co.

k. <Insert manufacturer's name.>

2. Construction:

a. Tappings:  Factory-fabricated steel, welded to tank before testing and labeling.  Include ASME B1.20.1, pipe thread.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

c. Air-Charging Valve:  Factory installed.

If more than one compression tank is required on Project, delete subparagraph and associated subparagraphs below and schedule tanks on Drawings.

3. Capacity and Characteristics:

a. Working-Pressure Rating:  [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert psig (kPa)>.

b. Capacity Acceptable:  [2 gal. (7.6 L)] [4 gal. (15.1 L)] [7 gal. (26.5 L)] [10 gal. (37.9 L)] <Insert volume> minimum.

c. Air Precharge Pressure:  <Insert system pressure.>

2.7 WATER HEATER ACCESSORIES

A. Combination Temperature and Pressure Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valves with sensing element that extends into storage tank.

B. Pressure Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3.  Include pressure setting less than water heater working-pressure rating.

Indicate on Drawings where each type of water heater support in four paragraphs below is required.  Delete support types not required.  Water heaters can also be installed at or above ceilings on suspended platforms or brackets.

C. Water Heater Stand and Drain-Pan Units:  High-density-polyethylene-plastic, 18-inch- (457-mm-) high, enclosed-base stand complying with IAPMO PS 103 and IAS No. 2.  Include integral or separate drain pan with raised edge and NPS 1 (DN 25) drain outlet with ASME B1.20.1 pipe thread.

D. Water Heater Stands:  Water heater manufacturer's factory-fabricated steel stand for floor mounting and capable of supporting water heater and water.  Include dimension that will support bottom of water heater a minimum of 18 inches (457 mm) above the floor.

E. Water Heater Mounting Brackets:  Water heater manufacturer's factory-fabricated steel bracket for wall mounting and capable of supporting water heater and water.

F. Drain Pans:  Corrosion-resistant metal with raised edge.  Include dimensions not less than base of water heater and include drain outlet not less than NPS 3/4 (DN 20).

Retain first paragraph below only if required for multiple water heater arrangement.  Verify availability.  Some water heater manufacturers can provide piping manifold kits for their water heaters.  Larger manifolds can be field fabricated from water piping and valves.

G. Piping Manifold Kits:  Water heater manufacturer's factory-fabricated inlet and outlet piping arrangement for multiple-unit installation.  Include piping and valves for field assembly that are capable of isolating each water heater and of providing balanced flow through each water heater.

Option in first paragraph below is not applicable if applying for LEED certification.

H. Piping-Type Heat Traps:  Field-fabricated piping arrangement according to ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

I. Water Regulators:  ASSE 1003, water-pressure reducing valve.  Set at 25-psig- (172.5-kPa-) maximum outlet pressure, unless otherwise indicated.

J. Shock Absorbers:  ASSE 1010 or PDI WH 201, Size A water hammer arrester.

2.8 SOURCE QUALITY CONTROL

A. Test and inspect water heater storage tanks, specified to be ASME-code construction, according to ASME Boiler and Pressure Vessel Code.

Retain first paragraph below if tank testing by manufacturer is required.  Retain option if testing of only commercial water-heater tanks is required.

B. Hydrostatically test[ commercial] water heater storage tanks before shipment to minimum of one and one-half times pressure rating.

C. Prepare test reports.

PART 3 -  EXECUTION

3.1 WATER HEATER INSTALLATION

A. Install commercial water heaters on concrete bases.

1. Exception:  Omit concrete bases for commercial water heaters if installation on stand, bracket, suspended platform, or direct on floor is indicated.

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.  Concrete bases are usually not provided for household or light-commercial water heaters in finished spaces.

2. Concrete base construction requirements are specified in Division 15 Section "Basic Mechanical Materials and Methods."

B. Install water heaters level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

Retain first paragraph below only if seismic restraint is required.

C. Install seismic restraints for[ light-commercial and] commercial water heaters.  Anchor to substrate.

D. Install combination temperature and pressure relief valves in top portion of storage tanks.  Use relief valves with sensing elements that extend into tanks.  Extend commercial-water-heater relief-valve outlet, with drain piping same as domestic water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

E. Install[ combination temperature and] pressure relief valves in water piping for water heaters without storage.  Extend commercial-water-heater relief-valve outlet, with drain piping same as domestic water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

F. Install water-heater drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for water heaters that do not have tank drains.  Refer to Division 15 Section "Plumbing Specialties" for hose-end drain valves.

G. Install thermometer on outlet piping of water heaters.  Refer to Division 15 Section "Meters and Gages" for thermometers.

Retain paragraph below only if required.

H. Install thermometers on inlet and outlet piping of household, collector-to-tank, solar-electric water heaters.  Refer to Division 15 Section "Meters and Gages" for thermometers.

Retain first paragraph below only if required.

I. Install pressure gage(s) on[ inlet and] outlet of commercial electric water- heater piping.  Refer to Division 15 Section "Meters and Gages" for pressure gages.

J. Assemble and install inlet and outlet piping manifold kits for multiple water heaters.  Fabricate, modify, or arrange manifolds for balanced water flow through each water heater.  Include shutoff valve, thermometer in each water heater inlet and outlet, and throttling valve in each water heater outlet.  Refer to Division 15 Section "Valves" for general-duty valves and to Division 15 Section "Meters and Gages" for thermometers.

K. Install water regulator, with integral bypass relief valve, in booster-heater inlet piping and water hammer arrester in booster-heater outlet piping.

L. Install piping-type heat traps on inlet and outlet piping of water heater storage tanks without integral or fitting-type heat traps.

M. Fill water heaters with water.

Retain paragraph below only if required.

N. Charge compression tanks with air.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to water heaters to allow service and maintenance.  Arrange piping for easy removal of water heaters.

C. Ground equipment according to Division 16 Section "Grounding and Bonding."

D. Connect wiring according to Division 16 Section "Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with paragraph above.  Edit to suit Project.

1. Leak Test:  After installation, test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, confirm proper operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace water heaters that do not pass tests and inspections and retest as specified above.

3.4 DEMONSTRATION

Retain this Article for commercial and instantaneous electric water heaters.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain [commercial] [and] [instantaneous] electric water heaters.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15485END OF SECTION 15485

ELECTRIC WATER HEATERS
15485 - 1

