Copyright 2004 AIA
MASTERSPEC Full Length
03/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15512 - CAST-IRON BOILERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged cast-iron boilers, trim, and accessories for generating [hot water] [steam] with the following configurations and burners:

Adjust list below to suit Project.

1. [Factory] [Field] assembled.

2. [Atmospheric gas] [Sealed-combustion, gas] [Forced-draft, gas] [Oil] [Combination gas and oil] burner.

1.3 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other work.

Retain first subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Manufacturer Seismic Qualification Certification:  Submit certification that boiler, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For boilers, components, and accessories to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

H. Other Informational Submittals:

1. Startup service reports.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1 Compliance:  Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Delete first paragraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

D. DOE Compliance:  Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

E. I=B=R Compliance:  Boilers shall be tested and rated according to HI's "Rating Procedure for Heating Boilers" and "Testing Standard for Commercial Boilers," with I=B=R emblem on a nameplate affixed to boiler.

Retain second option in paragraph below for combination burners.

F. UL Compliance:  Test boilers for compliance with [UL 726, "Oil-Fired Boiler Assemblies] [UL 726, "Oil-Fired Boiler Assemblies," and UL 795, "Commercial-Industrial Gas Heating Equipment] [UL 795, "Commercial-Industrial Gas Heating Equipment]." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace controls and heat exchangers of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Controls:  [Two] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Heat Exchangers:  [Five] [10] [20] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 15 Section "Heating Boilers and Accessories" for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Burnham Hydronics.

2. Crown Boiler Co.

3. Hydrotherm, Inc.; a division of Mestek, Inc.

4. Lennox Industries Inc.

5. Peerless Boilers.

6. Slant/Fin Corp.

7. Smith Cast Iron Boilers.

8. Viessmann Manufacturing Co. (US) Inc.

9. Weil-McLain; a United Dominion Company.

10. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory fabricated and [field ]assembled.

Retain one of two subparagraphs below.  Retain first for factory-assembled boilers and second for field-assembled boilers.

1. Cast-iron sections shall be sealed pressure tight and held together with tie rods[ set on an insulated steel base]; including insulated jacket and flue-gas vent connection.

2. Ship cast-iron sections disassembled with all materials and equipment, including seals, tie rods, and insulated jacket and flue-gas vent connection for field assembly.

B. Cast-Iron Section Design:

1. Configuration:  Wet [base] [back] [leg].

2. Number of Passes:  [Single] [Multiple].

3. Sectional Joints:  High-temperature sealant to seal flue-gas passages not in contact with heating medium, [tapered cast-iron push nipples,] [O-ring gaskets,] [fiber roping,] and held together with tie rods.

4. Drain and blowdown tappings.

5. Return injection tube to equalize water flow to all sections.

6. Crown inspection tappings with brass plugs.

Separator in subparagraph below is available only in small residential-size boilers.  Verify availability with manufacturer.

7. Built-in air separator.

C. Combustion Chamber:  Equipped with [ceramic-fiber target wall] [refractory] [insulation] [and] flame observation ports, front and back.

D. Casing:

1. Jacket:  [Galvanized ]sheet metal, with snap-in or interlocking closures and [baked-enamel] [powder-coated] protective finish.

2. Insulation:  Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, mineral-fiber insulation surrounding the heat exchanger.

Feature in first subparagraph below is unique for some boiler manufacturers.

3. Combustion Chamber Access:  Refractory lined, hinged, front.

4. Access:  For cleaning between cast-iron sections.

5. Draft Hood:  Flue canopy and [top] [rear] flue connection shall be constructed of [aluminized] [stainless] steel containing adjustable outlet damper assembly.

Delete first subparagraph below if boiler design permits.

6. Insulated base constructed of aluminized steel to permit boiler to be installed on combustible floor.

7. Mounting Frame:  Steel rails to mount assembled boiler package on concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when mounting base is anchored to building structure.

Cabinet in subparagraph below is available only in residential natural-draft boilers.

8. Control Cabinet:  Sheet metal casing shall cover all controls, gas train, and burner.

Delete paragraph below if boiler has forced-draft burner.  If retaining, verify draft-diverter configuration with manufacturer.

E. Draft Diverter:  [Steel assembly integral with boiler casing] [Separate galvanized-steel assembly].

Retain one of five "Burner" articles below.

2.3 BURNER

Retain this Article for atmospheric gas burners.

A. Burner Tubes and Orifices:  [Stainless steel] [Cast iron], for [natural] [propane] gas.

Retain one of two "Gas Train" paragraphs below.  First applies to commercial boilers; second applies to residential boilers.  Retain any of three control sequences with any of four safety requirements.

B. Gas Train:  Control devices and [full-modulation] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

C. Gas Train:  Combination gas valve with manual shutoff, pressure regulator, and pilot adjustment.

D. Pilot:  [Standing] [Intermittent-electric-spark] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

2.4 BURNER

Retain this Article for residential-size boilers with sealed-combustion burners.

A. Burner Tubes and Orifices:  [Stainless steel] [Cast iron], for [natural] [propane] gas.

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

C. Gas Train:  Combination gas valve with manual shutoff, pressure regulator, and pilot adjustment.

D. Pilot:  [Standing] [Intermittent-electric-spark] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

2.5 BURNER

Retain this Article for forced-draft burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for [natural] [propane] gas.

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

D. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

E. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert amount> ppm.

2.6 BURNER

Retain this Article for oil burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for fuel oil.

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

1. Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 15-inch Hg (50.7-kPa) vacuum.

2. Oil Piping Specialties:

a. Suction-line, manual, gate valve.

b. Removable-mesh oil strainer.

c. 0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

d. 0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

e. Nozzle-line, solenoid-safety-shutoff oil valve.

D. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid using [cadmium sulfide] [UV scanner] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

E. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [30] <Insert amount> ppm.

2.7 BURNER

Retain this Article for combination gas and oil burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for fuel oil and [natural] [propane] gas.

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

1. Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 15-inch Hg (50.7-kPa) vacuum.

2. Oil Piping Specialties:

a. Suction-line, manual, gate valve.

b. Removable-mesh oil strainer.

c. 0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

d. 0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

e. Nozzle-line, solenoid-safety-shutoff oil valve.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

D. Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

E. Gas Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

F. Oil Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [UV scanner] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

G. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert amount> ppm.

Retain one of two "Trim" articles below.

2.8 TRIM

Retain this Article for hot-water boilers.

A. Include devices sized to comply with ANSI B31.9, "Building Services Piping."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers:  Operating[, firing rate,] and high limit.

C. Safety Relief Valve:  ASME rated.

D. Pressure and Temperature Gage:  Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent:  [Automatic] [Manual].

F. Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end gate valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic water heaters.

G. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of cast-iron sections and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.9 TRIM

Retain this Article for steam boilers.

A. Include devices sized to comply with ANSI B31.9, "Building Services Piping."

Retain option in paragraph below if using modulating or low-high-low firing sequence.

B. Pressure Controllers:  Operating[, firing rate,] and high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of boiler.  Coordinate with Division 15 Section "Steam and Condensate Piping."

C. Safety Relief Valve:

1. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

2. Description:  Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage:  Minimum 3-1/2-inch (89-mm) diameter.  Gage shall have normal operating pressure about 50 percent of full range.

E. Water Column:  Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves:  Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

G. Blowdown Valves:  Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.

H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size as or larger than nozzle.  Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Factory-installed, stop-check valve and stop valve at boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating stop-check valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic water heaters.

J. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of cast-iron sections and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.10 CONTROLS

Retain paragraph below if controls are specified in Division 15 Section "HVAC Instrumentation and Controls."

A. Refer to Division 15 Section "HVAC Instrumentation and Controls."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust:  Set points shall be adjustable.

Retain two subparagraphs below for steam boilers.

3. Operating Pressure Control:  Factory wired and mounted to cycle burner.

4. Low-Water Cutoff and Pump Control:  Cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

5. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

6. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

7. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

a. Include automatic, alternating-firing sequence for multiple boilers.

C. Burner Operating Controls:  To maintain safe operating conditions, burner safety controls limit burner operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design [temperature] [pressure].

In subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

2. Low-Water Cutoff Switch:  [Electronic] [Float and electronic] probe shall prevent burner operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

First two subparagraphs below apply to atmospheric burners.  Some boilers may be equipped with only one of two switches below.  Verify availability with boiler manufacturer.

3. Blocked Vent Safety Switch:  Manual-reset switch factory mounted on draft diverter.

4. Rollout Safety Switch:  Factory mounted on boiler combustion chamber.

5. Audible Alarm:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

D. Building Automation System Interface:  Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring:  On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control:  On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.

2. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation.  Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.11 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article.  Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

B. Single-Point Field Power Connection:  Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

1. House in NEMA 250, Type [1] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install factory wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.12 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

A. Heating Medium:  [Hot water] [Steam].

Retain one of first two paragraphs below.  Retain first for hot-water boilers and second for steam boilers.  For steam boilers, limit steam pressure to 15 psig (104 kPa) or less.

B. Design Water Pressure Rating:  [30 psig (207 kPa)] [50 psig (345 kPa)] [80 psig (550 kPa)] <Insert pressure rating>.

C. Design Steam Pressure Rating:  [Steam, 15 psig (104 kPa)] <Insert pressure rating>.

D. Safety Relief Valve Setting:  <Insert psig (kPa).>

Retain four paragraphs below for hot-water boilers.

E. Entering-Water Temperature:  <Insert deg F (deg C).>

F. Leaving-Water Temperature:  <Insert deg F (deg C).>

G. Design Water Flow Rate:  <Insert gpm (L/s).>

H. Design Pressure Drop:  <Insert psig (kPa).>

Retain two paragraphs below for steam boilers.

I. Steam Operating Pressure:  <Insert psig (kPa).>

J. Steam Flow Rate:  <Insert lb/h (kg/s).>

Retain one of first three paragraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

K. Minimum Efficiency AFUE:  <Insert value> percent.

L. Minimum Thermal Efficiency:  <Insert value> percent.

M. Minimum Combustion Efficiency:  <Insert value> percent.

N. Number of Passes:  [One] [Two] <Insert number>.

Retain one of first four paragraphs below.  Retain one of first three input rating methods for gas.

O. AGA Input:  <Insert MBh (kW).>

P. I=B=R Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

Q. Gas Input:  <Insert cfh (mL/s).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

R. Oil Input:  <Insert gph (mL/s).>

Retain one of five paragraphs below for rating methods.

S. AGA Output Capacity:  <Insert MBh (kW).>

T. DOE Output Capacity:  <Insert MBh (kW).>

U. Net I=B=R Output Capacity:  <Insert MBh (kW).>

V. Gross I=B=R Output Capacity:  <Insert MBh (kW).>

W. Equivalent Direct Radiation:  <Insert EDR (W).>

Retain paragraph and subparagraphs below if boiler is equipped with tankless water heater.

X. Tankless Water Heater:

1. Design Water Flow:  <Insert gpm (L/s).>

2. Design Pressure Drop:  <Insert psig (kPa).>

3. Entering-Water Temperature:  <Insert deg F (deg C).>

4. Leaving-Water Temperature:  <Insert deg F (deg C).>

Consider impact of site altitude on fan and motor.

Y. Blower:

1. Motor Horsepower:  <Insert value.>

2. RPM:  <Insert value.>

Z. Electrical Characteristics:

1. Volts:  [115] [208] [230] [460] <Insert value> V.

2. Phase:  [Single] [Three].

3. Hertz:  [50] [60].

4. Full-Load Amperes:  <Insert value.>

5. Minimum Circuit Ampacity:  <Insert value.>

6. Maximum Overcurrent Protection:  <Insert amperage.>

2.13 SOURCE QUALITY CONTROL

Retain this Article for factory-assembled boilers.  Factory tests are an additional cost item.

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

B. Burner and Hydrostatic Test:  Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

Retain paragraph below if Owner wants to witness source quality-control testing.

C. Allow Owner access to source quality-control testing of boilers.  Notify Architect 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Examine mechanical spaces for suitable conditions where boilers will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Coordinate selection of device and deflection in first paragraph below with Division 15 Section "Mechanical Vibration and Seismic Controls."

B. Vibration Isolation:  Elastomeric [isolator pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Install gas-fired boilers according to NFPA 54.

Retain paragraph above for gas-fired boilers and paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

D. Install oil-fired boilers according to NFPA 31.

Delete first paragraph below if boiler is delivered fully assembled.

E. Assemble boiler sections in sequence and seal between each section.

F. Assemble and install boiler trim.

G. Install electrical devices furnished with boiler but not specified to be factory mounted.

H. Install control wiring to field-mounted electrical devices.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect gas piping to boiler gas-train inlet with union.  Piping shall be at least full size of gas train connection.  Provide a reducer if required.

Retain paragraph above for gas-fired boilers and first paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

D. Connect oil piping full size to burner inlet with shutoff valve and union.

E. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

F. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

G. Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 15 Section "Steam and Condensate Piping" or "Hydronic Piping."

H. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

I. Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

J. Connect breeching full size to boiler outlet.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for venting materials.

K. Install flue-gas recirculation duct from vent to burner.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for recirculation duct materials.

L. Ground equipment according to Division 16 Section "Grounding and Bonding."

M. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

3. Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

a. Burner Test:  Adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency.

b. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and [water temperature] [steam pressure].

c. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments:  When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.

E. Performance Tests:

1. Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

2. Boilers shall comply with performance requirements indicated, as determined by field performance tests.  Adjust, modify, or replace equipment to comply.

3. Perform field performance tests to determine capacity and efficiency of boilers.

a. For dual-fuel boilers, perform tests for each fuel.

b. Test for full capacity.

c. Test for boiler efficiency at [low fire 20, 40, 60, 80, 100, 80, 60, 40, and 20] <Insert range> percent of full capacity.  Determine efficiency at each test point.

4. Repeat tests until results comply with requirements indicated.

5. Provide analysis equipment required to determine performance.

6. Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

7. Notify Architect in advance of test dates.

8. Document test results in a report and submit to Architect.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[  Video training sessions.] Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15512END OF SECTION 15512

CAST-IRON BOILERS
15512 - 1

