Copyright 2004 AIA
MASTERSPEC Full Length
03/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15518 - FIRE-TUBE BOILERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, factory-fabricated and -assembled boilers, trim, and accessories for generating [hot water] [steam] with the following configurations and burners:

Adjust list below to suit Project.

1. [Horizontal, fire-tube] [Vertical, fire-tube] [Fire-box] boiler.

2. [Gas] [Oil] [Combination gas and oil] burner.

1.3 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

Retain subparagraph below if equipment includes wiring.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Manufacturer Seismic Qualification Certification:  Submit certification that boiler, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For boilers, components, and accessories to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

H. Other Informational Submittals:

Retain first subparagraph below for steam boilers operating at more than 15 psig (104 kPa) or hot-water boilers operating at more than 160 psig (1100 kPa) or 250 deg F (120 deg C).

1. ASME Stamp Certification and Report:  Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

2. Startup service reports.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1 Compliance:  Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Retain second option in paragraph below for combination burners.

D. UL Compliance:  Test Boilers for compliance with [UL 726, "Oil-Fired Boiler Assemblies."] [UL 726, "Oil-Fired Boiler Assemblies" and UL 795, "Commercial-Industrial Gas Heating Equipment."] [UL 795, "Commercial-Industrial Gas Heating Equipment."] Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace front- and rear-door refractories and heat exchangers of boilers that fail in materials or workmanship within specified warranty period.

Retain subparagraph below for horizontal, fire-tube and fire-box boilers only.  The need for a refractory warranty depends on boiler design and is intended more for dryback boilers.  Although front- and rear-door refractory warranties are available, a refractory warranty could penalize dryback boilers if both a dryback and a wetback boiler are allowed.  Warranty should be reviewed with Owner and specified only when requested by Owner.  Consult manufacturer to determine necessity for and availability of this warranty.

1. Horizontal, Fire-Tube and Fire-Box Boilers:  Refractory in front and rear doors, [10] <Insert number> years from date of startup by factory-authorized personnel.

Retain subparagraph below for vertical, fire-tube boilers only.

2. Vertical, Fire-Tube Boilers and Heat Exchanger:  [Five] <Insert number> years from date of Substantial Completion, if following water-treatment program recommended by manufacturer.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 15 Section "Heating Boilers and Accessories" for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Retain list below for horizontal, fire-tube boilers.

1. AESYS Technologies, LLC.

2. Burnham Hydronics.

3. Cleaver-Brooks; div. of Aqua-Chem, Inc.

4. Hurst Boiler & Welding Company, Inc.

5. Iron Fireman Combustion Products.

6. Lattner Boiler Manufacturing.

7. L.E.S., Inc.

8. Sellers Engineering Co.

9. Superior Boiler Works, Inc.

10. <Insert manufacturer's name.>

Retain list below for vertical, fire-tube boilers.

11. Columbia Boiler Company.

12. Fulton Boiler Works, Inc.

13. Hurst Boiler & Welding Company, Inc.

14. Lattner Boiler Manufacturing.

15. L.E.S., Inc.

16. Patterson-Kelley.

17. Precision Boilers.

18. PVI Industries, LLC.

19. <Insert manufacturer's name.>

Retain list below for fire-box boilers.

20. Hurst Boiler & Welding Company, Inc.

21. L.E.S., Inc.

22. <Insert manufacturer's name.>

Retain one of three "Manufactured Units" articles below.

2.2 MANUFACTURED UNITS

This Article is for horizontal, fire-tube boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, horizontal, fire-tube boilers with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, water supply and return connections, and controls.

B. Pressure Vessel Design:  Straight, steel tubes [rolled] [welded] into steel headers.  [Three] [Four] passes with [dry] [wet]-back design.  Minimum heat-exchanger surface of 5 sq. ft./bhp (2.1 sq. m/10 kW).  Include the following accessories:

1. Handholes for water-side inspections.

2. Lifting lugs on top of boiler.

3. Minimum NPS 1 (DN 25) hose-end drain valves at shell low point.

Retain two subparagraphs below for hot-water boilers only.

4. Tappings or flanges for supply- and return-water piping.

5. Built-in air separator.

Retain two subparagraphs below for steam boilers only.

6. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

7. Tappings for steam supply, makeup, level controls, and chemical treatment.

Some boiler designs do not use refractory to insulate the doors.  Verify door insulation with manufacturer.

C. Front and Rear Doors:

1. [Bolted] [Hinged] [Davited], sealed with heat-resistant gaskets and fastened with lugs and cap screws.

2. Designed so tube sheets and flues are fully accessible for inspection or cleaning when doors are open.

3. Include observation ports in doors at both ends of boiler for inspection of flame conditions.

4. Door [refractory] [insulation] shall be accessible for inspection and maintenance.

D. Casing:

1. Insulation:  Minimum 2-inch- (50-mm-) thick, mineral-fiber insulation surrounding the boiler shell.

2. Flue Connection:  Flange at top of boiler.

3. Jacket:  [Galvanized sheet] [Sheet] metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

4. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when mounting base is anchored to building structure.

Select one of four options in subparagraph below.  Type 1 is the most common, and Type 12 is second.  Type 4X is used primarily in corrosive environments.

5. Control Compartment Enclosure:  NEMA 250, Type [1] [4] [4X] [12] <Insert type>.

Retain paragraph below if required by stack draft design conditions.

E. Barometric Damper:  Galvanized-steel assembly with flue-gas thermometer having a minimum 3-1/2-inch- (89-mm-) diameter dial.

2.3 MANUFACTURED UNITS

This Article is for vertical, fire-tube boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, vertical, fire-tube boilers with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, water supply and return connections, and controls.

B. Pressure Vessel Design:  Straight, steel pipe welded in a concentric pattern to separate flue-gas and heating media to form [two] [four] passes with welded fins to improve heat transfer in secondary flue-gas passages.  Include the following accessories:

1. Handholes for water-side inspections.

2. Lifting lugs on top of boiler.

3. Minimum NPS 1 (DN 25) hose-end drain valves at water passage low point.

Retain two subparagraphs below for hot-water boilers only.

4. Tappings or flanges for supply- and return-water piping.

5. Built-in air separator.

Retain two subparagraphs below for steam boilers only.

6. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

7. Tappings for steam supply, makeup, level controls, and chemical treatment.

C. Combustion Chamber:  Equipped with flame retainer to lengthen flame-residence time.

D. Casing:

1. Insulation:  Minimum 4-inch- (100-mm-) thick, mineral-fiber insulation surrounding the heat exchanger and combustion chamber.

2. Flue Connection:  Top connection, constructed of [aluminized] [stainless] steel.

Retain one of first two subparagraphs below.

3. Jacket:  Mirror-finish stainless steel with screw-fastened closures.

4. Jacket:  [Galvanized sheet] [Sheet] metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

5. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when mounting base is anchored to building structure.

Select one of four options in subparagraph below.  Type 1 is the most common, and Type 12 is second.  Type 4X is used primarily in corrosive environments.

6. Control Compartment Enclosure:  NEMA 250, Type [1] [4] [4X] [12] <Insert type>.

Retain paragraph below if required by stack draft design conditions.

E. Barometric Damper:  Galvanized-steel assembly with flue-gas thermometer having a minimum 3-1/2-inch- (89-mm-) diameter dial.

2.4 MANUFACTURED UNITS

This Article is for fire-box boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, fire-box boilers with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, water supply and return connections, and controls.

B. Pressure Vessel Design:  Straight, steel tubes [rolled] [welded] into steel headers.  Three passes with wet-back design.  Minimum heat-exchanger surface of 5 sq. ft./bhp (2.1 sq. m/10 kW).  Include the following features and accessories:

1. Tube Size and Thickness:  [Minimum NPS 2 (DN 50), minimum 0.105 inch (2.667 mm) thick] <Insert size and thickness>.

2. Brass washout plugs.

3. Steel turbulators.

4. Lifting lugs on top of boiler.

5. Minimum NPS 1 (DN 25) hose-end drain valves at shell low point.

Retain two subparagraphs below for hot-water boilers only.

6. Tappings or flanges for supply- and return-water piping.

7. Built-in air separator.

Retain two subparagraphs below for steam boilers only.

8. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

9. Tappings for steam supply, makeup, level controls, and chemical treatment.

C. Combustion Chamber:  Welded steel, [waterwall and -floor design] [water-leg design with refractory insulation poured in the floor].  Flame observation port.

D. Casing:

1. Insulation:  Minimum 2-inch- (50-mm-) thick, [foil-backed, ]mineral-fiber insulation surrounding the boiler shell.

2. Insulated removable smoke boxes and reversing chamber cover.

3. Flue Connection:  Steel [top] [rear].

4. Jacket:  Sheet metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

Select one of five options in first subparagraph below.  Type 1 is the most common, and Type 12 is second.  Type 4X is used primarily in corrosive environments.

5. Control Compartment Enclosure:  NEMA 250, Type [1] [1A] [4] [4X] [12] <Insert type>.

6. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when mounting base is anchored to building structure.

Retain paragraph below if required by stack draft design conditions.

E. Barometric Damper:  Galvanized-steel assembly with flue-gas thermometer having a minimum 3-1/2-inch- (89-mm-) diameter dial.

Retain one of three "Burner" articles below.

2.5 BURNER

Retain this Article for forced-draft gas burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for [natural] [propane] gas.[  Mount burner on hinged access door to permit access to combustion chamber.]

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

D. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

E. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert value> ppm.

2.6 BURNER

Retain this Article for oil burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for fuel oil.[  Mount burner on hinged access door to permit access to combustion chamber.]

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

1. Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 15-inch Hg (50.7-kPa) vacuum.

2. Oil Piping Specialties:

a. Suction-line, manual, gate valve.

b. Removable-mesh oil strainer.

c. 0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

d. 0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

e. Nozzle-line, solenoid-safety-shutoff oil valve.

D. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [UV scanner] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

E. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [30] <Insert value> ppm.

2.7 BURNER

Retain this Article for combination gas and oil burners.

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for fuel oil and [natural] [propane] gas.[  Mount burner on hinged access door to permit access to combustion chamber.]

B. Blower:  Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 15 Section "Motors."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

C. Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

1. Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 15-inch Hg (50.7-kPa) vacuum.

2. Oil Piping Specialties:

a. Suction-line, manual, gate valve.

b. Removable-mesh oil strainer.

c. 0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

d. 0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

e. Nozzle-line, solenoid-safety-shutoff oil valve.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

D. Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

E. Gas Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

F. Oil Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [UV scanner] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

G. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert value> ppm.

Retain one of two "Trim" articles below.

2.8 TRIM

Retain this Article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers:  Operating[, firing rate,] and high limit.

C. Safety Relief Valve:  ASME rated.

D. Pressure and Temperature Gage:  Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent:  [Automatic] [Manual].

F. Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end gate valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic water heaters.

G. Tankless Heater:  [Carbon-steel] [Bronze] header with copper-tube heat exchanger, mounted in a port of upper drum and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.9 TRIM

Retain this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in paragraph below if using modulating or low-high-low firing sequence.

B. Pressure Controllers:  Operating[, firing rate,] and high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of boiler.  Coordinate with Division 15 Section "Steam and Condensate Piping."

C. Safety Relief Valve:

1. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

2. Description:  Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage:  Minimum 3-1/2-inch (89-mm) diameter.  Gage shall have normal operating pressure about 50 percent of full range.

E. Water Column:  Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves:  Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves:  Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.[  Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]

H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle.  Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Factory-installed, stop-check valve and stop valve for field installation at boiler outlet with free-blow drain valve for field installation between the two valves and visible when operating stop-check valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic water heaters.

J. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in a port of upper manifold and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.10 CONTROLS

Retain paragraph below if controls are specified in Division 15 Section "HVAC Instrumentation and Controls."

A. Refer to Division 15 Section "HVAC Instrumentation and Controls."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust:  Set points shall be adjustable.

Retain first two subparagraphs below for steam boilers.

3. Operating Pressure Control:  Factory wired and mounted to cycle burner.

Continuous operating feedwater pump operation with a modulating valve is a control application more commonly used for large boiler applications.

4. Low-Water Cutoff and Pump Control:  [Cycle feedwater pump(s)] [Operate feedwater pump(s) continuously and modulate valve] for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

5. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

6. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

7. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

a. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

C. Burner Operating Controls:  To maintain safe operating conditions, burner safety controls limit burner operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design [temperature] [pressure].

In first subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

2. Low-Water Cutoff Switch:  [Electronic] [Float and electronic] probe shall prevent burner operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

3. Audible Alarm:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

D. Building Automation System Interface:  Factory-install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring:  On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control:  On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.

2. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation.  Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.11 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article.  Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

B. Single-Point Field Power Connection:  Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

Select one of four options in first subparagraph below.  Type 1 is the most common, and Type 12 is second.  Type 4X is used primarily in corrosive environments.

1. House in NEMA 250, Type [1] [4] [4X] [12] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.12 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

A. Heating Medium:  [Hot water] [Steam].

Retain one of first two paragraphs below.  Retain first for hot-water boilers and second for steam boilers.  In paragraph below, 30- and 125-psig (207- and 860-kPa) ratings are available only in horizontal, fire-tube design.

B. Design Pressure Rating:  [30 psig (207 kPa)] [60 psig (420 kPa)] [100 psig (690 kPa)] [125 psig (860 kPa)] [140 psig (966 kPa)] [160 psig (1100 kPa)] <Insert value>.

In first paragraph below, 200- and 300-psig (1380- and 2070-kPa) ratings are available only in horizontal, fire-tube boilers.

C. Design Pressure Rating:  [15 psig (104 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] [350 psig (2415 kPa)] <Insert value>.

D. Safety Relief Valve Setting:  <Insert psig (kPa).>

Retain four paragraphs below for hot-water boilers; delete for steam boilers.

E. Entering-Water Temperature:  <Insert deg F (deg C).>

F. Leaving-Water Temperature:  <Insert deg F (deg C).>

G. Design Water Flow Rate:  <Insert gpm (L/s).>

H. Design Pressure Drop:  <Insert psig (kPa).>

Retain two paragraphs below for steam boilers; delete for hot-water boilers.

I. Steam Operating Pressure:  <Insert psig (kPa).>

J. Steam Flow Rate:  <Insert lb/h (kg/s).>

Retain one of first three paragraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

K. Minimum Efficiency AFUE:  <Insert value> percent.

L. Minimum Thermal Efficiency:  <Insert value> percent.

M. Minimum Combustion Efficiency:  <Insert value> percent.

N. Number of Passes:  [Two] [Four] <Insert number>.

Retain one of first four paragraphs below.  Retain one of first three input rating methods for gas.

O. AGA Input:  <Insert MBh (kW).>

P. I=B=R Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

Q. Gas Input:  <Insert cfh (mL/s).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

R. Oil Input:  <Insert gph (mL/s).>

Retain one of three paragraphs below for rating methods.

S. AGA Output Capacity:  <Insert MBh (kW).>

T. DOE Output Capacity:  <Insert MBh (kW).>

U. Equivalent Direct Radiation:  <Insert EDR (W).>

Retain paragraph and subparagraphs below if boiler is equipped with tankless water heater.

V. Tankless Water Heater:

1. Design Water Flow:  <Insert gpm (L/s).>

2. Design Pressure Drop:  <Insert psig (kPa).>

3. Entering-Water Temperature:  <Insert deg F (deg C).>

4. Leaving-Water Temperature:  <Insert deg F (deg C).>

Consider impact of site altitude on fan and motor.

W. Burner Blower:

1. Motor Horsepower:  <Insert value.>

2. RPM:  <Insert value.>

X. Electrical Characteristics:

1. Volts:  [115] [208] [230] [460] <Insert value> V.

2. Phase:  [Single] [Three].

3. Hertz:  [50] [60].

4. Full-Load Amperes:  <Insert value.>

5. Minimum Circuit Ampacity:  <Insert value.>

6. Maximum Overcurrent Protection:  <Insert amperage.>

2.13 SOURCE QUALITY CONTROL

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

Retain paragraph below for factory-assembled boilers.

B. Burner and Hydrostatic Test:  Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

Retain paragraph below if Owner wants to witness source quality-control testing.

C. Allow Owner access to source quality-control testing of boilers.  Notify Architect 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Examine mechanical spaces for suitable conditions where boilers will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Coordinate selection of device and deflection in first paragraph below with Division 15 Section "Mechanical Vibration and Seismic Controls."

B. Vibration Isolation:  Elastomeric [isolator pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Install gas-fired boilers according to NFPA 54.

Retain paragraph above for gas-fired boilers and first paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

D. Install oil-fired boilers according to NFPA 31.

E. Assemble and install boiler trim.

F. Install electrical devices furnished with boiler but not specified to be factory mounted.

G. Install control wiring to field-mounted electrical devices.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect gas piping to boiler gas-train inlet with union.  Piping shall be at least full size of gas train connection.  Provide a reducer if required.

Retain paragraph above for gas-fired boilers and first paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

D. Connect oil piping full size to burner inlet with shutoff valve and union.

E. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

F. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

G. Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 15 Section "Steam and Condensate Piping" or "Hydronic Piping."

H. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

I. Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

J. Connect breeching full size to boiler outlet.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for venting materials.

K. Install flue-gas recirculation duct from vent to burner.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for recirculation duct materials.

L. Ground equipment according to Division 16 Section "Grounding and Bonding."

M. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

3. Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Retain first subparagraph below for field-assembled boilers.

a. Burner Test:  Adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency.

b. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level, and [water temperature] [steam pressure].

c. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments:  When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.

E. Performance Tests:

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

2. Boilers shall comply with performance requirements indicated, as determined by field performance tests.  Adjust, modify, or replace equipment in order to comply.

3. Perform field performance tests to determine the capacity and efficiency of boilers.

a. For dual-fuel boilers, perform tests for each fuel.

b. Test for full capacity.

c. Test for boiler efficiency at [low fire, 20, 40, 60, 80, 100, 80, 60, 40 and 20] <Insert range> percent of full capacity.  Determine efficiency at each test point.

4. Repeat tests until results comply with requirements indicated.

5. Provide analysis equipment required to determine performance.

6. Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

7. Notify Architect in advance of test dates.

8. Document test results in a report and submit to Architect.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[  Video training sessions.] Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15518END OF SECTION 15518

FIRE-TUBE BOILERS
15518 - 1

