Copyright 2005 AIA
MASTERSPEC Full Length
03/05 (R 06/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15629 - SCROLL WATER CHILLERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Packaged, water-cooled, electric-motor-driven, scroll water chillers.

2. Packaged, air-cooled, electric-motor-driven, scroll water chillers.

3. Packaged refrigerant recovery units.

Retain paragraph below for water-cooled water chillers.

B. Related Sections:

Retain subparagraph below for requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 15 Section "Refrigerant Monitoring and Safety Equipment" for refrigerant monitors, alarms, supplemental breathing apparatus, and ventilation equipment interlocks.

1.3 DEFINITIONS

Retain definitions remaining after this Section has been edited.

A. COP:  Coefficient of performance.  The ratio of the rate of heat removal to the rate of energy input using consistent units for any given set of rating conditions.

B. EER:  Energy-efficiency ratio.  The ratio of the cooling capacity given in terms of Btu/h to the total power input given in terms of watts at any given set of rating conditions.

C. IPLV:  Integrated part-load value.  A single number part-load efficiency figure of merit calculated per the method defined by ARI 550/590 and referenced to ARI standard rating conditions.

D. kW/Ton:  The ratio of total power input of the chiller in kilowatts to the net refrigerating capacity in tons at any given set of rating conditions.

E. NPLV:  Nonstandard part-load value.  A single number part-load efficiency figure of merit calculated per the method defined by ARI 550/590 and intended for operating conditions other than the ARI standard rating conditions.

1.4 PERFORMANCE REQUIREMENTS

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

A. Seismic Performance:  Scroll water chillers shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First three paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  Include refrigerant, rated capacities, operating characteristics, furnished specialties, and accessories.

1. Performance at ARI standard conditions and at conditions indicated.

2. Performance at ARI standard unloading conditions.

3. Minimum evaporator flow rate.

4. Refrigerant capacity of water chiller.

5. Oil capacity of water chiller.

6. Fluid capacity of evaporator.

Retain first subparagraph below for water-cooled water chillers.

7. Fluid capacity of condenser.

8. Characteristics of safety relief valves.

Retain first two subparagraphs below for water-cooled water chillers.

9. Minimum entering condenser-water temperature.

10. Performance at varying capacity with constant design condenser-water temperature.  Repeat performance at varying capacity for different condenser-water temperatures from design to minimum in [5 deg F (3 deg C)] <Insert deg F (deg C)> increments.

Retain two subparagraphs below for air-cooled water chillers.

11. Minimum entering condenser-air temperature

12. Performance at varying capacity with constant design entering condenser-air temperature.  Repeat performance at varying capacity for different entering condenser-air temperatures from design to minimum in [10 deg F (6 deg C)] <Insert deg F (deg C)> increments.

B. LEED Submittal:

Retain subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

C. Shop Drawings:  Complete set of manufacturer's prints of water chiller assemblies, control panels, sections and elevations, and unit isolation.  Include the following:

1. Assembled unit dimensions.

2. Weight and load distribution.

3. Required clearances for maintenance and operation.

4. Size and location of piping and wiring connections.

5. Wiring Diagrams:  For power, signal, and control wiring.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Structural supports.

2. Piping roughing-in requirements.

3. Wiring roughing-in requirements, including spaces reserved for electrical equipment.

4. Access requirements, including working clearances for mechanical controls and electrical equipment, and tube pull and service clearances.

Retain first paragraph below if retaining certification in "Quality Assurance" Article.

E. Certificates:  For certification required in "Quality Assurance" Article.

Some manufacturers will not provide certification specified in first paragraph below.  Verify availability with manufacturers and retain below if required by seismic criteria applicable to Project.  See the "Seismic Considerations" Article in the Evaluations.  Coordinate below with Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."  See SEI/ASCE 7 for certification requirements for equipment and components.

F. Seismic Qualification Certificates:  For water chillers, accessories, and components from manufacturers.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

G. Source quality-control test reports.

H. Startup service reports.

I. Operation and Maintenance Data:  For each water chiller to include in emergency, operation, and maintenance manuals.

J. Warranty:  Sample of special warranty.

1.6 QUALITY ASSURANCE

Retain first paragraph below if ARI certification is required and Project requirements fall within limits of ARI 590 certification program.  ARI 550/590 standard is broken into two certification programs; ARI 590 certification program is applicable to scroll water chillers.  Review the latest version to confirm requirements.

A. ARI Certification:  Certify chiller according to ARI 590 certification program.

B. ARI Rating:  Rate water chiller performance according to requirements in ARI 550/590, "Water Chilling Packages Using the Vapor Compression Cycle."

C. ASHRAE Compliance:  ASHRAE 15 for safety code for mechanical refrigeration.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  LEED-NC Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1-2004.  Coordinate efficiency requirements with Part 2 "Capacities and Characteristics" paragraphs.

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

E. ASME Compliance:  Fabricate and stamp water chiller heat exchangers to comply with ASME Boiler and Pressure Vessel Code.

F. Comply with NFPA 70.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Ship water chillers from the factory fully charged with refrigerant and filled with oil.

Retain paragraph below only for projects with special shipping requirements.  Export shipping adds cost.

B. Package water chiller for export shipping.

1.8 COORDINATION

Retain first paragraph below for mounting water chillers on concrete bases.

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

Retain first paragraph below for mounting water chillers on a structural-steel support structure.

B. Coordinate sizes, locations, and anchoring attachments of structural-steel support structures.

Retain paragraph below for roof-mounted, air-cooled water chillers.

C. Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

1.9 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of water chillers that fail in materials or workmanship within specified period.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

1. Compressor Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 PACKAGED WATER-COOLED WATER CHILLERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. McQuay International.

2. Trane.

3. <Insert manufacturer's name>.

C. Description:  Factory-assembled and run-tested water chiller complete with compressor(s), compressor motors and motor controllers, evaporator, condenser where indicated, electrical power, controls, and indicated accessories.

Retain first paragraph below for projects in seismic areas.

D. Fabricate water chiller mounting base with reinforcement strong enough to resist water chiller movement during a seismic event when water chiller is anchored to field support structure.

E. Compressors:

1. Description:  Positive-displacement direct drive with hermetically sealed casing.

2. Each compressor provided with suction and discharge service valves, crankcase oil heater, and suction strainer.

3. Operating Speed:  Nominal 3600 rpm for 60-Hz applications.

Retain option in first subparagraph below if capacity control below the smallest chiller step is required.  See Evaluations.

4. Capacity Control:  On-off compressor cycling[, plus hot-gas bypass].

5. Oil Lubrication System:  Automatic pump with strainer, sight glass, filling connection, filter with magnetic plug, and initial oil charge.

Retain first subparagraph below for factory-installed vibration isolation.  McQuay is the only listed manufacturer offering these isolators.

6. Vibration Isolation:  Mount individual compressors on vibration isolators.

Retain subparagraph below for projects with stringent acoustical requirements.  Sound-reduction packages are typically an optional feature.

7. Sound-reduction package shall consist of acoustic enclosures around the compressors that are designed to reduce sound level without affecting performance.

F. Compressor Motors:

1. Hermetically sealed and cooled by refrigerant suction gas.

2. High-torque, two-pole induction type with inherent thermal-overload protection on each phase.

G. Compressor Motor Controllers:

1. Across the Line:  NEMA ICS 2, Class A, full voltage, nonreversing.

H. Refrigeration:

LEED-NC Credit EA 4 requires that new HVAC&R systems be HCFC free.  Because R-22 is an HCFC and is the only refrigerant offered by manufacturers listed, the credit cannot be attained.  See the Evaluations.

1. Refrigerant:  R-22.  Classified as Safety Group A1 according to ASHRAE 34.

2. Refrigerant Compatibility:  Parts exposed to refrigerants shall be fully compatible with refrigerants, and pressure components shall be rated for refrigerant pressures.

3. Refrigerant Circuit:  Each circuit shall include a thermal-expansion valve, refrigerant charging connections, a hot-gas muffler, compressor suction and discharge shutoff valves, a liquid-line shutoff valve, a replaceable-core filter-dryer, a sight glass with moisture indicator, a liquid-line solenoid valve, and an insulated suction line.

Subparagraph below is not applicable to all chiller types and sizes.  Consult manufacturers.

4. Refrigerant Isolation:  Factory install positive shutoff isolation valves in the compressor discharge line and the refrigerant liquid-line to allow the isolation and storage of the refrigerant charge in the chiller condenser.

I. Evaporator:

Retain first subparagraph below if more than one evaporator type is used on Project.  See Evaluations for discussion of evaporator types.

1. Brazed-plate or shell-and-tube design, as indicated.

Retain first subparagraph below for water chillers with shell-and-tube evaporators.  Trane offers only shell-and-tube evaporators for water-cooled water chillers.

2. Shell and Tube:

a. Description:  Direct-expansion, shell-and-tube design with fluid flowing through the shell and refrigerant flowing through the tubes within the shell.

b. Code Compliance:  Tested and stamped according to ASME Boiler and Pressure Vessel Code.

c. Shell Material:  Carbon steel.

d. Shell Heads:  Removable carbon-steel heads with multipass baffles designed to ensure positive oil return and located at each end of the tube bundle.

e. Shell Nozzles:  Fluid nozzles located along the side of the shell and terminated with mechanical-coupling end connections for connection to field piping.

f. Tube Construction:  Individually replaceable copper tubes with enhanced fin design, expanded into tube sheets.

Retain subparagraph below for water chillers with brazed-plate evaporators.  McQuay offers only brazed-plate evaporators for water-cooled water chillers.

3. Brazed Plate:

a. Direct-expansion, single-pass, brazed-plate design.

b. Type 316 stainless-steel construction.

c. Code Compliance:  Tested and stamped according to ASME Boiler and Pressure Vessel Code.

d. Fluid Nozzles:  Terminate with mechanical-coupling end connections for connection to field piping.

J. Condenser:

Retain first subparagraph below if more than one condenser type is used on Project.

1. Shell and tube or without integral condenser; as indicated.

Retain first subparagraph below for water chillers with shell-and-tube condensers.

2. Shell and Tube:

a. Description:  Shell-and-tube design with refrigerant flowing through the shell and fluid flowing through the tubes within the shell.

b. Provides positive subcooling of liquid refrigerant.

c. Code Compliance:  Tested and stamped according to ASME Boiler and Pressure Vessel Code.

d. Shell Material:  Carbon steel.

e. Water Boxes:  Removable, of carbon-steel construction, located at each end of the tube bundle with fluid nozzles terminated with mechanical-coupling end connections for connection to field piping.

f. Tube Construction:  Individually replaceable copper tubes with enhanced fin design, expanded into tube sheets.

g. Provide each condenser with a pressure relief device, purge cock, and liquid-line shutoff valve.

Retain subparagraph below for water chillers with remote field-installed condensers.  Air-cooled condensers are specified in Division 15 Section "Air-Cooled Condensers."

3. Provide water chiller without an integral condenser and design chiller for field connection to remote condenser.  Coordinate requirements with Division 15 Section "Air-Cooled Condensers."

K. Electrical Power:

Not all manufacturers provide all features indicated in subparagraphs below.  Verify availability with manufacturers.

1. Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to water chiller.

2. House in a unit-mounted, NEMA 250, [Type 1] <Insert type> enclosure with hinged access door with lock and key or padlock and key.

3. Wiring shall be numbered and color-coded to match wiring diagram.

4. Install factory wiring outside of an enclosure in a raceway.

5. Field power interface shall be to [wire lugs] [NEMA KS 1, heavy-duty, nonfused disconnect switch].

6. Provide branch power circuit to each motor and to controls with one of the following disconnecting means:

a. NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 60947-4-1.

b. NEMA KS 1, heavy-duty, nonfusible switch.

c. NEMA AB 1, motor-circuit protector (circuit breaker) with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

7. Provide each motor with overcurrent protection.

8. Overload relay sized according to UL 1995, or an integral component of water chiller control microprocessor.

9. Phase-Failure and Undervoltage:  Solid-state sensing with adjustable settings.

10. Controls Transformer:  Unit-mounted transformer with primary and secondary fuses and sized with enough capacity to operate electrical load plus spare capacity.

11. Control Relays:  Auxiliary and adjustable time-delay relays.

12. Indicate the following for water chiller electrical power supply:

a. Current, phase to phase, for all three phases.

b. Voltage, phase to phase and phase to neutral for all three phases.

c. Three-phase real power (kilowatts).

d. Three-phase reactive power (kilovolt amperes reactive).

e. Power factor.

f. Running log of total power versus time (kilowatt hours).

g. Fault log, with time and date of each.

h. <Insert features>.

L. Controls:

1. Stand-alone, microprocessor based.

2. Enclosure:  Share enclosure with electrical power devices or provide a separate enclosure of matching construction.

3. Operator Interface:  Keypad or pressure-sensitive touch screen.  Multiple-character, backlit, liquid-crystal display or light-emitting diodes.  Display the following:

Verify availability of items in list below; status displays may vary depending on unit size.

a. Date and time.

b. Operating or alarm status.

c. Operating hours.

d. Outside-air temperature if required for chilled-water reset.

e. Temperature and pressure of operating set points.

f. Entering and leaving temperatures of chilled water.

g. Entering and leaving temperatures of condenser water.

h. Refrigerant pressures in evaporator and condenser.

i. Saturation temperature in evaporator and condenser.

j. No cooling load condition.

k. Elapsed time meter (compressor run status).

l. Pump status.

m. Antirecycling timer status.

n. Percent of maximum motor amperage.

o. Current-limit set point.

p. Number of compressor starts.

q. <Insert items>.

4. Control Functions:

Verify availability of items in list below; functions may vary depending on unit size.

a. Manual or automatic startup and shutdown time schedule.

b. Entering and leaving chilled-water temperatures, control set points, and motor load limit.  Chilled-water leaving temperature shall be reset based on [return-water] [outside-air] [space] temperature.

c. Current limit and demand limit.

d. Condenser-water temperature.

e. External water chiller emergency stop.

f. Antirecycling timer.

g. Automatic lead-lag switching.

h. <Insert functions>.

5. Manual-Reset Safety Controls:  The following conditions shall shut down water chiller and require manual reset:

Verify availability of items in list below; conditions may vary depending on unit size.

a. Low evaporator pressure or high condenser pressure.

b. Low chilled-water temperature.

c. Refrigerant high pressure.

d. High or low oil pressure.

e. High oil temperature.

f. Loss of chilled-water flow.

g. Loss of condenser-water flow.

h. Control device failure.

i. <Insert items>.

Retain subparagraph below if water chiller controls interface with building automation system.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

6. Building Automation System Interface:  Factory-installed hardware and software to enable building automation system to monitor, control, and display water chiller status and alarms.

Retain first subparagraph below if interface with building automation system is through hardwired points and minimal interface is required.

a. Hardwired Points:

1) Monitoring:  On/off status, [common trouble alarm] [electrical power demand (kilowatts)] [electrical power consumption (kilowatt hours)] <Insert monitoring point>.

2) Control:  On/off operation, [chilled-water discharge temperature set-point adjustment] [electrical power demand limit] <Insert control point>.

Delete "Hardwired Points" Subparagraph above and retain subparagraph below if extensive interface with building automation system is required and is beyond what hardwired points can provide.  Requirement may exclude some manufacturers.

b. [ASHRAE 135 (BACnet)] [LonTalk] [Modbus] [Industry-accepted open-protocol] <Insert type of interface> communication interface with building automation system shall enable building automation system operator to remotely control and monitor the water chiller from an operator workstation.  Control features and monitoring points displayed locally at water chiller control panel shall be available through building automation system.

M. Insulation:

1. Material:  Closed-cell, flexible elastomeric, thermal insulation complying with ASTM C 534, Type I, for tubular materials and Type II, for sheet materials.

2. Thickness:  [3/4 inch (19 mm)] <Insert thickness>.

3. Factory-applied insulation over cold surfaces of water chiller components.

a. Adhesive:  As recommended by insulation manufacturer and applied to 100 percent of insulation contact surface.  Seal seams and joints.

4. Apply protective coating to exposed surfaces of insulation.

N. Accessories:

Consult manufacturer for availability of accessories listed.

1. Factory-furnished, chilled-[ and condenser-]water flow switches for field installation.

2. Individual compressor suction and discharge pressure gages with shutoff valves for each refrigeration circuit.

3. Factory-furnished [neoprene] [spring] [neoprene or spring] isolators for field installation.

If Project has more than one type or configuration of water chiller, delete paragraph below and schedule water chillers on Drawings.

O. Capacities and Characteristics:

1. Capacity:  <Insert tons (kW)>.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  LEED-NC Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1-2004.  Coordinate efficiency requirements with "Quality Assurance" Article.

2. Full-Load Efficiency:

Retain one of first three subparagraphs below.  First subparagraph is used in ASHRAE/IESNA 90.1-2004.

a. COP:  <Insert number>.

b. EER:  <Insert number>.

c. Power Input/Cooling Output, kW/Ton (kW/kW):  <Insert value>.

3. Part-Load Efficiency:

Retain one of first two subparagraphs below.  Retain first subparagraph if operating conditions reference ARI standard conditions; retain second subparagraph if operating conditions are other than ARI standard rating conditions.

a. IPLV:  <Insert number>.

b. NPLV:  <Insert number>.

First option in first subparagraph below is available only from McQuay; second option is available only from Trane.

4. Evaporator Type:  [Brazed plate] [Shell and tube] [Brazed plate or shell and tube].

5. Evaporator Pressure Rating:  <Insert psig (kPa)>.

6. Evaporator Fluid Type:  [Water] <Insert fluid type>.

7. Design Evaporator Fluid Flow Rate:  <Insert gpm (L/s)>.

8. Minimum Evaporator Fluid Flow Rate:  <Insert gpm (L/s)>.

9. Evaporator Entering-Fluid Temperature:  <Insert deg F (deg C)>.

10. Evaporator Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

11. Evaporator Fluid Pressure Drop:  <Insert feet of head (kPa)>.

Fouling factor units in first subparagraph below are consistent with ARI 550/590; first option is based on ARI 550/590 standard rating.

12. Evaporator Fouling Factor:  [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000044 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

13. Condenser Type:  [Shell and tube] [Chiller without integral condenser].

Retain first seven subparagraphs below if condenser is integral to water chiller; delete if not integral.

14. Condenser Pressure Rating:  <Insert psig (kPa)>.

15. Condenser Fluid Type:  [Water] <Insert fluid type>.

16. Condenser Fluid Flow Rate:  <Insert gpm (L/s)>.

17. Condenser Entering-Fluid Temperature:  <Insert deg F (deg C)>.

18. Condenser Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

19. Condenser Fluid Pressure Drop:  <Insert feet of head (kPa)>.

Fouling factor units in first subparagraph below are consistent with ARI 550/590; first option is based on ARI 550/590 standard rating.

20. Condenser Fouling Factor:  [0.00025 sq. ft. x h x deg F/Btu (0.000044 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] [0.001 sq. ft. x h x deg F/Btu (0.00022 sq. m x deg C/W)] <Insert factor>.

Second option in first subparagraph below is not available in all chiller sizes.  Consult manufacturer.

21. Number of Refrigeration Circuits:  [One] [Two].

Copy first two subparagraphs below and insert values for each compressor of multiple compressor units.

22. Compressor Rated Load Amperes:  <Insert value>.

23. Compressor Locked-Rotor Amperes:  <Insert value>.

24. Controls Power Connection:  Fed through integral transformer.

25. Chiller Power Input:  <Insert kilowatts>.

26. Chiller Minimum Circuit Ampacity:  <Insert value>.

27. Chiller Maximum Overcurrent Protection Device:  <Insert amperage>.

28. Chiller Electrical Characteristics:  [208] [240] [480] [600] <Insert value>-V ac, three phase, 60 Hz.

29. Noise Rating:  <Insert dBA> at <Insert distance in feet (m)> when measured according to ARI 575.

2.2 PACKAGED AIR-COOLED WATER CHILLERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Carrier Corporation; a United Technologies company.

2. McQuay International.

3. Trane.

4. York International Corporation.

5. <Insert manufacturer's name>.

C. Description:  Factory-assembled and run-tested water chiller complete with base and frame, condenser casing, compressors, compressor motors and motor controllers, evaporator, condenser coils, condenser fans and motors, electrical power, controls, and accessories.

Retain first paragraph below for projects in seismic areas.

D. Fabricate base, frame, and attachment to water chiller components strong enough to resist movement during a seismic event when water chiller base is anchored to field support structure.

E. Cabinet:

1. Base:  Galvanized-steel base extending the perimeter of water chiller.  Secure frame, compressors, and evaporator to base to provide a single-piece unit.

2. Frame:  Rigid galvanized-steel frame secured to base and designed to support cabinet, condenser, control panel, and other chiller components not directly supported from base.

3. Casing: Galvanized steel.

4. Finish:  Coat base, frame, and casing with a corrosion-resistant coating capable of withstanding a [500] <Insert hours>-hour salt-spray test according to ASTM B 117.

Retain first subparagraph below for projects with stringent acoustical requirements.  Sound-reduction packages are typically an optional feature.

5. Sound-reduction package consisting of the following:

a. Acoustic enclosure around compressors.

b. Reduced-speed fans with acoustic treatment.

c. Designed to reduce sound level without affecting performance.

Retain subparagraph below for projects with security requirements and where restricted access is not provided.  Security packages are typically an optional feature and can conflict with other available optional packages such as the sound-reduction package.  Consult manufacturer.

6. Security Package:  Provide security grilles with fasteners for additional protection of compressors, evaporator, and condenser coils.  Grilles shall be coated for corrosion resistance and shall be removable for service access.

F. Compressors:

1. Description:  Positive-displacement direct drive with hermetically sealed casing.

2. Each compressor provided with suction and discharge service valves, crankcase oil heater, and suction strainer.

3. Operating Speed:  Nominal 3600 rpm for 60-Hz applications.

Retain option in first subparagraph below if capacity control below the smallest chiller step is required.  See Evaluations.

4. Capacity Control:  On-off compressor cycling[, plus hot-gas bypass].

5. Oil Lubrication System:  Automatic pump with strainer, sight glass, filling connection, filter with magnetic plug, and initial oil charge.

Retain subparagraph below for factory-installed vibration isolation.  McQuay and York are the only listed manufacturers offering these isolators.

6. Vibration Isolation:  Mount individual compressors on vibration isolators.

G. Compressor Motors:

1. Hermetically sealed and cooled by refrigerant suction gas.

2. High-torque, two-pole induction type with inherent thermal-overload protection on each phase.

H. Compressor Motor Controllers:

1. Across the Line:  NEMA ICS 2, Class A, full voltage, nonreversing.

I. Refrigeration:

LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second, third, or sixth option in first subparagraph below to comply with Credit EA 4.  See Evaluations.

1. Refrigerant:  [R-22] [R-407c] [R-410a] [R-22 or R-407c] [R-22 or R-410a] [R-407c or R-410a] [R-22, R-407c, or R-410a].  Classified as Safety Group A1 according to ASHRAE 34.

2. Refrigerant Compatibility:  Parts exposed to refrigerants shall be fully compatible with refrigerants, and pressure components shall be rated for refrigerant pressures.

3. Refrigerant Circuit:  Each circuit shall include a thermal-expansion valve, refrigerant charging connections, a hot-gas muffler, compressor suction and discharge shutoff valves, a liquid-line shutoff valve, a replaceable-core filter-dryer, a sight glass with moisture indicator, a liquid-line solenoid valve, and an insulated suction line.

Subparagraph below is not applicable to all chiller types and sizes.  Consult manufacturer.

4. Refrigerant Isolation:  Factory install positive shutoff isolation valves in the compressor discharge line and the refrigerant liquid-line to allow the isolation and storage of the refrigerant charge in the chiller condenser.

J. Evaporator:

Retain first subparagraph below if more than one evaporator type is used on Project.  See Evaluations for discussion of evaporator types.

1. Brazed-plate or shell-and-tube design, as indicated.

Retain first subparagraph below for water chillers with shell-and-tube evaporators.  York offers only shell-and-tube evaporators for air-cooled water chillers.  Carrier and McQuay evaporator offerings vary by water chiller size.

2. Shell and Tube:

a. Description:  Direct-expansion, shell-and-tube design with fluid flowing through the shell and refrigerant flowing through the tubes within the shell.

b. Code Compliance:  Tested and stamped according to ASME Boiler and Pressure Vessel Code.

c. Shell Material:  Carbon steel.

d. Shell Heads:  Removable carbon-steel heads with multipass baffles designed to ensure positive oil return and located at each end of the tube bundle.

e. Shell Nozzles:  Fluid nozzles located along the side of the shell and terminated with mechanical-coupling end connections for connection to field piping.

f. Tube Construction:  Individually replaceable copper tubes with enhanced fin design, expanded into tube sheets.

Retain first subparagraph below for water chillers with brazed-plate evaporators.  Trane offers only brazed-plate evaporators for air-cooled water chillers.

3. Brazed Plate:

a. Direct-expansion, single-pass, brazed-plate design.

b. Type 316 stainless-steel construction.

c. Code Compliance:  Tested and stamped according to ASME Boiler and Pressure Vessel Code.

d. Fluid Nozzles:  Terminate with mechanical-coupling end connections for connection to field piping.

Retain first subparagraph below if water chiller is exposed to ambient temperatures capable of freezing the fluid in the evaporator.  See Evaluations for discussion of evaporator freeze protection.

4. Heater:  Factory-installed and -wired electric heater with integral controls designed to protect the evaporator to minus 20 deg F (minus 29 deg C).

5. Remote Mounting:  Designed for remote field mounting where indicated.  Provide kit for field installation.

K. Air-Cooled Condenser:

1. Plate-fin coil with integral subcooling on each circuit, rated at 450 psig (3103 kPa).

a. Construct coils of copper tubes mechanically bonded to [aluminum] [aluminum with precoated epoxy-phenolic] [copper] fins.

Retain first subparagraph below with first or third option in subparagraph above to provide additional corrosion protection.  See Evaluations.

b. Coat coils with a baked epoxy corrosion-resistant coating after fabrication.

Retain first subparagraph below if additional protection is required.  Hail protection is typically an optional feature.  Consult manufacturer.

c. Hail Protection:  Provide condenser coils with louvers, baffles, or hoods to protect against hail damage.

2. Fans:  Direct-drive propeller type with statically and dynamically balanced fan blades, arranged for vertical air discharge.

3. Fan Motors:  Totally enclosed nonventilating (TENV) or totally enclosed air over (TEAO) enclosure, with permanently lubricated bearings, and having built-in overcurrent- and thermal-overload protection.

4. Fan Guards:  Steel safety guards with corrosion-resistant coating.

L. Electrical Power:

Not all manufacturers provide all features indicated in subparagraphs below.  Verify availability with manufacturers.

1. Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to water chiller.

2. House in a unit-mounted, NEMA 250, [Type 3R] <Insert type> enclosure with hinged access door with lock and key or padlock and key.

3. Wiring shall be numbered and color-coded to match wiring diagram.

4. Install factory wiring outside of an enclosure in a raceway.

5. Field power interface shall be to [wire lugs] [NEMA KS 1, heavy-duty, nonfused disconnect switch].

6. Provide branch power circuit to each motor and to controls with one of the following disconnecting means:

a. NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 60947-4-1.

b. NEMA KS 1, heavy-duty, nonfusible switch.

c. NEMA AB 1, motor-circuit protector (circuit breaker) with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

7. Provide each motor with overcurrent protection.

8. Overload relay sized according to UL 1995, or an integral component of water chiller control microprocessor.

9. Phase-Failure and Undervoltage:  Solid-state sensing with adjustable settings.

Retain first subparagraph below for power factor correction.  York is the only manufacturer indicating this option in its product data.  Consult other manufacturers for availability.

10. Provide power factor correction capacitors to correct power factor to [0.90] [0.95] <Insert value> at full load.

Retain first subparagraph below if required for controls or unit-mounted convenience power receptacle.

11. Transformer:  Unit-mounted transformer with primary and secondary fuses and sized with enough capacity to operate electrical load plus spare capacity.

a. Power unit-mounted controls where indicated.

Retain first subparagraph below if unit-mounted convenience power receptacle is required.  Trane and York do not offer this option.

b. Power unit-mounted, ground fault interrupt (GFI) duplex receptacle.

12. Control Relays:  Auxiliary and adjustable time-delay relays.

13. Indicate the following for water chiller electrical power supply:

a. Current, phase to phase, for all three phases.

b. Voltage, phase to phase and phase to neutral for all three phases.

c. Three-phase real power (kilowatts).

d. Three-phase reactive power (kilovolt amperes reactive).

e. Power factor.

f. Running log of total power versus time (kilowatt hours).

g. Fault log, with time and date of each.

h. <Insert features>.

M. Controls:

1. Stand-alone, microprocessor based.

2. Enclosure:  Share enclosure with electrical power devices or provide a separate enclosure of matching construction.

3. Operator Interface:  Keypad or pressure-sensitive touch screen.  Multiple-character, backlit, liquid-crystal display or light-emitting diodes.  Display the following:

Verify availability of items in list below; status displays may vary depending on unit size.

a. Date and time.

b. Operating or alarm status.

c. Operating hours.

d. Outside-air temperature if required for chilled-water reset.

e. Temperature and pressure of operating set points.

f. Entering and leaving temperatures of chilled water.

g. Refrigerant pressures in evaporator and condenser.

h. Saturation temperature in evaporator and condenser.

i. No cooling load condition.

j. Elapsed time meter (compressor run status).

k. Pump status.

l. Antirecycling timer status.

m. Percent of maximum motor amperage.

n. Current-limit set point.

o. Number of compressor starts.

p. <Insert items>.

4. Control Functions:

Verify availability of items in list below; functions may vary depending on unit size.

a. Manual or automatic startup and shutdown time schedule.

b. Entering and leaving chilled-water temperatures, control set points, and motor load limit.  Chilled-water leaving temperature shall be reset based on [return-water] [outside-air] [space] temperature.

c. Current limit and demand limit.

d. External water chiller emergency stop.

e. Antirecycling timer.

f. Automatic lead-lag switching.

g. <Insert functions>.

5. Manual-Reset Safety Controls:  The following conditions shall shut down water chiller and require manual reset:

Verify availability of items in list below; conditions may vary depending on unit size.

a. Low evaporator pressure or high condenser pressure.

b. Low chilled-water temperature.

c. Refrigerant high pressure.

d. High or low oil pressure.

e. High oil temperature.

f. Loss of chilled-water flow.

g. Control device failure.

h. <Insert items>.

Retain subparagraph below if water chiller controls interface with building automation system.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

6. Building Automation System Interface:  Factory-installed hardware and software to enable building automation system to monitor, control, and display water chiller status and alarms.

Retain first subparagraph below if interface with building automation system is through hardwired points and minimal interface is required.

a. Hardwired Points:

1) Monitoring:  On/off status, [common trouble alarm] [electrical power demand (kilowatts)] [electrical power consumption (kilowatt hours)] <Insert monitoring point>.

2) Control:  On/off operation, [chilled-water discharge temperature set-point adjustment] [electrical power demand limit] <Insert control point>.

Delete "Hardwired Points" Subparagraph above and retain subparagraph below if extensive interface with building automation system is required and is beyond what hardwired points can provide.  Requirement may exclude some manufacturers.

b. [ASHRAE 135 (BACnet)] [LonTalk] [Industry-accepted open-protocol] <Insert type of interface> communication interface with building automation system shall enable building automation system operator to remotely control and monitor the water chiller from an operator workstation.  Control features and monitoring points displayed locally at water chiller control panel shall be available through building automation system.

N. Insulation:

1. Material:  Closed-cell, flexible elastomeric, thermal insulation complying with ASTM C 534, Type I, for tubular materials and Type II, for sheet materials.

Second option in first subparagraph below is offered only by McQuay and York.

2. Thickness:  [3/4 inch (19 mm)] [1-1/2 inches (38 mm)] <Insert thickness>.

3. Factory-applied insulation over cold surfaces of water chiller components.

a. Adhesive:  As recommended by insulation manufacturer and applied to 100 percent of insulation contact surface.  Seal seams and joints.

4. Apply protective coating to exposed surfaces of insulation.

O. Accessories:

Consult manufacturer for availability of accessories listed.

1. Factory-furnished, chilled-[ and condenser-]water flow switches for field installation.

2. Individual compressor suction and discharge pressure gages with shutoff valves for each refrigeration circuit.

3. Factory-furnished [neoprene] [spring] [neoprene or spring] isolators for field installation.

If Project has more than one type or configuration of water chiller, delete paragraph below and schedule water chillers on Drawings.

P. Capacities and Characteristics:

1. Capacity:  <Insert tons (kW)>.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  LEED-NC Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1-2004.  Coordinate efficiency requirements with "Quality Assurance" Article.

2. Full-Load Efficiency:

Retain one of first three subparagraphs below.  First subparagraph is used in ASHRAE/IESNA 90.1-2004.

a. COP:  <Insert number>.

b. EER:  <Insert number>.

c. Power Input/Cooling Output, kW/Ton (kW/kW):  <Insert value>.

3. Part-Load Efficiency:

Retain one of first two subparagraphs below.  Retain first subparagraph if operating conditions reference ARI standard conditions; retain second subparagraph if operating conditions are other than ARI standard rating conditions.

a. IPLV:  <Insert number>.

b. NPLV:  <Insert number>.

Retain first subparagraph below if low ambient operation is required.  McQuay, Trane, and York can operate to 0 deg F (minus 18 deg C) with optional accessories.  Carrier can operate to minus 20 deg F (minus 29 deg C).

4. Low Ambient Operation:  Chiller designed for operation to [0 deg F (minus 18 deg C)] <Insert value>.

Retain first subparagraph below if high ambient operation is required.  McQuay, Trane, and York can operate to 115 deg F (46 deg C) and above with optional accessories.  Carrier can operate to 120 deg F (50 deg C).

5. High Ambient Operation:  Chiller designed for operation to [115 deg F (46 deg C)] <Insert value>.

6. Evaporator Configuration:  [Integral to chiller] [Shipped loose for remote field installation].

7. Evaporator Pressure Rating:  [150 psig (1034 kPa)] [300 psig (2068 kPa)] <Insert value>.

8. Evaporator Fluid Type:  [Water] <Insert fluid type>.

9. Design Evaporator Fluid Flow Rate:  <Insert gpm (L/s)>.

10. Minimum Evaporator Fluid Flow Rate:  <Insert gpm (L/s)>.

11. Evaporator Entering-Fluid Temperature:  <Insert deg F (deg C)>.

12. Evaporator Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

13. Evaporator Fluid Pressure Drop:  <Insert feet of head (kPa)>.

Fouling factor units in first subparagraph below are consistent with ARI 550/590; first option is based on ARI 550/590 standard rating.

14. Evaporator Fouling Factor:  [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000044 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

15. Condenser Entering-Air Temperature:  <Insert deg F (deg C)>.

16. Site Altitude:  <Insert feet (m)>.

17. Number of Refrigeration Circuits:  [One] [Two].

Copy first two subparagraphs below and insert values for each compressor of multiple compressor units.

18. Compressor Rated Load Amperes:  <Insert value>.

19. Compressor Locked-Rotor Amperes:  <Insert value>.

20. Controls Power Connection:  [Fed through integral transformer] [Separate field power connection].

Retain first four subparagraphs below if retaining second option in subparagraph above.

a. Controls Power Input:  <Insert kilowatts>.

b. Controls Minimum Circuit Ampacity:  <Insert value>.

c. Controls Maximum Overcurrent Protection Device:  <Insert amperage>.

d. Controls Electrical Characteristics:  [120] <Insert value>-V ac, single phase, 60 Hz.

21. Chiller Power Input:  <Insert kilowatts>.

22. Chiller Minimum Circuit Ampacity:  <Insert value>.

23. Chiller Maximum Overcurrent Protection Device:  <Insert amperage>.

24. Chiller Electrical Characteristics:  [208] [240] [480] [600] <Insert value>-V ac, three phase, 60 Hz.

25. Noise Rating:  <Insert dBA> at <Insert distance in feet (m)> when measured according to ARI 370.

2.3 PACKAGED REFRIGERANT RECOVERY UNITS

A. Packaged portable unit shall consist of compressor, air-cooled condenser, recovery system, tank pressure gages, filter-dryer, and valving that allows for switching between liquid and vapor recovery mode.  Refrigerant recovery unit shall be factory mounted on an ASME-constructed and -stamped refrigerant storage vessel that is sized to hold the full refrigerant charge of the largest water chiller.

2.4 SOURCE QUALITY CONTROL

A. Perform functional test of water chillers before shipping.

Factory performance tests are an added cost option and may not be available from some manufacturers.  Verify requirement with Owner.

B. Factory performance test water chillers, before shipping, according to ARI 550/590, "Water Chilling Packages Using the Vapor Compression Cycle."

Retain subparagraph below to witness testing.

1. Allow [Owner] <Insert entity> access to place where water chillers are being tested.  Notify Architect [14] <Insert number> days in advance of testing.

Retain option in first paragraph below for water-cooled water chillers.

C. Factory test and inspect evaporator [and water-cooled condenser ]according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.  Stamp with ASME label.

Retain first paragraph below for water chillers located indoors.

D. For water chillers located indoors, rate sound power level according to ARI 575 procedure.

Retain paragraph below for water chillers located outdoors.

E. For water chillers located outdoors, rate sound power level according to ARI 370 procedure.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before water chiller installation, examine roughing-in for equipment support, anchor-bolt sizes and locations, piping, and electrical connections to verify actual locations, sizes, and other conditions affecting water chiller performance, maintenance, and operations.

1. Water chiller locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 WATER CHILLER INSTALLATION

Retain first paragraph below if water chillers are installed on a support structure other than a concrete base.  Indicate design of support structure on Drawings.

A. Install water chillers on support structure indicated.

Retain one of first four paragraphs below.  If more than one "Equipment Mounting" Paragraph is required, show mounting type on Drawings.  Coordinate with Drawings and Sections specifying vibration and seismic controls.  Retain or insert amount of required deflection.

Retain first paragraph for equipment supported on concrete base and vibration isolation devices.

B. Equipment Mounting:  Install water chiller on concrete bases using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]." Comply with requirements for vibration isolation devices specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

2. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

3. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

4. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for equipment supported on vibration isolation devices without a concrete base.

C. Equipment Mounting:  Install water chiller using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements for vibration isolation devices specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

Retain first paragraph below for equipment supported on a vibration isolation inertia base.

D. Equipment Mounting:  Install water chiller on vibration isolation inertia bases.  Comply with requirements specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain first paragraph below for equipment installed on concrete bases without vibration isolation devices.  This may be appropriate for water chillers on structural slabs-on-grade.

E. Equipment Mounting:  Install water chiller on concrete bases.  Comply with requirements in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

F. Maintain manufacturer's recommended clearances for service and maintenance.

G. Charge water chiller with refrigerant if not factory charged and fill with oil if not factory installed.

H. Install separate devices furnished by manufacturer and not factory installed.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be omitted.

A. Comply with requirements in Division 15 Section "Hydronic Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first paragraph below for chillers with remote evaporator or condenser.

B. Comply with requirements in Division 15 Section "Refrigerant Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

C. Install piping adjacent to chiller to allow service and maintenance.

D. Evaporator Fluid Connections:  Connect to evaporator inlet with shutoff valve,[ strainer,] [ flexible connector,] thermometer, and plugged tee with pressure gage.  Connect to evaporator outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with pressure gage,[ flow meter,] and drain connection with valve.  Make connections to water chiller with a [union] [flange] [mechanical coupling] [union, flange, or mechanical coupling].

Retain first paragraph below for water-cooled water chillers.

E. Condenser Fluid Connections:  Connect to condenser inlet with shutoff valve,[ strainer,] [ flexible connector,] thermometer, and plugged tee with pressure gage.  Connect to condenser outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with pressure gage,[ flow meter,] and drain connection with valve.  Make connections to water chiller with a [union] [flange] [mechanical coupling] [union, flange, or mechanical coupling].

Retain first paragraph below for chillers installed indoors.

F. Refrigerant Pressure Relief Valve Connections:  For water chillers installed indoors, extend vent piping to the outside without valves or restrictions.[  Comply with ASHRAE 15.]

G. Connect each drain connection with a union and drain pipe and extend pipe, full size of connection, to floor drain.  Provide a shutoff valve at each connection if required.

3.4 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Verify that refrigerant charge is sufficient and water chiller has been leak tested.

2. Verify that pumps are installed and functional.

3. Verify that thermometers and gages are installed.

4. Operate water chiller for run-in period.

5. Check bearing lubrication and oil levels.

6. Verify that refrigerant pressure relief device for chillers installed indoors is vented outside.

7. Verify proper motor rotation.

8. Verify static deflection of vibration isolators, including deflection during water chiller startup and shutdown.

Retain option in first subparagraph below for water-cooled water chillers.

9. Verify and record performance of chilled-[ and condenser-]water flow and low-temperature interlocks.

10. Verify and record performance of water chiller protection devices.

11. Test and adjust controls and safeties.  Replace damaged or malfunctioning controls and equipment.

D. Prepare a written startup report that records results of tests and inspections.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain water chillers.[  Video record the training sessions.]

END OF SECTION 15629

SCROLL WATER CHILLERS
15629 - 1

