Copyright 2003 AIA
MASTERSPEC
09/03

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15769 - RADIANT HEATING AND COOLING UNITS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Electric radiant heaters.

2. Prefabricated electric radiant heating panels.

3. Hydronic heating and cooling panels.

1.3 DEFINITIONS

Retain terms that remain after this Section has been edited.  For additional information on some terms, see Editing Instruction No. 5 in the Evaluations.

A. Low Voltage:  As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling and power-limited circuits

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, specialties, and accessories for each product indicated.

B. Shop Drawings:  Include plans, elevations, sections, details, and attachments to other work.  Detail equipment assemblies and suspension and attachment.  Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain subparagraph below if equipment includes wiring.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plan(s) and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Suspended ceiling components.

2. Structural members to which heaters and suspension systems will be attached.

3. Size and location of initial access modules for acoustical tile.

4. Items penetrating finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. <Insert item.>

5. Perimeter moldings.

D. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain paragraph and subparagraphs below with or without above.

E. Samples for Verification:  For each type of exposed finish required, prepared on Samples of size indicated below.

1. For Radiant Heater Finishes:  [4 by 4 inches (100 by 100 mm)] <Insert size>.

2. For Radiant Panel Finishes:  [12 by 12 inches (300 by 300 mm)] <Insert size>.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

F. Manufacturer Seismic Qualification Certification:  Submit certification that suspended radiant heaters and panels, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

G. Field quality-control test reports.

H. Operation and Maintenance Data:  For electric radiant heaters and panels to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.6 COORDINATION

Edit this Article to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of radiant heaters and panels and suspension system components with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 ELECTRIC RADIANT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Berko Electric Heating; a division of Marley Engineered Products.

2. Chromalox Inc.; a division of Emerson Electric Company.

3. Fostoria Industries, Inc.; a division of TPI Corporation.

4. Markel Products; a division of TPI Corporation.

5. Omega Engineering, Inc.

6. QMark Electric Heating; a division of Marley Engineered Products.

7. <Insert manufacturer's name.>

Retain one or more of three paragraphs below.  If more than one type of heating element is required, indicate each type in a schedule on Drawings.

D. Quartz Lamp Heating Elements:  Coiled tungsten-wire heating element enclosed in clear quartz tube.

E. Quartz Tube Heating Elements:  Nickel-chromium-wire heating element enclosed in quartz tube.

F. Metal-Sheathed Heating Elements:  Nickel-chromium-wire heating element embedded in magnesium oxide powder and enclosed in metal sheath.  Comply with UL 1030.

In first paragraph below, select UL 499 for supplemental heating applications requiring humidity control; select UL 2021 for comfort heating applications.  Select all three options if both applications are required.

G. Comply with [UL 499] [and] [UL 2021].

H. Enclosures:  [Aluminized] [Stainless] [Painted]-steel housing with anodized-aluminum reflector.

Retain subparagraph below for painted enclosures.

1. Finish:  Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain paragraph below for integral control device if control devices are not specified in Division 15 Section "HVAC Instrumentation and Controls."

I. Unit Controls:

Retain one or more of three subparagraphs below.  If more than one type of control device is required, indicate each type in a schedule on Drawings.

1. Line-voltage thermostat.

2. Enclosed contactor for remote thermostat.

3. Snow and ice detector with moisture sensor and integral temperature sensor.

If Project has more than one type or size of electric radiant heater, delete paragraph and subparagraphs below and schedule heaters on Drawings.

J. Capacities and Characteristics:

1. Enclosure Length:  <Insert inches (mm).>

2. Mounting Height:  <Insert feet (m).>

3. Heating Capacity:  <Insert kW.>

4. Radiation Pattern:  [30] [60] [90] <Insert number> [symmetric] [asymmetric]-degree-included angle.

5. Electrical Characteristics for Single-Point Connection:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.2 PREFABRICATED ELECTRIC RADIANT HEATING PANELS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Berko Electric Heating; a division of Marley Engineered Products.

2. Markel Products; a division of TPI Corporation.

3. QMark Electric Heating; a division of Marley Engineered Products.

4. SSHC, Inc.; Solid State Heating Division.

5. <Insert manufacturer's name.>

D. Description:  Sheet-metal-enclosed panel with heating element suitable for [lay-in installation flush with T-bar ceiling grid] [surface mounting] [recessed mounting].  Comply with UL 2021.

1. Panel:  Minimum 0.0276-inch- (0.7-mm-) thick, galvanized-steel sheet back panel riveted to minimum 0.0396-inch- (1.0-mm-) thick, galvanized-steel sheet front panel with fused-on crystalline surface.

Retain one of first two subparagraphs below.

2. Heating Element:  Powdered graphite sandwiched between sheets of electric insulation.

3. Heating Element:  Insulated resistive wires.

4. Electrical Connections:  Nonheating, high-temperature, insulated-copper leads, factory connected to heating element.

Retain one of three subparagraphs below.  If more than one type of finish is required, indicate each type in a schedule on Drawings.

5. Exposed-Side Panel Finish:  Apply silk-screened finish to match appearance of Architect-selected acoustical ceiling tiles.

6. Exposed-Side Panel Finish:  Factory prime coated, ready for field painting.

7. Exposed-Side Panel Finish:  Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain subparagraph below for surface-mounting panels.

8. Surface-Mounting Trim:  Sheet metal with baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

E. Wall Thermostat:  Bimetal, sensing elements calibrated from 55 to 90 deg F (13 to 32 deg C); with contacts suitable for [low] [line]-voltage circuit, and manually operated on-off switch with contactors, relays, and control transformers.

If Project has more than one type or size of prefabricated electric radiant heating panel, delete paragraph and subparagraphs below and schedule heating panels on Drawings.

F. Capacities and Characteristics:

1. Nominal Panel Size:  [24 by 24 inches (600 by 600 mm)] [24 by 36 inches (600 by 900 mm)] [24 by 48 inches (600 by 1200 mm)] [24 by 60 inches (600 by 1500 mm)] <Insert custom size>.

2. Heating Capacity:  [250] [375] [500] [570] [625] [750] [950] <Insert value> kW.

3. Electrical Characteristics for Single-Point Connection:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.3 HYDRONIC HEATING[ AND COOLING] PANELS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AIRTEX Radiant Systems; a division of Engineered Air Ltd.

2. Rosemex Products.

3. Sun-El Corporation.

4. Twa Panel Systems Inc.

5. <Insert manufacturer's name.>

D. Description:  [Modular] [Linear] sheet metal panel with serpentine water piping, suitable for [lay-in installation flush with T-bar ceiling grid] [surface mounting] [recessed mounting].

1. Panels:  Minimum [0.0336-inch- (0.86-mm-) thick, galvanized-steel] [0.0396-inch- (1.0-mm-) thick, aluminum] sheet.

2. Backing Insulation:  Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] <Insert thickness> thick, mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 612, Type IA or Type IB with factory-applied jacket.

Retain one of first three subparagraphs below.  If more than one type of finish is required, indicate each type in a schedule on Drawings.

3. Exposed-Side Panel Finish:  Apply silk-screened finish to match appearance of Architect-selected acoustical ceiling tiles.

4. Exposed-Side Panel Finish:  Factory prime coated, ready for field painting.

5. Exposed-Side Panel Finish:  Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

6. Factory Piping:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)] copper tube with ASME B16.22 wrought-copper fittings and brazed joints.  Piping shall be mechanically bonded to panel.

Retain subparagraph below for surface-mounting panels.

7. Surface-Mounting Trim:  Sheet metal with baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain subparagraph and associated subparagraphs below for linear panels only.

8. Accessories:

a. [5-inch (127-mm)] [6-inch (152-mm)] [8-inch (203-mm)] panel with drape track recess.

b. 5-inch (127-mm) male bullnose panel.

c. 5-inch (127-mm) female bullnose panel.

d. 4-inch (102-mm) male corner panel.

e. 4-inch (102-mm) female corner panel.

f. Inside corner panel.

g. 1/2-inch (13-mm) filler panel.

If Project has more than one type or size of hydronic heating and cooling panel, delete paragraph and subparagraphs below and schedule panels on Drawings.

E. Capacities and Characteristics:

1. Nominal Panel Size:  [24 by 24 inches (600 by 600 mm)] [24 by 36 inches (600 by 900 mm)] [24 by 48 inches (600 by 1200 mm)] [24 by 60 inches (600 by 1500 mm)] <Insert custom size>.

2. Piping Inlet and Outlet:  [NPS 1/2 (DN 15)] <Insert size>.

3. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Room Temperature:  <Insert deg F (deg C).>

c. Entering-Water Temperature:  <Insert deg F (deg C).>

d. Average Water Temperature:  <Insert deg F (deg C).>

e. Water Flow:  <Insert gpm (L/s).>

f. Water-Side Pressure Loss:  <Insert psig (kPa).>

4. Cooling:

a. Sensible Capacity:  <Insert Btu/h (kW).>

b. Dry-Bulb Room Temperature:  <Insert deg F (deg C).>

c. Wet-Bulb Room Temperature:  <Insert deg F (deg C).>

d. Entering-Water Temperature:  <Insert deg F (deg C).>

e. Average Water Temperature:  <Insert deg F (deg C).>

f. Water Flow:  <Insert gpm (L/s).>

g. Water-Side Pressure Loss:  <Insert psig (kPa).>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas to receive radiant heating and cooling units for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in for [hydronic piping] [electrical] connections to verify actual locations before radiant heating and cooling unit installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install radiant heating and cooling units level and plumb.

B. Suspend radiant heaters from structure.

C. Support for Radiant Heating and Cooling Panels in or on Grid-Type Suspended Ceilings:  Use grid as a support element.

1. Install a minimum of four ceiling support system rods or wires for each panel.  Locate not more than 6 inches (150 mm) from panel corners.

2. Support Clips:  Fasten to panel and to ceiling grid members at or near each panel corner with clips designed for the application.

3. Panels of Sizes Less Than Ceiling Grid:  Install as indicated on reflected ceiling plans or center in acoustical panel, and support panels independently with at least two 3/4-inch (19-mm) metal channels spanning and secured to ceiling tees.

Retain subparagraph below if Project is in a seismic area.

4. Install at least one independent support rod or wire from structure to a tab on panel.  Wire or rod shall have breaking strength of the weight of panel at a safety factor of 3.

To comply with requirements of the Americans with Disabilities Act, verify mounting height in paragraph below with authorities having jurisdiction

D. Verify locations of thermostats with Drawings and room details before installation.  Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

3.3 CONNECTIONS

Retain first three paragraphs below for hydronic heating and cooling panels.  Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Division 15 Section "Hydronic Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Unless otherwise indicated, install shutoff valve and union or flange at each connection.

C. Install piping adjacent to unit to allow service and maintenance.

D. Ground electric units according to Division 16 Section "Grounding and Bonding."

E. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Testing:  Perform the following field tests and inspections and prepare test reports:

Delete first subparagraph below if units do not have electric heat.

1. Operate electric heating elements through each stage to verify proper operation and electrical connections.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and units.

B. Remove and replace malfunctioning units and retest as specified above.

C. After installing panels, inspect unit cabinet for damage to finish.  Remove paint splatters and other spots, dirt, and debris.  Repair damaged finish to match original finish.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain radiant heaters and panels.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15769

RADIANT HEATING AND COOLING UNITS
15769 - 1

