Copyright 2002 AIA
MASTERSPEC
09/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 16075 - ELECTRICAL IDENTIFICATION
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Identification for raceway and metal-clad cable.

2. Identification for conductors and communication and control cable.

3. Underground-line warning tape.

4. Warning labels and signs.

5. Instruction signs.

6. Equipment identification labels.

7. Miscellaneous identification products.

1.3 SUBMITTALS

A. Product Data:  For each electrical identification product indicated.

Retain two paragraphs below if Project requirements are complex.

B. Identification Schedule:  An index of nomenclature of electrical equipment and system components used in identification signs and labels.

C. Samples:  For each type of label and sign to illustrate size, colors, lettering style, mounting provisions, and graphic features of identification products.

1.4 QUALITY ASSURANCE

Retain first paragraph below for projects with electrical utility work, including underground and overhead distribution and medium-voltage cabling.

A. Comply with ANSI A13.1 and ANSI C2.

B. Comply with NFPA 70.

C. Comply with 29 CFR 1910.145.

1.5 COORDINATION

A. Coordinate identification names, abbreviations, colors, and other features with requirements in the Contract Documents, Shop Drawings, manufacturer's wiring diagrams, and the Operation and Maintenance Manual, and with those required by codes, standards, and 29 CFR 1910.145.  Use consistent designations throughout Project.

B. Coordinate installation of identifying devices with completion of covering and painting of surfaces where devices are to be applied.

C. Coordinate installation of identifying devices with location of access panels and doors.

D. Install identifying devices before installing acoustical ceilings and similar concealment.

PART 2 -  PRODUCTS

Retain products in articles below that are retained in Part 3 "Application" Article.  Consider alternatives before specifying self-adhesive identification products.  See Editing Instruction No. 1 and "Writing Guide" Article in the Evaluations.

2.1 RACEWAY AND METAL-CLAD CABLE IDENTIFICATION MATERIALS

Retain this Article if Project requires identification beyond requirements in NFPA 70.  See "Specifying Considerations" Article in the Evaluations.

A. Comply with ANSI A13.1 for minimum size of letters for legend and for minimum length of color field for each raceway and cable size.

B. Color for Printed Legend:

1. Power Circuits:  Black letters on an orange field.

2. <Insert systems and assigned colors.>

3. Legend:  Indicate system or service and voltage, if applicable.

Retain one or more of four paragraphs below.  Coordinate with Part 3 "Application" Article.  See Editing Instruction No. 1 in the Evaluations for a discussion on self-adhesive product in first paragraph.

C. Self-Adhesive Vinyl Labels:  Preprinted, flexible label laminated with a clear, weather- and chemical-resistant coating and matching wraparound adhesive tape for securing ends of legend label.

D. Snap-Around Labels:  Slit, pretensioned, flexible, preprinted, color-coded acrylic sleeves, with diameter sized to suit diameter of raceway or cable it identifies and to stay in place by gripping action.

E. Snap-Around, Color-Coding Bands:  Slit, pretensioned, flexible, solid-colored acrylic sleeves, 2 inches (50 mm) long, with diameter sized to suit diameter of raceway or cable it identifies and to stay in place by gripping action.

F. Self-Adhesive Vinyl Tape:  Colored, heavy duty, waterproof, fade resistant; 2 inches (50 mm) wide; compounded for outdoor use.

2.2 CONDUCTOR AND COMMUNICATION- AND CONTROL-CABLE IDENTIFICATION MATERIALS

Retain this Article if Project requires identification beyond requirements in NFPA 70.  See "Specifying Considerations" Article in the Evaluations.

Retain first paragraph below for colored tape used to identify phase or voltage of circuits.

A. Color-Coding Conductor Tape:  Colored, self-adhesive vinyl tape not less than 3 mils (0.08 mm) thick by 1 to 2 inches (25 to 50 mm) wide.

B. Marker Tapes:  Vinyl or vinyl-cloth, self-adhesive wraparound type, with circuit identification legend machine printed by thermal transfer or equivalent process.

C. Aluminum Wraparound Marker Labels:  Cut from 0.014-inch- (0.35-mm-) thick aluminum sheet, with stamped, embossed, or scribed legend, and fitted with tabs and matching slots for permanently securing around wire or cable jacket or around groups of conductors.

D. Metal Tags:  Brass or aluminum, 2 by 2 by 0.05 inch (50 by 50 by 1.3 mm), with stamped legend, punched for use with self-locking nylon tie fastener.

Specify thicker tags in paragraph below where exposed to damage or rough service.

E. Write-On Tags:  Polyester tag, [0.010 inch (0.25 mm)] [0.015 inch (0.38 mm)] <Insert thickness> thick, with corrosion-resistant grommet and polyester or nylon tie for attachment to conductor or cable.

1. Marker for Tags:  Permanent, waterproof, black ink marker recommended by tag manufacturer.

2.3 UNDERGROUND-LINE WARNING TAPE

A. Description:  Permanent, bright-colored, continuous-printed, polyethylene tape.

1. Not less than 6 inches (150 mm) wide by 4 mils (0.102 mm) thick.

2. Compounded for permanent direct-burial service.

3. Embedded continuous metallic strip or core.

4. Printed legend shall indicate type of underground line.

2.4 WARNING LABELS AND SIGNS

A. Comply with NFPA 70 and 29 CFR 1910.145.

B. Self-Adhesive Warning Labels:  Factory printed, multicolor, pressure-sensitive adhesive labels, configured for display on front cover, door, or other access to equipment, unless otherwise indicated.

C. Baked-Enamel Warning Signs:  Preprinted aluminum signs, punched or drilled for fasteners, with colors, legend, and size required for application.  1/4-inch (6.4-mm) grommets in corners for mounting.  Nominal size, 7 by 10 inches (180 by 250 mm).

D. Metal-Backed, Butyrate Warning Signs:  Weather-resistant, nonfading, preprinted, cellulose-acetate butyrate signs with 0.0396-inch (1-mm) galvanized-steel backing; and with colors, legend, and size required for application.  1/4-inch (6.4-mm) grommets in corners for mounting.  Nominal size, 10 by 14 inches (250 by 360 mm).

E. Warning label and sign shall include, but are not limited to, the following legends:

1. Multiple Power Source Warning:  "DANGER - ELECTRICAL SHOCK HAZARD - EQUIPMENT HAS MULTIPLE POWER SOURCES."

Dimension in first subparagraph below is clear space prescribed in NFPA 70 (2002 Edition), Table 110-26(A)(1), for equipment with nominal voltage to ground of 151 to 600 V, and with grounded parts, including concrete, brick, or tile walls, opposite the equipment.  Additional clear space is required at this voltage if there are unguarded exposed live parts on both sides of the workspace.  Retain below and revise to suit Project conditions or requirements of authorities having jurisdiction, or indicate varying clearance requirements on Drawings.

2. Workspace Clearance Warning:  "WARNING - OSHA REGULATION - AREA IN FRONT OF ELECTRICAL EQUIPMENT MUST BE KEPT CLEAR FOR 36 INCHES (915 MM)."

3. <Insert names and wording of additional warning signs or labels.>

2.5 INSTRUCTION SIGNS

Coordinate this Article with Drawings.

A. Engraved, laminated acrylic or melamine plastic, minimum 1/16 inch (1.6 mm) thick for signs up to 20 sq. in. (129 sq. cm) and 1/8 inch (3.2 mm) thick for larger sizes.

1. Engraved legend with [black letters on white face] <Insert colors>.

2. Punched or drilled for mechanical fasteners.

3. Framed with mitered acrylic molding and arranged for attachment at applicable equipment.

2.6 EQUIPMENT IDENTIFICATION LABELS

Retain one of four paragraphs below to specify type of labels Contractor must use to comply with NFPA 70 (2002 Edition), Article 110-22, "Identification of Disconnecting Means."  Note that, unless otherwise indicated, the labeling products selected below will also be used for labeling that is not required by NFPA 70 but may be specified in Part 3 "Application" Article to identify equipment other than disconnect devices.  See Evaluations.

A. Adhesive Film Label:  Machine printed, in black, by thermal transfer or equivalent process.  Minimum letter height shall be 3/8 inch (10 mm).

B. Adhesive Film Label with Clear Protective Overlay:  Machine printed, in black, by thermal transfer or equivalent process.  Minimum letter height shall be 3/8 inch (10 mm).  Overlay shall provide a weatherproof and ultraviolet-resistant seal for label.

C. Self-Adhesive, Engraved, Laminated Acrylic or Melamine Label:  Adhesive backed, with white letters on a dark-gray background.  Minimum letter height shall be 3/8 inch (10 mm).

D. Engraved, Laminated Acrylic or Melamine Label:  Punched or drilled for screw mounting.  White letters on a dark-gray background.  Minimum letter height shall be 3/8 inch (10 mm).

Retain paragraph below to specify type of label for identifying outdoor equipment if specified in Part 3 "Application" Article.

E. Stenciled Legend:  In nonfading, waterproof, [black] <Insert color> ink or paint.  Minimum letter height shall be [1 inch (25 mm)] <Insert height>.

2.7 MISCELLANEOUS IDENTIFICATION PRODUCTS

A. Cable Ties:  Fungus-inert, self-extinguishing, 1-piece, self-locking, Type 6/6 nylon cable ties.

1. Minimum Width:  3/16 inch (5 mm).

2. Tensile Strength:  50 lb (22.6 kg), minimum.

3. Temperature Range:  Minus 40 to plus 185 deg F (Minus 40 to plus 85 deg C).

4. Color:  Black, except where used for color-coding.

B. Paint:  Paint materials and application requirements are specified in Division 9 painting Sections.

Nine subparagraphs and associated subparagraphs below describe some typical surfaces and paint systems.  For surfaces and paint systems other than those listed below, see Division 9 painting Sections.

1. Exterior Concrete, Stucco, and Masonry (Other Than Concrete Unit Masonry):

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Exterior concrete and masonry primer.

2) Finish Coats:  Exterior semigloss acrylic enamel.

2. Exterior Concrete Unit Masonry:

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a block filler.

1) Block Filler:  Concrete unit masonry block filler.

2) Finish Coats:  Exterior semigloss acrylic enamel.

3. Exterior Ferrous Metal:

a. Semigloss Alkyd-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Exterior ferrous-metal primer.

2) Finish Coats:  Exterior semigloss alkyd enamel.

4. Exterior Zinc-Coated Metal (except Raceways):

a. Semigloss Alkyd-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Exterior zinc-coated metal primer.

2) Finish Coats:  Exterior semigloss alkyd enamel.

5. Interior Concrete and Masonry (Other Than Concrete Unit Masonry):

a. Semigloss Alkyd-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Interior concrete and masonry primer.

2) Finish Coats:  Interior semigloss alkyd enamel.

6. Interior Concrete Unit Masonry:

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a block filler.

1) Block Filler:  Concrete unit masonry block filler.

2) Finish Coats:  Interior semigloss acrylic enamel.

7. Interior Gypsum Board:

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Interior gypsum board primer.

2) Finish Coats:  Interior semigloss acrylic enamel.

8. Interior Ferrous Metal:

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Interior ferrous-metal primer.

2) Finish Coats:  Interior semigloss acrylic enamel.

9. Interior Zinc-Coated Metal (except Raceways):

a. Semigloss Acrylic-Enamel Finish:  [One] [Two] <Insert number> finish coat(s) over a primer.

1) Primer:  Interior zinc-coated metal primer.

2) Finish Coats:  Interior semigloss acrylic enamel.

C. Fasteners for Labels and Signs:  Self-tapping, stainless-steel screws or stainless-steel machine screws with nuts and flat and lock washers.

PART 3 -  EXECUTION

3.1 APPLICATION

Revise this Article to suit Project.

Retain paragraph and subparagraphs below if Project contains concealed wiring more than 600 V that is adjacent to accessible building surfaces; for example, wiring below floors or wiring in vertical shafts behind gypsum board or masonry partitions.

A. Raceways and Duct Banks More Than 600 V Concealed within Buildings:  4-inch- (100-mm-) wide black stripes on 10-inch (250-mm) centers over orange background that extends full length of raceway or duct and is 12 inches (300 mm) wide.  Stencil legend "DANGER CONCEALED HIGH VOLTAGE WIRING" with 3-inch- (75-mm-) high black letters on 20-inch (500-mm) centers.  Stop stripes at legends.  Apply to the following finished surfaces:

1. Floor surface directly above conduits running beneath and within 12 inches (300 mm) of a floor that is in contact with earth or is framed above unexcavated space.

2. Wall surfaces directly external to raceways concealed within wall.

3. Accessible surfaces of concrete envelope around raceways in vertical shafts, exposed in the building, or concealed above suspended ceilings.

Retain first paragraph below for circuits operating more than 600 V; paragraph contains requirements exceeding those in NFPA 70.

B. Accessible Raceways and Metal-Clad Cables More Than 600 V:  Identify with "DANGER-HIGH VOLTAGE" in black letters at least 2 inches (50 mm) high, with [self-adhesive vinyl labels] [snap-around labels].  Repeat legend at 10-foot (3-m) maximum intervals.

C. Accessible Raceways and Metal-Clad Cables, 600 V or Less, for Service, Feeder, and Branch Circuits More Than [30 A] <Insert Current>:  Identify with orange [self-adhesive vinyl label] [snap-around label] [self-adhesive vinyl tape applied in bands].

D. Accessible Raceways and Cables of Auxiliary Systems:  Identify the following systems with color-coded, [self-adhesive vinyl tape applied in bands] [snap-around, color-coding bands]:

Revise list below to suit Project.

1. Fire Alarm System:  Red.

2. Fire-Suppression Supervisory and Control System:  Red and yellow.

3. Combined Fire Alarm and Security System:  Red and blue.

4. Security System:  Blue and yellow.

5. Mechanical and Electrical Supervisory System:  Green and blue.

6. Telecommunication System:  Green and yellow.

7. Control Wiring:  Green and red.

8. <Insert system name and identifying colors.>

E. Power-Circuit Conductor Identification:  For [primary] [and] [secondary] conductors No. [1/0] <Insert size> AWG and larger in vaults, pull and junction boxes, manholes, and handholes use [color-coding conductor tape] [marker tape] [aluminum wraparound marker labels] [metal tags] [write-on tags].  Identify source and circuit number of each set of conductors.  For single conductor cables, identify phase in addition to the above.

F. Branch-Circuit Conductor Identification:  Where there are conductors for more than three branch circuits in same junction or pull box, use [color-coding conductor tape] [marker tape] [aluminum wraparound marker labels] [metal tags] [write-on tags].  Identify each ungrounded conductor according to source and circuit number.

Retain first paragraph below for future expansion circuits or if required for circuits for other purposes.  Coordinate with Drawings.

G. Conductors to Be Extended in the Future:  Attach [write-on tags] [marker tape] to conductors and list source and circuit number.

H. Auxiliary Electrical Systems Conductor Identification:  Identify field-installed alarm, control, signal, sound, intercommunications, voice, and data connections.

1. Identify conductors, cables, and terminals in enclosures and at junctions, terminals, and pull points.  Identify by system and circuit designation.

2. Use system of marker tape designations that is uniform and consistent with system used by manufacturer for factory-installed connections.

3. Coordinate identification with Project Drawings, manufacturer's wiring diagrams, and Operation and Maintenance Manual.

I. Locations of Underground Lines:  Identify with underground-line warning tape for power, lighting, communication, and control wiring and optical fiber cable.  [Limit use of underground-line warning tape to direct-buried cables] [Install underground-line warning tape for both direct-buried cables and cables in raceway].

J. Warning Labels for Indoor Cabinets, Boxes, and Enclosures for Power and Lighting:  Comply with 29 CFR 1910.145 and apply [self-adhesive warning labels] [baked-enamel warning signs] [metal-backed, butyrate warning signs].  Identify system voltage with black letters on an orange background.  Apply to exterior of door, cover, or other access.

1. Equipment with Multiple Power or Control Sources:  Apply to door or cover of equipment including, but not limited to, the following:

a. Power transfer switches.

b. Controls with external control power connections.

c. <Insert items.>

2. Equipment Requiring Workspace Clearance According to NFPA 70:  Unless otherwise indicated, apply to door or cover of equipment but not on flush panelboards and similar equipment in finished spaces.

K. Instruction Signs:

1. Operating Instructions:  Install instruction signs to facilitate proper operation and maintenance of electrical systems and items to which they connect.  Install instruction signs with approved legend where instructions are needed for system or equipment operation.

2. Emergency Operating Instructions:  Install instruction signs with white legend on a red background with minimum 3/8-inch- (10-mm-) high letters for emergency instructions at equipment used for [power transfer] [load shedding] <Insert emergency operations>.

Coordinate paragraph and subparagraphs below with electrical Sections in Divisions 2, 13, and 16.  Delete items not in Project.

L. Equipment Identification Labels:  On each unit of equipment, install unique designation label that is consistent with wiring diagrams, schedules, and Operation and Maintenance Manual.  Apply labels to disconnect switches and protection equipment, central or master units, control panels, control stations, terminal cabinets, and racks of each system.  Systems include power, lighting, control, communication, signal, monitoring, and alarm systems unless equipment is provided with its own identification.

1. Labeling Instructions:

a. Indoor Equipment:  [Adhesive film label] [Adhesive film label with clear protective overlay] [Self-adhesive, engraved, laminated acrylic or melamine label] [Engraved, laminated acrylic or melamine label].  Unless otherwise indicated, provide a single line of text with 1/2-inch- (13-mm-) high letters on 1-1/2-inch- (38-mm-) high label; where 2 lines of text are required, use labels 2 inches (50 mm) high.

b. Outdoor Equipment:  [Engraved, laminated acrylic or melamine label] [Stenciled legend 4 inches (100 mm) high].

c. Elevated Components:  Increase sizes of labels and letters to those appropriate for viewing from the floor.

2. Equipment to Be Labeled:

Identification labeling of some items listed below may be required by individual Sections or by NFPA 70.

a. Panelboards, electrical cabinets, and enclosures.

b. Access doors and panels for concealed electrical items.

c. Electrical switchgear and switchboards.

d. Transformers.

e. Electrical substations.

f. Emergency system boxes and enclosures.

g. Motor-control centers.

h. Disconnect switches.

i. Enclosed circuit breakers.

j. Motor starters.

k. Push-button stations.

l. Power transfer equipment.

m. Contactors.

n. Remote-controlled switches, dimmer modules, and control devices.

o. Battery inverter units.

p. Battery racks.

q. Power-generating units.

r. Voice and data cable terminal equipment.

s. Master clock and program equipment.

t. Intercommunication and call system master and staff stations.

u. Television/audio components, racks, and controls.

v. Fire-alarm control panel and annunciators.

w. Security and intrusion-detection control stations, control panels, terminal cabinets, and racks.

x. Monitoring and control equipment.

y. Uninterruptible power supply equipment.

z. Terminals, racks, and patch panels for voice and data communication and for signal and control functions.

aa. <Insert equipment.>

3.2 INSTALLATION

A. Verify identity of each item before installing identification products.

Coordinate first paragraph below with Drawings.

B. Location:  Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment.

C. Apply identification devices to surfaces that require finish after completing finish work.

Retain paragraph below if self-adhesive identification products are specified.

D. Self-Adhesive Identification Products:  Clean surfaces before application, using materials and methods recommended by manufacturer of identification device.

Retain paragraph below for nonadhesive signs or labels.

E. Attach nonadhesive signs and plastic labels with screws and auxiliary hardware appropriate to the location and substrate.

Retain paragraph below if color-coded bands are specified to identify different systems and distinguish one from another.

F. System Identification Color Banding for Raceways and Cables:  Each color band shall completely encircle cable or conduit.  Place adjacent bands of two-color markings in contact, side by side.  Locate bands at changes in direction, at penetrations of walls and floors, at 50-foot (15-m) maximum intervals in straight runs, and at 25-foot (7.6-m) maximum intervals in congested areas.

Retain first paragraph and subparagraphs below if color-coding of power and lighting conductors for phase or voltage level identification is required to satisfy the Code, authorities having jurisdiction, or special Project requirements.  If retaining, coordinate with Division 16 Section "Conductors and Cables" and edit to indicate extent of color-coding required.  For existing buildings, clarify if requirements apply to both old and new wiring or to new wiring only.  Below applies only to phase conductors.  Color-coding of grounded and grounding conductors is dictated by the Code.

G. Color-Coding for Phase[ and Voltage Level] Identification, 600 V and Less:  Use the colors listed below for ungrounded [service] [feeder] [branch-circuit] [service, feeder, and branch-circuit] conductors.

1. Color shall be [factory applied] [factory applied or, for sizes larger than No. 10 AWG if authorities having jurisdiction permit, field applied].

2. Colors for 208/120-V Circuits:

a. Phase A:  Black.

b. Phase B:  Red.

c. Phase C:  Blue.

3. Colors for 480/277-V Circuits:

Colors specified in three subparagraphs below are those generally used for phase conductors at this voltage.

a. Phase A:  Brown.

b. Phase B:  Orange.

c. Phase C:  Yellow.

If field-applied color-coding is permitted, retain subparagraph below.

4. Field-Applied, Color-Coding Conductor Tape:  Apply in half-lapped turns for a minimum distance of 6 inches (150 mm) from terminal points and in boxes where splices or taps are made.  Apply last two turns of tape with no tension to prevent possible unwinding.  Locate bands to avoid obscuring factory cable markings.

H. Aluminum Wraparound Marker Labels and Metal Tags:  Secure tight to surface of conductor or cable at a location with high visibility and accessibility.

I. Underground-Line Warning Tape:  During backfilling of trenches install continuous underground-line warning tape directly above line at 6 to 8 inches (150 to 200 mm) below finished grade.  Use multiple tapes where width of multiple lines installed in a common trench [or concrete envelope ]exceeds 16 inches (400 mm) overall.

J. Painted Identification:  Prepare surface and apply paint according to Division 9 painting Sections.

END OF SECTION 16075

ELECTRICAL IDENTIFICATION
16075 - 11

