Copyright 2006 AIA
MASTERSPEC Full Length
03/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16123 - CONTROL-VOLTAGE ELECTRICAL POWER CABLES
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. UTP cabling.

2. [50/125] [62.5/125]-micrometer, multimode optical fiber cabling.

3. RS-232 cabling.

4. RS-485 cabling.

5. Low-voltage control cabling.

6. Control-circuit conductors.

7. Identification products.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. Basket Cable Tray:  A fabricated structure consisting of wire mesh bottom and side rails.

B. Channel Cable Tray:  A fabricated structure consisting of a one-piece, ventilated-bottom or solid-bottom channel section.

C. EMI:  Electromagnetic interference.

D. IDC:  Insulation displacement connector.

E. Ladder Cable Tray:  A fabricated structure consisting of two longitudinal side rails connected by individual transverse members (rungs).

F. Low Voltage:  As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control and signaling power-limited circuits.

G. Open Cabling:  Passing telecommunications cabling through open space (e.g., between the studs of a wall cavity).

H. RCDD:  Registered Communications Distribution Designer.

I. Solid-Bottom or Nonventilated Cable Tray:  A fabricated structure consisting of integral or separate longitudinal side rails, and a bottom without ventilation openings.

J. Trough or Ventilated Cable Tray:  A fabricated structure consisting of integral or separate longitudinal rails and a bottom having openings sufficient for the passage of air and using 75 percent or less of the plan area of the surface to support cables.

K. UTP:  Unshielded twisted pair.

1.4 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  For cable tray layout, showing cable tray route to scale, with relationship between the tray and adjacent structural, electrical, and mechanical elements.  Include the following:

1. Vertical and horizontal offsets and transitions.

2. Clearances for access above and to side of cable trays.

3. Vertical elevation of cable trays above the floor or bottom of ceiling structure.

4. Load calculations to show dead and live loads as not exceeding manufacturer's rating for tray and its support elements.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For qualified layout technician, installation supervisor, and field inspector.

D. Source quality-control reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

E. Field quality-control reports.

F. Maintenance Data:  For wire and cable to include in maintenance manuals.

1.5 QUALITY ASSURANCE

Retain first paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 1 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications:  Member company of an NRTL.

Retain subparagraph below for UTP and optical fiber cabling.  See Editing Instruction No. 2 in the Evaluations for discussion of qualifications of the RCDD designation.

1. Testing Agency's Field Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

B. Surface-Burning Characteristics:  As determined by testing identical products according to ASTM E 84 by a qualified testing agency.  Identify products with appropriate markings of applicable testing agency.

1. Flame-Spread Index:  [25] <Insert value> or less.

2. Smoke-Developed Index:  [50] [450] <Insert value> or less.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

1.6 DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, telecommunications cables should be tested upon receipt.  Low-voltage wires and cables do not normally require testing before installation.

A. Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

1. Test optical fiber cable to determine the continuity of the strand end to end.  Use [optical fiber flashlight] [optical loss test set] [optical fiber flashlight or optical loss test set] <Insert test>.

2. Test optical fiber cable on reels.  Use an optical time domain reflectometer to verify the cable length and locate cable defects, splices, and connector; include the loss value of each.  Retain test data and include the record in maintenance data.

3. Test each pair of UTP cable for open and short circuits.

1.7 PROJECT CONDITIONS

A. Environmental Limitations:  Do not deliver or install UTP and optical fiber cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

PART 2 -  PRODUCTS

2.1 PATHWAYS

Retain first paragraph below if the use of open cabling is permitted.

A. Support of Open Cabling:  NRTL labeled for support of [Category 5e] [Category 6] <Insert other cabling types> cabling, designed to prevent degradation of cable performance and pinch points that could damage cable.

1. Support brackets with cable tie slots for fastening cable ties to brackets.

2. Lacing bars, spools, J-hooks, and D-rings.

3. Straps and other devices.

B. Cable Trays:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cable Management Solutions, Inc.

b. Cablofil Inc.

c. Cooper B-Line, Inc.

d. Cope - Tyco/Allied Tube & Conduit.

e. GS Metals Corp.

f. <Insert manufacturer's name>.

Besides both corrosion-protection options in subparagraph below, alternative methods include trays fabricated from Types 304 and 316 stainless steel, steel with electrogalvanized zinc plating then coated with yellow dichromate, steel coated with PVC, and steel with powder coating,

2. Cable Tray Materials:  Metal, suitable for indoors and protected against corrosion by [electroplated zinc galvanizing, complying with ASTM B 633, Type 1, not less than 0.000472 inch (0.012 mm) thick] [hot-dip galvanizing, complying with ASTM A 123/A 123M, Grade 0.55, not less than 0.002165 inch (0.055 mm) thick].

Retain one or more of five subparagraphs below.  If multiple types or various dimensions of cable trays are required, delete subparagraphs and indicate location and dimensions on Drawings.  Trays in first subparagraph are generally available in widths of between 2 and 24 inches (50 and 600 mm) and in depths of between 1 and 4 inches (25 and 100 mm).

a. Basket Cable Trays:  [6 inches (150 mm) wide and 2 inches (50 mm) deep] <Insert dimensions>.  Wire mesh spacing shall not exceed 2 by 4 inches (50 by 100 mm).

Trays in first subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm).

b. Trough or Ventilated Cable Trays:  [Nominally 6 inches (150 mm)] <Insert dimension> wide.

Trays in first subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm) and in rung spacings of between 6 and 18 inches (150 and 455 mm).

c. Ladder Cable Trays:  [Nominally 18 inches (455 mm)] <Insert dimension> wide, and a rung spacing of [12 inches (305 mm)] <Insert dimension>.

Trays in first subparagraph below are generally available in widths of 3, 4, and 6 inches (75, 100, and 150 mm).

d. Channel Cable Trays:  One-piece construction, [nominally 4 inches (100 mm)] <Insert dimension> wide.  Slot spacing shall not exceed 4-1/2 inches (115 mm) o.c.

Trays in subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm).

e. Solid-Bottom or Nonventilated Cable Trays:  One-piece construction, [nominally 12 inches (305 mm)] <Insert dimension> wide.  Provide [with] [without] solid covers.

C. Conduit and Boxes:  Comply with requirements in Division 16 Section "Raceways and Boxes."[  Flexible metal conduit shall not be used.]

1. Outlet boxes shall be no smaller than 2 inches (50 mm) wide, 3 inches (75 mm) high, and 2-1/2 inches (64 mm) deep.

2.2 BACKBOARDS

A. Description:  Plywood, [fire-retardant treated, ]3/4 by 48 by 96 inches (19 by 1220 by 2440 mm).  Comply with requirements for plywood backing panels in Division 6 Section "Rough Carpentry."

2.3 UTP CABLE

Copy this article and re-edit for each product if cable products with multiple four-pair binder groups are specified.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Belden CDT Inc.; Electronics Division.

2. Berk-Tek; a Nexans company.

3. CommScope, Inc.

4. Draka USA.

5. Genesis Cable Products; Honeywell International, Inc.

6. KRONE Incorporated.

7. Mohawk; a division of Belden CDT.

8. Nordex/CDT; a subsidiary of Cable Design Technologies.

9. Superior Essex Inc.

10. SYSTIMAX Solutions; a CommScope, Inc. brand.

11. 3M.

12. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

13. <Insert manufacturer's name>.

Revise option in paragraph below to specify cables of other than 25-pair binder groups.

B. Description:  100-ohm, four-pair UTP[, formed into 25-pair binder groups covered with a blue thermoplastic jacket].

1. Comply with ICEA S-90-661 for mechanical properties.

2. Comply with TIA/EIA-568-B.1 for performance specifications.

3. Comply with TIA/EIA-568-B.2, [Category 5e] [Category 6].

4. Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

a. Communications, General Purpose:  Type CM or Type CMG[; or Type MPP, Type CMP, Type MPR, Type CMR, Type MP, or Type MPG].

b. Communications, Plenum Rated:  Type CMP[ or Type MPP], complying with NFPA 262.

c. Communications, Riser Rated:  Type CMR[; or Type MPP, Type CMP, or Type MPR]; complying with UL 1666.

d. Communications, Limited Purpose:  Type CMX[; or Type MPP, Type CMP, Type MPR, Type CMR, Type MP, Type MPG, Type CM, or Type CMG].

e. Multipurpose:  Type MP or Type MPG[; or Type MPP or Type MPR].

f. Multipurpose, Plenum Rated:  Type MPP, complying with NFPA 262.

g. Multipurpose, Riser Rated:  Type MPR[ or Type MPP], complying with UL 1666.

2.4 UTP CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. American Technology Systems Industries, Inc.

2. Dynacom Corporation.

3. Hubbell Premise Wiring.

4. KRONE Incorporated.

5. Leviton Voice & Data Division.

6. Molex Premise Networks; a division of Molex, Inc.

7. Nordex/CDT; a subsidiary of Cable Design Technologies.

8. Panduit Corp.

9. Siemon Co. (The).

10. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

11. <Insert manufacturer's name>.

Type of connecting hardware depends on the equipment to which cable is connected.  Retain first paragraph below if UTP cable terminations are not specified with connected equipment.  Specifying connecting hardware permits testing of cables before they are connected to the equipment.

B. UTP Cable Connecting Hardware:  IDC type, using modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of the same category or higher.

Revise paragraph below to match equipment requirements; delete if connecting blocks are specified with the equipment.

C. Connecting Blocks:  [110 style for Category 5e] [110 style for Category 6] [66 style for Category 5e].  Provide blocks for the number of cables terminated on the block, plus [25] <Insert number> percent spare; integral with connector bodies, including plugs and jacks where indicated.

2.5 OPTICAL FIBER CABLE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Berk-Tek; a Nexans company.

2. CommScope, Inc.

3. Corning Cable Systems.

4. General Cable Technologies Corporation.

5. Mohawk; a division of Belden CDT.

6. Nordex/CDT; a subsidiary of Cable Design Technologies.

7. Optical Connectivity Solutions Division; Emerson Network Power.

8. Superior Essex Inc.

9. SYSTIMAX Solutions; a CommScope, Inc. brand.

10. 3M.

11. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

12. <Insert manufacturer's name>.

B. Description:  Multimode, [50/125] [62.5/125]-micrometer, [24] <Insert number>-fiber, [nonconductive, ]tight buffer, optical fiber cable.

1. Comply with ICEA S-83-596 for mechanical properties.

2. Comply with TIA/EIA-568-B.3 for performance specifications.

Retain first option in first subparagraph below for 50/125-micrometer cable; retain second option for 62.5/125-micrometer cable.

3. Comply with [TIA/EIA-492AAAA-B] [TIA/EIA-492AAAA-A] for detailed specifications.

4. Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444, UL 1651, and NFPA 70 for the following types:

Type requirements in first six subparagraphs below are minimum requirements and may need to be revised to suit Project.  Types OFC, OFCR, OFCG, and OFCP are conductive optical fiber cables that might have application in industrial settings.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

a. General Purpose, Nonconductive:  Type OFN or OFNG[, or Type OFNR or Type OFNP].

b. Plenum Rated, Nonconductive:  Type OFNP, complying with NFPA 262.

c. Riser Rated, Nonconductive:  Type OFNR[ or Type OFNP], complying with UL 1666.

d. General Purpose, Conductive:  Type OFC or Type OFCG[; or Type OFNG, Type OFN, Type OFCR, Type OFNR, Type OFCP, or Type OFNP].

e. Plenum Rated, Conductive:  Type OFCP[ or Type OFNP], complying with NFPA 262.

f. Riser Rated, Conductive:  Type OFCR[; or Type OFNR, Type OFCP, or Type OFNP]; complying with UL 1666.

Retain first subparagraph below even if nonconductive cable is specified in subparagraphs above.  If both conductive and nonconductive cables are specified, indicate locations of each on Drawings.

5. Conductive cable shall be [steel] [aluminum]-armored type.

6. Maximum Attenuation:  [3.5] <Insert number> dB/km at 850 nm; [1.5] <Insert number> dB/km at 1300 nm.

7. Minimum Modal Bandwidth:  160 MHz-km at 850 nm; 500 MHz-km at 1300 nm.

C. Jacket:

1. Jacket Color:  [Aqua for 50/125] [Orange for 62.5/125]-micrometer cable.

2. Cable cordage jacket, fiber, unit, and group color shall be according to TIA/EIA-598-B.

3. Imprinted with fiber count, fiber type, and aggregate length at regular intervals not to exceed 40 inches (1000 mm).

2.6 OPTICAL FIBER CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. ADC.

2. American Technology Systems Industries, Inc.

3. Berk-Tek; a Nexans company.

4. Corning Cable Systems.

5. Dynacom Corporation.

6. Hubbell Premise Wiring.

7. Molex Premise Networks; a division of Molex, Inc.

8. Nordex/CDT; a subsidiary of Cable Design Technologies.

9. Optical Connectivity Solutions Division; Emerson Network Power.

10. Siemon Co. (The).

11. <Insert manufacturer's name>.

Type of connecting hardware depends on the equipment to which cable is connected.  Retain paragraph below if optical fiber cable terminations are not specified with connected equipment.  Specifying connecting hardware permits testing of cables before they are connected to the equipment.

B. Cable Connecting Hardware:  Comply with the Fiber Optic Connector Intermateability Standards (FOCIS) specifications of TIA/EIA-604-2, TIA/EIA-604-3-A, and TIA/EIA-604-12.  Comply with TIA/EIA-568-B.3.

Type SC is a subscriber connector; Type ST is a straight-tip, single-fiber connector; both are commonly used.  Recently developed connectors are Type LC, which is an upgraded version of either Type SC or ST connector with a lower insertion loss, and Type MT-RJ, which is a no-epoxy, no-polish connector.

1. Quick-connect, simplex and duplex, [Type SC] [Type ST] [Type LC] [Type MT-RJ] connectors.  Insertion loss not more than 0.75 dB.

2. Type SFF connectors may be used in termination racks, panels, and equipment packages.

2.7 RS-232 CABLE

RS-232 communications require three conductors with an overall shield.  Circuit is limited to a distance of not more than 50 feet (15 m).

A. Standard Cable:  NFPA 70, Type CM.

1. Paired, two pairs, No. 22 AWG, stranded (7x30) tinned-copper conductors.

2. Polypropylene insulation.

3. Individual aluminum foil-polyester tape shielded pairs with 100 percent shield coverage.

4. PVC jacket.

5. Pairs are cabled on common axis with No. 24 AWG, stranded (7x32) tinned-copper drain wire.

6. Flame Resistance:  Comply with UL 1581.

B. Plenum-Rated Cable:  NFPA 70, Type CMP.

1. Paired, two pairs, No. 22 AWG, stranded (7x30) tinned-copper conductors.

2. Plastic insulation.

3. Individual aluminum foil-polyester tape shielded pairs with 100 percent shield coverage.

4. Plastic jacket.

5. Pairs are cabled on common axis with No. 24 AWG, stranded (7x32) tinned-copper drain wire.

6. Flame Resistance:  Comply with NFPA 262.

2.8 RS-485 CABLE

RS-485 communications require two twisted pairs.  Circuit is limited to a distance of not more than 4000 feet (1220 m).

A. Standard Cable:  NFPA 70, Type CM[ or Type CMG].

1. Paired, two pairs, twisted, No. 22 AWG, stranded (7x30) tinned-copper conductors.

2. PVC insulation.

3. Unshielded.

4. PVC jacket.

5. Flame Resistance:  Comply with UL 1581.

B. Plenum-Rated Cable:  NFPA 70, Type CMP.

1. Paired, two pairs, No. 22 AWG, stranded (7x30) tinned-copper conductors.

2. Fluorinated ethylene propylene insulation.

3. Unshielded.

4. Fluorinated ethylene propylene jacket.

5. Flame Resistance:  NFPA 262, Flame Test.

2.9 LOW-VOLTAGE CONTROL CABLE

Retain one or more of four paragraphs below; difference in paragraphs is the conductor size and insulation type.  Other conductor sizes and insulation types are available.

A. Paired Cable:  NFPA 70, Type CMG.

1. One pair, twisted, No. 16 AWG, stranded (19x29) tinned-copper conductors.

2. PVC insulation.

3. Unshielded.

4. PVC jacket.

5. Flame Resistance:  Comply with UL 1581.

B. Plenum-Rated, Paired Cable:  NFPA 70, Type CMP.

1. One pair, twisted, No. 16 AWG, stranded (19x29) tinned-copper conductors.

2. PVC insulation.

3. Unshielded.

4. PVC jacket.

5. Flame Resistance:  Comply with NFPA 262.

C. Paired Cable:  NFPA 70, Type CMG.

1. One pair, twisted, No. 18 AWG, stranded (19x30) tinned-copper conductors.

2. PVC insulation.

3. Unshielded.

4. PVC jacket.

5. Flame Resistance:  Comply with UL 1581.

D. Plenum-Rated, Paired Cable:  NFPA 70, Type CMP.

1. One pair, twisted, No. 18 AWG, stranded (19x30) tinned-copper conductors.

2. Fluorinated ethylene propylene insulation.

3. Unshielded.

4. Plastic jacket.

5. Flame Resistance:  NFPA 262, Flame Test.

2.10 CONTROL-CIRCUIT CONDUCTORS

Retain option for UL 44 in first two paragraphs below if retaining option for Type XHHN.

A. Class 1 Control Circuits:  Stranded copper, [Type THHN-THWN] [Type XHHN], in raceway, complying with [UL 83] [UL 44].

B. Class 2 Control Circuits:  Stranded copper, [Type THHN-THWN, in raceway] [Type XHHN, in raceway] [power-limited cable, concealed in building finishes] [power-limited tray cable, in cable tray], complying with [UL 83] [UL 44].

C. Class 3 Remote-Control and Signal Circuits:  Stranded copper, Type TW or Type TF, complying with UL 83.

2.11 IDENTIFICATION PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Brady Corporation.

2. HellermannTyton.

3. Kroy LLC.

4. Panduit Corp.

5. <Insert manufacturer's name>.

B. Comply with UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

C. Comply with requirements in Division 16 Section "Electrical Identification."

2.12 SOURCE QUALITY CONTROL

Retain first paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

A. Testing Agency:  Engage a qualified testing agency to evaluate cables.

B. Factory test UTP and optical fiber cables on reels according to TIA/EIA-568-B.1.

C. Factory test UTP cables according to TIA/EIA-568-B.2.

D. Factory test multimode optical fiber cables according to TIA/EIA-526-14-A and TIA/EIA-568-B.3.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

E. Cable will be considered defective if it does not pass tests and inspections.

F. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 INSTALLATION OF PATHWAYS

A. Cable Trays:  Comply with NEMA VE 2 and TIA/EIA-569-A-7.

B. Comply with TIA/EIA-569-A for pull-box sizing and length of conduit and number of bends between pull points.

C. Comply with requirements in Division 16 Section "Raceways and Boxes" for installation of conduits and wireways.

D. Install manufactured conduit sweeps and long-radius elbows if possible.

E. Pathway Installation in Equipment Rooms:

1. Position conduit ends adjacent to a corner on backboard if a single piece of plywood is installed or in the corner of room if multiple sheets of plywood are installed around perimeter walls of room.

2. Install cable trays to route cables if conduits cannot be located in these positions.

3. Secure conduits to backboard if entering room from overhead.

4. Extend conduits [3 inches (75 mm)] <Insert dimension> above finished floor.

5. Install metal conduits with grounding bushings and connect with grounding conductor to grounding system.

F. Backboards:  Install backboards with 96-inch (2440-mm) dimension vertical.  Butt adjacent sheets tightly and form smooth gap-free corners and joints.

3.2 INSTALLATION OF CONDUCTORS AND CABLES

A. Comply with NECA 1.

B. General Requirements for Cabling:

Retain one of first two subparagraphs below for UTP and optical fiber cabling.

1. Comply with TIA/EIA-568-B.1.

2. Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

3. Terminate all conductors; no cable shall contain unterminated elements.  Make terminations only at indicated outlets, terminals, and cross-connect and patch panels.

4. Cables may not be spliced.  Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

5. Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter.  Install lacing bars and distribution spools.

6. Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

7. Cold-Weather Installation:  Bring cable to room temperature before dereeling.  Heat lamps shall not be used for heating.

8. Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, "Pulling Cable."  Monitor cable pull tensions.

C. UTP Cable Installation:

1. Comply with TIA/EIA-568-B.2.

2. Install 110-style IDC termination hardware unless otherwise indicated.

3. Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

D. Installation of Control-Circuit Conductors:

1. Install wiring in raceways.  Comply with requirements specified in Division 16 Section "Raceways and Boxes."

E. Optical Fiber Cable Installation:

1. Comply with TIA/EIA-568-B.3.

2. Cable shall be terminated on connecting hardware that is rack or cabinet mounted.

F. Open-Cable Installation:

1. Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

2. Suspend copper cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceilings by cable supports not more than [60 inches (1525 mm)] <Insert dimension> apart.

3. Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

G. Installation of Cable Routed Exposed under Raised Floors:

1. Install plenum-rated cable only.

2. Install cabling after the flooring system has been installed in raised floor areas.

3. Coil cable [72 inches (1830 mm)] <Insert size> long shall be neatly coiled not less than [12 inches (305 mm)] <Insert size> in diameter below each feed point.

See Editing Instruction No. 3 in the Evaluations for discussion of EMI.

H. Separation from EMI Sources:

1. Comply with BICSI TDMM and TIA/EIA-569-A recommendations for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

2. Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches (127 mm).

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches (305 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches (600 mm).

3. Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches (64 mm).

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches (150 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches (305 mm).

4. Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  No requirement.

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches (75 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches (150 mm).

5. Separation between Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger:  A minimum of 48 inches (1200 mm).

6. Separation between Cables and Fluorescent Fixtures:  A minimum of 5 inches (127 mm).

3.3 REMOVAL OF CONDUCTORS AND CABLES

A. Remove abandoned conductors and cables.

3.4 CONTROL-CIRCUIT CONDUCTORS

A. Minimum Conductor Sizes:

1. Class 1 remote-control and signal circuits, [No 14] <Insert wire size> AWG.

2. Class 2 low-energy, remote-control, and signal circuits, [No. 16] <Insert wire size> AWG.

3. Class 3 low-energy, remote-control, alarm, and signal circuits, [No 12] <Insert wire size> AWG.

3.5 FIRESTOPPING

A. Comply with requirements in Division 7 Section "Through-Penetration Firestop Systems."

B. Comply with TIA/EIA-569-A, Annex A, "Firestopping."

C. Comply with BICSI TDMM, "Firestopping Systems" Article.

3.6 GROUNDING

Retain one or both paragraphs below.

A. For data communication wiring, comply with ANSI-J-STD-607-A and with BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

B. For low-voltage wiring and cabling, comply with requirements in Division 16 Section "Grounding and Bonding."

3.7 IDENTIFICATION

A. Identify system components, wiring, and cabling according to TIA/EIA-606-A.  Comply with requirements for identification specified in Division 16 Section "Electrical Identification."

3.8 FIELD QUALITY CONTROL

Retain one of first two paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Visually inspect UTP and optical fiber cable jacket materials for UL or third-party certification markings.  Inspect cabling terminations to confirm color-coding for pin assignments, and inspect cabling connections to confirm compliance with TIA/EIA-568-B.1.

2. Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

Retain first subparagraph below if verification of quality is to be performed before completion of the cabling.  Delete if not retaining cable connecting hardware in "UTP Cable Hardware" Article.

3. Test UTP cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination but not after cross connection.

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2.  Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

Retain subparagraph below if verification of quality is to be performed before completion of the cabling.  Delete if not retaining cable connecting hardware in "Optical Fiber Cable Hardware" Article.

4. Optical Fiber Cable Tests:

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.1.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

b. Link End-to-End Attenuation Tests:

1) Multimode Link Measurements:  Test at 850 or 1300 nm in one direction according to TIA/EIA-526-14-A, Method B, One Reference Jumper.

2) Attenuation test results for links shall be less than 2.0 dB.  Attenuation test results shall be less than that calculated according to equation in TIA/EIA-568-B.1.

D. Document data for each measurement.  Print data for submittals in a summary report that is formatted using Table 10.1 in BICSI TDMM as a guide, or transfer the data from the instrument to the computer, save as text files, print, and submit.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

E. End-to-end cabling will be considered defective if it does not pass tests and inspections.

F. Prepare test and inspection reports.

END OF SECTION 16123

CONTROL-VOLTAGE ELECTRICAL POWER CABLES
16123 - 1

