Copyright 2004 AIA
MASTERSPEC
06/04

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16139 - CABLE TRAYS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [steel] [aluminum] [stainless-steel] [fiberglass] cable trays and accessories.

1.3 SUBMITTALS

A. Product Data:  Include data indicating dimensions and finishes for each type of cable tray indicated.

B. Shop Drawings:  For each type of cable tray.

1. Show fabrication and installation details of cable tray, including plans, elevations, and sections of components and attachments to other construction elements.  Designate components and accessories, including clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings.

Retain subparagraph and associated subparagraphs below if products are required to withstand seismic loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify product's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

2. Seismic-Restraint Details:  Signed and sealed by a qualified professional engineer, licensed in the state where Project is located, who is responsible for their preparation.

a. Design Calculations:  Calculate requirements for selecting seismic restraints.

b. Detail fabrication, including anchorages and attachments to structure and to supported cable trays.

Retain first paragraph and subparagraphs below if Drawings do not include detailed floor plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Floor plans and sections, drawn to scale.  Include scaled cable tray layout and relationships between components and adjacent structural, electrical, and mechanical elements.  Show the following:

1. Vertical and horizontal offsets and transitions.

2. Clearances for access above and to side of cable trays.

3. Vertical elevation of cable trays above the floor or bottom of ceiling structure.

D. Field quality-control reports.

E. Operation and Maintenance Data:  For cable trays to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain cable tray components through one source from a single manufacturer.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

1.5 DELIVERY, STORAGE, AND HANDLING

Retain one of four paragraphs in this Article.

Retain one of first two paragraphs below depending on importance of tray's appearance.

A. [Steel cable tray, hot dip galvanized after fabrication,] [Aluminum cable tray] [Stainless-steel cable tray] [Fiberglass cable tray] may be stored outside without cover, but shall be loosely stacked, elevated off the ground, and ventilated to prevent staining during storage.

B. Store indoors to prevent water or other foreign materials from staining or adhering to cable tray.  Unpack and dry wet materials before storage.

C. Steel, [mill galvanized] [electrogalvanized] [factory-primed] cable tray shall be stored in a well-ventilated, dry location.  Unpack and dry wet materials before storage.

D. [PVC-coated] [Field-painted] cable tray shall be stored indoors.  Protect cable tray from scratching and marring of finish.  Unpack and dry wet materials before storage.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers in this Article.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Chalfant Manufacturing Company.

2. Cooper B-Line, Inc.

3. Cope, T. J., Inc.; a subsidiary of Allied Tube & Conduit.

4. GS Metals Corp.; GLOBETRAY Products.

5. MONO-SYSTEMS, Inc.

6. MPHusky.

7. PW Industries.

8. <Insert manufacturer's name.>

2.2 MATERIALS AND FINISHES

Select one of first four paragraphs and associated subparagraphs below.  See Evaluations for discussion of cable tray materials and finishes.

A. Cable Trays, Fittings, and Accessories:  Steel, complying with NEMA VE 1.

Retain one of seven subparagraphs below.

1. Factory-standard primer, ready for field painting; with cadmium-plated hardware according to ASTM B 766.

2. Mill galvanized before fabrication, complying with ASTM A 653/A 653M, G90 (Z275) coating; with hardware [galvanized according to ASTM B 633] [cadmium plated according to ASTM B 766].

3. Electrogalvanized before fabrication, complying with ASTM B 633; with hardware galvanized according to ASTM B 633.

4. Hot-dip galvanized after fabrication, complying with ASTM A 123/A 123M, Class B2; with [chromium-zinc, ASTM F 1136,] [Type 316 stainless-steel] hardware.

5. PVC coating applied in a fluidized bed or by electrostatic spray; with [chromium-zinc, ASTM F 1136] [Type 316 stainless-steel] hardware.

6. Epoxy-resin paint over paint manufacturer's recommended primer and corrosion-inhibiting treatment; with [cadmium-plated hardware according to ASTM B 766] [Type 316 stainless-steel hardware].

7. <Insert finish.>

B. Cable Trays, Fittings, and Accessories:  Aluminum, complying with NEMA VE 1, Aluminum Association's Alloy 6063-T6 for rails, rungs, and cable trays, and Alloy 5052-H32 or Alloy 6061-T6 for fabricated parts; with [chromium-zinc, ASTM F 1136,] [Type 316 stainless-steel] splice-plate fasteners, bolts, and screws

C. Cable Trays, Fittings, and Accessories:  Stainless steel, Type [304] [or] [316], complying with NEMA VE 1.

D. Cable Trays, Fittings, and Accessories:  Fiberglass, complying with NEMA FG 1 and UL 568.  Splice-plate fasteners, bolts, and screws shall be fiberglass-encapsulated stainless steel.  Design fasteners so that no metal is visible when fully assembled and tightened.  Fastener encapsulation shall not be damaged when torqued to manufacturer's recommended value.

E. Sizes and Configurations:  Refer to the Cable Tray Schedule on Drawings for specific requirements for types, materials, sizes, and configurations.

1. Center-hanger supports may be used only when specifically indicated.

2.3 CABLE TRAY ACCESSORIES

A. Fittings:  Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.

Select one of four cover options in paragraph below.  If more than one type is required, delete here and indicate on Drawings or in a schedule.  Delete paragraph if only single-rail-type cable tray is used or if cable tray covers are not required.

B. Covers:  [Solid] [Louvered] [Ventilated-hat] [2-in-3 pitch cover] type of same materials and finishes as cable tray.

Delete first paragraph below if not applicable.

C. Barrier Strips:  Same materials and finishes as cable tray.

D. Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer.

2.4 WARNING SIGNS

Revise size of lettering in first paragraph below to suit 25-foot (7.6-m) viewing distance.

A. Lettering:  1-1/2-inch- (40-mm-) high, black letters on yellow background with legend "WARNING!  NOT TO BE USED AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL."

B. Materials and fastening are specified in Division 16 Section "Electrical Identification."

2.5 SOURCE QUALITY CONTROL

A. Perform design and production tests according to [NEMA FG 1] [NEMA VE 1].

PART 3 -  EXECUTION

3.1 CABLE TRAY INSTALLATION

A. Comply with recommendations in NEMA VE 2.  Install as a complete system, including all necessary fasteners, hold-down clips, splice-plate support systems, barrier strips, hinged horizontal and vertical splice plates, elbows, reducers, tees, and crosses.

B. Remove burrs and sharp edges from cable trays.

C. Fasten cable tray supports to building structure[ and install seismic restraints].

1. Design each fastener and support to carry load indicated by seismic requirements[ and to comply with seismic-restraint details according to Division 16 Section "Electrical Supports and Seismic Restraints."]

2. Place supports so that spans do not exceed maximum spans on schedules.

3. Construct supports from channel members, threaded rods, and other appurtenances furnished by cable tray manufacturer.  Arrange supports in trapeze or wall-bracket form as required by application.

4. Support bus assembly to prevent twisting from eccentric loading.

5. Manufacture center-hung support, designed for 60 percent versus 40 percent eccentric loading condition, with a safety factor of 3.

6. Locate and install supports according to [NEMA FG 1] [NEMA VE 1].

Retain paragraph below if cable tray connects to equipment.

D. Make connections to equipment with flanged fittings fastened to cable tray and to equipment.  Support cable tray independent of fittings.  Do not carry weight of cable tray on equipment enclosure.

Retain first paragraph below if expansion fittings are required.

E. Install expansion connectors where cable tray crosses building expansion joint and in cable tray runs that exceed dimensions recommended in [NEMA FG 1] [NEMA VE 1].  Space connectors and set gaps according to applicable standard.

F. Make changes in direction and elevation using standard fittings.

G. Make cable tray connections using standard fittings.

H. Seal penetrations through fire and smoke barriers according to Division 7 Section "Through-Penetration Firestop Systems."

If cable trays are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions or use "repairable" firestop-sealing material.  Include specific firestopping requirements of this Section in a schedule developed in the Division 7 Section referenced in paragraph above.

I. Sleeves for Future Cables:  Install capped sleeves for future cables through firestop-sealed cable tray penetrations of fire and smoke barriers.

J. Workspace:  Install cable trays with enough space to permit access for installing cables.

Retain first paragraph below if systems are mixed.

K. Install barriers to separate cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600, 5000, and 15 000 V.

L. After installation of cable trays is completed, install warning signs in visible locations on or near cable trays.

3.2 CABLE INSTALLATION

Retain first two paragraphs below if applicable; these requirements are optional in NEMA VE 2.

A. Install cables only when cable tray installation has been completed and inspected.

B. Fasten cables on horizontal runs with cable clamps or cable ties as recommended by NEMA VE 2.  Tighten clamps only enough to secure the cable, without indenting the cable jacket.  Install cable ties with a tool that includes an automatic pressure-limiting device.

C. On vertical runs, fasten cables to tray every 18 inches (457 mm).  Install intermediate supports when cable weight exceeds the load-carrying capacity of the tray rungs.

D. In existing construction, remove inactive or dead cables from cable tray.

E. Install covers after installation of cable is completed.

3.3 CONNECTIONS

A. Ground cable trays according to manufacturer's written instructions.

Retain paragraph below for metallic cable trays if grounding, in addition to tray metallic path, is desired.

B. Install an insulated equipment grounding conductor with cable tray, in addition to those required by NFPA 70.

3.4 FIELD QUALITY CONTROL

A. After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements.  Perform the following field quality-control survey:

1. Visually inspect cable insulation for damage.  Correct sharp corners, protuberances in cable tray, vibration, and thermal expansion and contraction conditions, which may cause or have caused damage.

2. Verify that the number, size, and voltage of cables in cable tray do not exceed that permitted by NFPA 70.  Verify that communication or data-processing circuits are separated from power circuits by barriers.

3. Verify that there is no intrusion of such items as pipe, hangers, or other equipment that could damage cables.

4. Remove deposits of dust, industrial process materials, trash of any description, and any blockage of tray ventilation.

5. Visually inspect each cable tray joint and each ground connection for mechanical continuity.  Check bolted connections between sections for corrosion.  Clean and retorque in suspect areas.

6. Check for missing or damaged bolts, bolt heads, or nuts.  When found, replace with specified hardware.

7. Perform visual and mechanical checks for adequacy of cable tray grounding; verify that all takeoff raceways are bonded to cable tray.

B. Report results in writing.

3.5 PROTECTION

A. Protect installed cable trays.

1. Repair damage to galvanized finishes with zinc-rich paint recommended by cable tray manufacturer.

2. Repair damage to PVC or paint finishes with matching touchup coating recommended by cable tray manufacturer.

3. Install temporary protection for cables in open trays to protect exposed cables from falling objects or debris during construction.  Temporary protection for cables and cable tray can be constructed of wood or metal materials until the risk of damage is over.

END OF SECTION 16139

CABLE TRAYS
16139 - 1

