Copyright 2002 AIA
MASTERSPEC
09/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 16289 - TRANSIENT VOLTAGE SUPPRESSION
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes TVSSs for low-voltage power, control, and communication equipment.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 16 Section "Wiring Devices" for devices with integral TVSSs.

2. Division 16 Section "Switchboards" for factory-installed TVSSs.

3. Division 16 Section "Panelboards" for factory-installed TVSSs.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. ATS:  Acceptance Testing Specifications.

B. SVR:  Suppressed voltage rating.

C. TVSS:  Transient voltage surge suppressor.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include rated capacities, operating weights, operating characteristics, furnished specialties, and accessories.

B. Product Certificates:  For transient voltage suppression devices, signed by product manufacturer certifying compliance with the following standards:

1. UL 1283.

2. UL 1449.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For testing agency.

Retain first paragraph and subparagraphs below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports, including the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Failed test results and corrective action taken to achieve requirements.

E. Operation and Maintenance Data:  For transient voltage suppression devices to include in emergency, operation, and maintenance manuals.

F. Warranties:  Special warranties specified in this Section.

1.5 QUALITY ASSURANCE

If an independent testing agency is required, see Division 1 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent testing agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Source Limitations:  Obtain suppression devices and accessories through one source from a single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

C. Product Options:  Drawings indicate size, dimensional requirements, and electrical performance of suppressors and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with IEEE C62.41, "IEEE Guide for Surge Voltages in Low Voltage AC Power Circuits," and test devices according to IEEE C62.45, "IEEE Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits."

F. Comply with NEMA LS 1, "Low Voltage Surge Protection Devices."

G. Comply with UL 1283, "Electromagnetic Interference Filters," and UL 1449, "Transient Voltage Surge Suppressors."

1.6 PROJECT CONDITIONS

Retain first paragraph below for existing utilities.  Coordinate with requirements specified in Division 1 Section "Temporary Facilities and Controls" for temporary utilities.

A. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Revise first subparagraph below to suit Project.

1. Notify Architect not less than two days in advance of proposed utility interruptions.

2. Do not proceed with utility interruptions without Architect's written permission.

B. Service Conditions:  Rate surge protection devices for continuous operation under the following conditions, unless otherwise indicated:

1. Maximum Continuous Operating Voltage:  Not less than 115 percent of nominal system operating voltage.

2. Operating Temperature:  30 to 120 deg F (0 to 50 deg C).

3. Humidity:  0 to 85 percent, noncondensing.

4. Altitude:  Less than 20,000 feet (6090 m) above sea level.

1.7 COORDINATION

Retain first paragraph below for field-mounted suppressors.

A. Coordinate location of field-mounted surge suppressors to allow adequate clearances for maintenance.

B. Coordinate surge protection devices with Division 16 Section "Electrical Power Monitoring and Control."

1.8 WARRANTY

Most manufacturers offer five-year extended warranties on their equipment.  Some manufacturers of cord-connected, plug-in surge suppressors offer extended warranties that either repair or replace damaged equipment that is protected by the suppressor.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of surge suppressors that fail in materials or workmanship within five years from date of Substantial Completion.

Retain paragraph below if equipment repair or replacement is included.

B. Special Warranty for Cord-Connected, Plug-in Surge Suppressors:  Manufacturer's standard form in which manufacturer agrees to repair or replace electronic equipment connected to circuits protected by surge suppressors.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Replaceable Protection Modules:  One of each size and type installed.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Advanced Protection Technologies, Inc.

2. Atlantic Scientific.

3. Current Technology, Inc.

4. Cutler-Hammer, Inc.; Eaton Corporation.

5. Entrelec International.

6. General Electric Company.

7. Innovative Technology, Inc.

8. Intermatic, Inc.

9. LEA International.

10. Leviton Mfg. Company Inc.

11. Liebert Corporation; a division of Emerson.

12. Northern Technologies, Inc.

13. Siemens Energy & Automation, Inc.

14. Square D; Schneider Electric.

15. Surge Suppression Incorporated.

16. Sutton Designs Inc.

17. Transtector Systems, Inc.

18. Tycor; Cutler-Hammer, Inc.

19. United Power Corporation.

20. Zero Surge Inc.

21. <Insert manufacturer's name.>

2.2 SERVICE ENTRANCE SUPPRESSORS

Retain one of two paragraphs and associated subparagraphs below.  Comply with manufacturer's written recommendations for connecting TVSS devices to distribution system.

A. Surge Protection Device Description:  Non-modular, sine-wave-tracking type with the following features and accessories:

Retain accessories in three subparagraphs below to suit Project.

1. LED indicator lights for power and protection status.

2. Audible alarm, with silencing switch, to indicate when protection has failed.

3. One set of dry contacts rated at 5 A and 250-V ac, for remote monitoring of protection status.

B. Surge Protection Device Description:  Modular design with field-replaceable modules, sine-wave-tracking type with the following features and accessories:

Retain accessories in 11 subparagraphs below to suit Project; verify availability and compatibility with manufacturer.

If specifying fuses for connecting TVSS devices to distribution system, verify ability of fuses to withstand surges consistent with ultimate surge current rating of device.

1. Fuses, rated at 200-kA interrupting capacity.

2. Fabrication using bolted compression lugs for internal wiring.

3. Integral disconnect switch.

4. Redundant suppression circuits.

5. Redundant replaceable modules.

6. Arrangement with copper bus bars and for bolted connections to phase buses, neutral bus, and ground bus.

Retain subparagraph above or first subparagraph below depending on service entrance equipment.

7. Arrangement with wire connections to phase buses, neutral bus, and ground bus.

8. LED indicator lights for power and protection status.

9. Audible alarm, with silencing switch, to indicate when protection has failed.

10. One set of dry contacts rated at 5 A and 250-V ac, for remote monitoring of protection status.  Coordinate with building power monitoring and control system.

11. Surge-event operations counter.

Retain first option in first paragraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

C. Peak Single-Impulse Surge Current Rating:  [320] [240] [160] kA per phase.

D. Connection Means:  Permanently wired.

Retain one of four paragraphs and associated subparagraphs below.  Adjust clamping voltages to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage.  Reference to UL 1449 is to the Second Edition.

E. Protection modes and UL 1449 SVR for grounded wye circuits with voltages of [480Y/277] [208Y/120] [600Y/347], 3-phase, 4-wire circuits shall be as follows:

1. Line to Neutral:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

2. Line to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

3. Neutral to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

F. Protection modes and UL 1449 SVR for 240/120-V, single-phase, 3-wire circuits shall be as follows:

1. Line to Neutral:  400 V.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

G. Protection modes and UL 1449 SVR for 240/120-V, 3-phase, 4-wire circuits with high leg shall be as follows:

1. Line to Neutral:  400 V, 800 V from high leg.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

H. Protection modes and UL 1449 SVR for voltages of 240, 480, or 600, 3-phase, 3-wire, delta circuits shall be as follows:

1. Line to Line:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

2. Line to Ground:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

2.3 PANELBOARD SUPPRESSORS

Retain one of two paragraphs and associated subparagraphs below.  Comply with manufacturer's written recommendations for connecting TVSS devices to distribution system.

A. Surge Protection Device Description:  Non-modular, sine-wave-tracking type with the following features and accessories:

Retain accessories in three subparagraphs below to suit Project.

1. LED indicator lights for power and protection status.

2. Audible alarm, with silencing switch, to indicate when protection has failed.

3. One set of dry contacts rated at 5 A and 250-V ac, for remote monitoring of protection status.

B. Surge Protection Device Description:  Modular design with field-replaceable modules, sign-wave-tracking type with the following features and accessories:

Retain accessories in 10 subparagraphs below to suit Project; verify availability and compatibility with manufacturer.

If specifying fuses for connecting TVSS devices to distribution system, verify ability of fuses to withstand surges consistent with ultimate surge current rating of device.

1. Fuses, rated at 200-kA interrupting capacity.

2. Fabrication using bolted compression lugs for internal wiring.

3. Integral disconnect switch.

4. Redundant suppression circuits.

5. Redundant replaceable modules.

6. Arrangement with wire connections to phase buses, neutral bus, and ground bus.

7. LED indicator lights for power and protection status.

8. Audible alarm, with silencing switch, to indicate when protection has failed.

9. One set of dry contacts rated at 5 A and 250-V, ac, for remote monitoring of protection status.  Coordinate with building power monitoring and control system.

10. Surge-event operations counter.

Retain first option in paragraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

C. Peak Single-Impulse Surge Current Rating:  [160] [120] [80] kA per phase.

Retain one of four paragraphs and associated subparagraphs below.  Adjust clamping voltages to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage.  Reference to UL 1449 is to the Second Edition.

D. Protection modes and UL 1449 SVR for grounded wye circuits with voltages of [480Y/277] [208Y/120] [600Y/347], 3-phase, 4-wire circuits shall be as follows:

1. Line to Neutral:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

2. Line to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

3. Neutral to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

E. Protection modes and UL 1449 SVR for 240/120-V, single-phase, 3-wire circuits shall be as follows:

1. Line to Neutral:  400 V.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

F. Protection modes and UL 1449 SVR for 240/120-V, 3-phase, 4-wire circuits with high leg shall be as follows:

1. Line to Neutral:  400 V, 800 V from high leg.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

G. Protection modes and UL 1449 SVR for voltages of 240, 480, or 600, 3-phase, 3-wire, delta circuits shall be as follows:

1. Line to Line:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

2. Line to Ground:  [1500 V for 480 V] [800 V for 240 V] [2500 V for 600 V].

2.4 SUPPRESSORS FOR ELECTRONIC-GRADE PANELBOARDS

A. Surge Protection Device Description:  Sine-wave-tracking type, panel-mounted design with the following features and accessories:

Retain accessories in four subparagraphs below to suit Project.

1. LED indicator lights for power and protection status.

2. Audible alarm, with silencing switch, to indicate when protection has failed.

3. One set of dry contacts rated at 5 A and 250-V ac, for remote monitoring of protection status.

4. Arrangement with wire connections to phase buses, neutral bus, and ground bus.

Retain first option in paragraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

B. Peak Single-Impulse Surge Current Rating:  [160] [120] [80] kA per phase.

Retain one of four paragraphs and associated subparagraphs below.  Adjust clamping voltages to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage.  Reference to UL 1449 is to the Second Edition.

C. Protection modes and UL 1449 SVR for grounded wye circuits with voltages of [480Y/277] [208Y/120] [600Y/347], 3-phase, 4-wire circuits shall be as follows:

1. Line to Neutral:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

2. Line to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

3. Neutral to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

D. Protection modes and UL 1449 SVR for 240/120-V, single-phase, 3-wire circuits shall be as follows:

1. Line to Neutral:  400 V.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

E. Protection modes and UL 1449 SVR for 240/120-V, 3-phase, 4-wire circuits with high leg shall be as follows:

1. Line to Neutral:  400 V, 800 V from high leg.

2. Line to Ground:  400 V.

3. Neutral to Ground:  400 V.

F. Protection modes and UL 1449 SVR for voltages of 240, 480, or 600, 3-phase, 3-wire, delta circuits shall be as follows:

1. Line to Line:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

2. Line to Ground:  [1500 V for 480 V] [800 V for 240 V] [2500 V for 600 V].

2.5 PLUG-IN SURGE SUPPRESSORS

A. Description:  Non-modular, plug-in suppressors with at least four 15-A, 120-V ac, NEMA WD 6, Configuration 15-15R receptacles, suitable to plug into a NEMA WD 6, Configuration 15-15R receptacle; with the following features and accessories:

1. LED indicator lights for power and protection status.

2. LED indicator lights for reverse polarity and open outlet ground.

3. Circuit breaker and thermal fusing.  When protection is lost, circuit opens and cannot be reset.

Retain subparagraph above or first subparagraph below.

4. Circuit breaker and thermal fusing.  Unit continues to supply power if protection is lost.

5. [Close-coupled direct plug-in] [Cord connected with 15-foot (4.5-m) line cord].

6. Rocker-type on-off switch, illuminated when in the on position.

7. One RJ11/12C telephone line protector, suitable for modem connection.  Maximum clamping voltage 220 peak on pins No. 3 and No. 4.

Retain first option in first paragraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

B. Peak Single-Impulse Surge Current Rating:  [33] [26] [13] kA per phase.

C. Protection modes and UL 1449 SVR shall be as follows:

1. Line to Neutral:  475 V.

2. Line to Ground:  475 V.

3. Neutral to Ground:  475 V.

2.6 ENCLOSURES

A. NEMA 250, with type matching the enclosure of panel or device being protected.

PART 3 -  EXECUTION

3.1 INSTALLATION OF SURGE PROTECTION DEVICES

A. Install devices at service entrance on load side, with ground lead bonded to service entrance ground.

B. Install devices for panelboard and auxiliary panels with conductors or buses between suppressor and points of attachment as short and straight as possible.  Do not exceed manufacturer's recommended lead length.  Do not bond neutral and ground.

Comply with manufacturer's written recommendation for conductor and circuit-breaker size for connecting TVSS devices to distribution system.  Match circuit-breaker size to conductor size.  Coordinate with Drawings.

1. Provide multipole, [30] [60] [100]-A circuit breaker as a dedicated disconnect for suppressor, unless otherwise indicated.

3.2 PLACING SYSTEM INTO SERVICE

A. Do not energize or connect [service entrance equipment] [panelboards] [control terminals] [data terminals] to their sources until surge protection devices are installed and connected.

3.3 FIELD QUALITY CONTROL

Retain paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] equipment installation, including connections[, and to assist in field testing].  Report results in writing.

1. Verify that electrical wiring installation complies with manufacturer's written installation requirements.

Retain one of first two paragraphs below.

B. Testing:  [Owner will engage] [Engage] a qualified testing and inspecting agency to perform field tests and inspections and prepare test reports:

C. Testing:  Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with either of last two paragraphs above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

1. After installing surge protection devices, but before electrical circuitry has been energized, test for compliance with requirements.

2. Complete startup checks according to manufacturer's written instructions.

3. Perform each visual and mechanical inspection and electrical test stated in NETA ATS, "Surge Arresters, Low-Voltage Surge Protection Devices" Section.  Certify compliance with test parameters.

D. Remove and replace malfunctioning units and retest as specified above.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain transient voltage suppression devices.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 16289

TRANSIENT VOLTAGE SUPPRESSION
16289 - 10

