Copyright 2005 AIA
MASTERSPEC Full Length
12/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16442 - PANELBOARDS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Distribution panelboards.

2. Lighting and appliance branch-circuit panelboards.

3. Load centers.

4. Electronic-grade panelboards.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. SVR:  Suppressed voltage rating.

B. TVSS:  Transient voltage surge suppressor.

1.4 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

A. Seismic Performance:  Panelboards shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of panelboard, switching and overcurrent protective device, transient voltage suppression device, accessory, and component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each panelboard and related equipment.

1. Include dimensioned plans, elevations, sections, and details.  Show tabulations of installed devices, equipment features, and ratings.

2. Detail enclosure types and details for types other than NEMA 250, Type 1.

3. Detail bus configuration, current, and voltage ratings.

4. Short-circuit current rating of panelboards and overcurrent protective devices.

Retain first subparagraph below if series rating of overcurrent protective devices is used.

5. Include evidence of NRTL listing for series rating of installed devices.

6. Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

7. Include wiring diagrams for power, signal, and control wiring.

Retain subparagraph below if final system short-circuit and coordination studies will be performed by designer or assigned to independent consultant.  These curves are also beneficial to Owner for future additions or reevaluations of settings of overcurrent protective devices.

8. Include time-current coordination curves for each type and rating of overcurrent protective device included in panelboards.  Submit on translucent log-log graft paper; include selectable ranges for each type of overcurrent protective device.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For qualified testing agency.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Vibration and Seismic Controls for Electrical Systems." See SEI/ASCE 7 for certification requirements for equipment and components.

D. Seismic Qualification Certificates:  Submit certification that panelboards, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Division 16 Section "Vibration and Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

E. Field Quality-Control Reports:

1. Test procedures used.

2. Test results that comply with requirements.

3. Results of failed tests and corrective action taken to achieve test results that comply with requirements.

Retain option in first paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

F. Panelboard Schedules:  For installation in panelboards.[  Submit final versions after load balancing.]

G. Operation and Maintenance Data:  For panelboards and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "Operation and Maintenance Data," include the following:

1. Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

2. Time-current curves, including selectable ranges for each type of overcurrent protective device that allows adjustments.

1.6 QUALITY ASSURANCE

Retain first paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 1 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications:  Member company of NETA or an NRTL.

1. Testing Agency's Field Supervisor:  Currently certified by NETA to supervise on-site testing.

B. Source Limitations:  Obtain panelboards, overcurrent protective devices, components, and accessories from single source from single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

C. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for panelboards including clearances between panelboards and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

E. Comply with NEMA PB 1.

F. Comply with NFPA 70.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Remove loose packing and flammable materials from inside panelboards; install temporary electric heating (250 W per panelboard) to prevent condensation.

See "Testing and Inspecting" Article in the Evaluations for guidance on which option to select in paragraph below.

B. Handle and prepare panelboards for installation according to [NECA 407] [NEMA PB 1].

1.8 PROJECT CONDITIONS

Retain first paragraph below for panelboards installed in typical environmental conditions.  For panelboards installed outdoors, in unconditioned spaces, or in unusual environmental conditions, revise paragraph to indicate maximum ambient temperature and expected humidity range.  See Editing Instruction No. 2 in the Evaluations.

A. Environmental Limitations:

1. Do not deliver or install panelboards until spaces are enclosed and weathertight, wet work in spaces is complete and dry, work above panelboards is complete, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

2. Rate equipment for continuous operation under the following conditions unless otherwise indicated:

In first subparagraph below, select first option for panelboards with fused switches; select second option for panelboards with circuit breakers.

a. Ambient Temperature:  Not exceeding [minus 22 deg F (minus 30 deg C)] [23 deg F (minus 5 deg C)] to plus 104 deg F (plus 40 deg C).

b. Altitude:  Not exceeding 6600 feet (2000 m).

Retain first paragraph below or revise to accommodate unusual service conditions that cannot be eliminated.  See Editing Instructions No. 2 and No. 3 in the Evaluations.

B. Service Conditions:  NEMA PB 1, usual service conditions, as follows:

1. Ambient temperatures within limits specified.

2. Altitude not exceeding 6600 feet (2000 m).

Retain paragraph below if interruption of existing electric service is required.

C. Interruption of Existing Electric Service:  Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of electric service.

2. Do not proceed with interruption of electric service without [Architect's] [Construction Manager's] [Owner's] written permission.

3. Comply with NFPA 70E.

1.9 COORDINATION

Revise first paragraph below for types of equipment that affect panelboard installation.

A. Coordinate layout and installation of panelboards and components with other construction that penetrates walls or is supported by them, including electrical and other types of equipment, raceways, piping, encumbrances to workspace clearance requirements, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

Retain paragraph below if freestanding panelboards are specified.

B. Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.10 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

1. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

1.11 EXTRA MATERIALS

Revise this article to include extra materials that Owner may require, such as GFCI or GFEP circuit breakers or circuit breakers used for switching service, which may fail more frequently due to continuous use.

Coordinate with Division 16 Section "Fuses" for quantities of spare fuses and spare-fuse cabinet to be provided.

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Keys:  [Two] <Insert number> spares for each type of panelboard cabinet lock.

2. Circuit Breakers Including GFCI and Ground Fault Equipment Protection (GFEP) Types:  [Two] <Insert number> spares for each panelboard.

3. Fuses for Fused Switches:  Equal to 10 percent of quantity installed for each size and type, but no fewer than three of each size and type.

4. Fuses for Fused Power-Circuit Devices:  Equal to 10 percent of quantity installed for each size and type, but no fewer than three of each size and type.

5. <Insert extra materials>.

PART 2 -  PRODUCTS

2.1 GENERAL REQUIREMENTS FOR PANELBOARDS

Retain first paragraph below for projects in seismic areas.  Coordinate with "Submittals" Article for submittal of manufacturer's seismic qualification certification.

A. Fabricate and test panelboards according to IEEE 344 to withstand seismic forces defined in Division 16 Section "Vibration and Seismic Controls for Electrical Systems."

B. Enclosures:  [Flush] [Surface] [Flush- and surface]-mounted cabinets.

1. Rated for environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types.  Coordinate first five subparagraphs below with Drawings (by identifying the designated areas) or schedules (by including the required enclosure type).  Availability of some enclosure types are limited by a panelboard's ampacity rating, included devices, or physical size; consult manufacturers for availability of, and limitations on, other than Type 1 enclosures.

a. Indoor Dry and Clean Locations:  NEMA 250, [Type 1] <Insert type>.

b. Outdoor Locations:  NEMA 250, [Type 3R] <Insert type>.

c. [Kitchen] [Wash-Down] Areas:  NEMA 250, [Type 4X] <Insert type>, [stainless steel] <Insert material>.

d. Other Wet or Damp Indoor Locations:  NEMA 250, [Type 4] <Insert type>.

Select first option in first subparagraph below for areas subject to lighter levels of contaminants and second option for areas subject to heavier levels.

e. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids:  NEMA 250, [Type 5] [Type 12].

Retain one of first two subparagraphs below.

2. Front:  Secured to box with concealed trim clamps.  For surface-mounted fronts, match box dimensions; for flush-mounted fronts, overlap box.

3. Hinged Front Cover:  Entire front trim hinged to box and with standard door within hinged trim cover.

First two subparagraphs below are optional features.  Coordinate with Drawings.

4. Skirt for Surface-Mounted Panelboards:  Same gage and finish as panelboard front with flanges for attachment to panelboard, wall, and ceiling or floor.

5. Gutter Extension and Barrier:  Same gage and finish as panelboard enclosure; integral with enclosure body.  Arrange to isolate individual panel sections.

Coordinate first subparagraph below with "Enclosures" Paragraph above.  Back boxes are also available painted.  Revise if required to include special finishes to match, e.g., stainless steel, epoxy, and fiberglass-reinforced polyester.

6. Finishes:

a. Panels and Trim:  [Steel] [and] [galvanized steel], factory finished immediately after cleaning and pretreating with manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat.

b. Back Boxes:  [Galvanized steel] [Same finish as panels and trim].

Retain first subparagraph below for installations in humid tropical environments.

c. Fungus Proofing:  Permanent fungicidal treatment for overcurrent protective devices and other components.

Retain first subparagraph below for use with lighting and appliance branch-circuit and distribution panelboards with doors.  With the increasing use of computer-generated directories, metal frames are becoming an expensive option for most manufacturers.

7. Directory Card:  Inside panelboard door, mounted in [transparent card holder] [metal frame with transparent protective cover].

8. <Insert optional features>.

Retain first paragraph below, and coordinate with Drawings and schedules, if Project requirements include identifying specific entry locations for incoming service or feeder raceways.

C. Incoming Mains Location:  [Top] [Bottom] [Top and bottom].

D. Phase, Neutral, and Ground Buses:

In first subparagraph below, first option is standard with most manufacturers; second option costs more.

1. Material:  [Tin-plated aluminum] [Hard-drawn copper, 98 percent conductivity].

Five subparagraphs below are optional features.  Ground and neutral buses in lighting and appliance panelboards are also referred to as "bars" in manufacturers' literature.  Coordinate with Drawings.

2. Equipment Ground Bus:  Adequate for feeder and branch-circuit equipment grounding conductors; bonded to box.

Isolated ground bus in first subparagraph below is sometimes physically located above and attached to the equipment ground bus with standoff insulators.  Frequently and incorrectly, contractors connect equipment grounding conductors to this bus instead of to the equipment ground bus, which can be hazardous if separate equipment grounding and isolated ground conductors are not both included in the feeder serving the panelboard.

3. Isolated Ground Bus:  Adequate for branch-circuit isolated ground conductors; insulated from box.

4. Extra-Capacity Neutral Bus:  Neutral bus rated 200 percent of phase bus and UL listed as suitable for nonlinear loads.

5. Split Bus:  Vertical buses divided into individual vertical sections.

6. <Insert optional features>.

Include instructions in first paragraph below if special sizing or oversizing of lugs is required, if allowing optional use of aluminum for circuits sized for copper conductors, or when upsizing conductors for voltage drop.

E. Conductor Connectors:  Suitable for use with conductor material and sizes.

1. Material:  [Tin-plated aluminum] [Hard-drawn copper, 98 percent conductivity].

2. Main and Neutral Lugs:  [Compression] [Mechanical] type.

See Editing Instruction No. 4 in the Evaluations for guidance on using compression versus mechanical lugs in first four subparagraphs below.

3. Ground Lugs and Bus-Configured Terminators:  [Compression] [Mechanical] type.

First three subparagraphs below are optional features.

4. Feed-Through Lugs:  [Compression] [Mechanical] type, suitable for use with conductor material.  Locate at opposite end of bus from incoming lugs or main device.

In first subparagraph below, NEMA PB 1 allows subfeed lugs to be located on the load or line side of main devices or on main-lugs-only panelboards; however, coordinate with specific manufacturers as some have restrictions on which options are available.

5. Subfeed (Double) Lugs:  [Compression] [Mechanical] type suitable for use with conductor material.  Locate at same end of bus as incoming lugs or main device.

6. Gutter-Tap Lugs:  [Compression] [Mechanical] type suitable for use with conductor material.  Locate at same end of bus as incoming lugs or main device.

7. Extra-Capacity Neutral Lugs:  Rated 200 percent of phase lugs mounted on extra-capacity neutral bus.

8. <Insert optional features>.

Retain first paragraph below for panelboards that incorporate one or more main service disconnecting and overcurrent protective devices and that are used as the service entrance, outside feeder, or separately derived source means of disconnect and overcurrent protection.

F. Service Equipment Label:  NRTL labeled for use as service equipment for panelboards or load centers with one or more main service disconnecting and overcurrent protective devices.

Retain first paragraph below if future provisions are required.

G. Future Devices:  Mounting brackets, bus connections, filler plates, and necessary appurtenances required for future installation of devices.

Retain one or both paragraphs below for series-rated system or system that has panelboards and circuit breakers rated for full value of short-circuit current available at location of equipment.

H. Panelboard Short-Circuit Current Rating:  Rated for series-connected system with integral or remote upstream overcurrent protective devices and labeled by an NRTL.  Include size and type of allowable upstream and branch devices, listed and labeled for series-connected short-circuit rating by an NRTL.

I. Panelboard Short-Circuit Current Rating:  Fully rated to interrupt symmetrical short-circuit current available at terminals.

2.2 DISTRIBUTION PANELBOARDS

Distribution panelboards, as specified in this article, fall under requirements of "Power Panelboards" in NFPA 70.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. Panelboards:  NEMA PB 1, power and feeder distribution type.

Distribution panelboards, as standard, do not have doors; consult manufacturers for availability and types of doors.  Retain first paragraph below if panelboards have doors.

D. Doors:  Secured with vault-type latch with tumbler lock; keyed alike.

1. For doors more than [36 inches (914 mm)] <Insert dimension> high, provide two latches, keyed alike.

Select one of first two options in first paragraph below for panelboards with main overcurrent protective devices; select third option for panelboards with only main lugs for the incoming feeder.  Consult manufacturers for limitations on ratings for each type of device selected.

E. Mains:  [Circuit breaker] [Fused switch] [Lugs only].

Retain one of first three paragraphs below.  Allowing only bolt-on circuit breakers will exclude Square D (Schneider Electric), which uses plug-in types with a positive-locking feature, as an approved manufacturer.

F. Branch Overcurrent Protective Devices for Circuit-Breaker Frame Sizes 125 A and Smaller:  [Plug-in] [Bolt-on] circuit breakers.

G. Branch Overcurrent Protective Devices for Circuit-Breaker Frame Sizes Larger Than 125 A:  Bolt-on circuit breakers; plug-in circuit breakers where individual positive-locking device requires mechanical release for removal.

H. Branch Overcurrent Protective Devices:  Fused switches.

Contactors can be incorporated to switch the entire panelboard or only a portion of the circuits.  Coordinate with Drawings and schedules to indicate contactor connections, type, quantity of circuits controlled, current ratings, external control circuits, and number of poles.  Consult manufacturers for their respective limitations on and availability of short-circuit ratings and electrically held contactors, which may not be available from all manufacturers.

I. Contactors in Main Bus:  NEMA ICS 2, Class A, [electrically] [mechanically] held, general-purpose controller, with same short-circuit interrupting rating as panelboard.

Retain one of two subparagraphs below.  If control-power transformer is used, specify capacity and associated fuses on Drawings.  If branch circuit is used, identify circuit on Drawings.  Use of branch circuits also requires a warning sign identifying sources of remote circuits.

1. Internal Control-Power Source:  Control-power transformer, with fused primary and secondary terminals, connected to main bus ahead of contactor connection.

2. External Control-Power Source:  [120-V branch circuit] [24-V control circuit] <Insert requirement>.

2.3 LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. Panelboards:  NEMA PB 1, lighting and appliance branch-circuit type.

Retain first paragraph below if mains are not indicated on Drawings.

D. Mains:  [Circuit breaker] [or] [lugs only].

E. Branch Overcurrent Protective Devices:  [Plug-in] [Bolt-on] circuit breakers, replaceable without disturbing adjacent units.

Contactors can be incorporated to switch the entire panelboard or only a portion of the circuits.  Coordinate with Drawings and schedules to indicate contactor connections, type, quantity of circuits controlled, current ratings, external control circuits, and number of poles.  Consult manufacturers for their respective limitations on and availability of short-circuit ratings and electrically held contactors, which may not be available from all manufacturers.

F. Contactors in Main Bus:  NEMA ICS 2, Class A, [electrically] [mechanically] held, general-purpose controller, with same short-circuit interrupting rating as panelboard.

Retain one of two subparagraphs below.  If control-power transformer is used, specify capacity and associated fuses on Drawings.  If branch circuit is used, identify circuit on Drawings.  Use of branch circuits also requires a warning sign identifying sources of remote circuits.

1. Internal Control-Power Source:  Control-power transformer, with fused primary and secondary terminals, connected to main bus ahead of contactor connection.

2. External Control-Power Source:  [120-V branch circuit] [24-V control circuit] <Insert requirement>.

G. Doors:  Concealed hinges; secured with flush latch with tumbler lock; keyed alike.

H. Column-Type Panelboards:  Narrow gutter extension, with cover, to overhead junction box equipped with ground and neutral terminal buses.

2.4 LOAD CENTERS

Load centers are not covered by NEMA PB 1; however, they are normally UL listed under either UL 67 or manufacturer's UL File Number.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. Load Centers:  Comply with UL 67.

Select first option in first paragraph below for load centers with main overcurrent protective devices; select second option for load centers with only main lugs for the incoming feeder.

D. Mains:  [Circuit breaker] [Lugs only].

E. Branch Overcurrent Protective Devices:  Plug-in circuit breakers, replaceable without disturbing adjacent units.

F. Conductor Connectors:  Mechanical type for main, neutral, and ground lugs and buses.

2.5 ELECTRONIC-GRADE PANELBOARDS

Electronic-grade panelboards are frequently assembled by integrators or contractors using prefabricated panelboards complying with UL 67 and with TVSS modules installed in them; however, this might negate UL 67 short-circuit current ratings of panelboards if they are not retested after installing TVSS modules.  The Section Text requires that electronic-grade panelboards be labeled by an NRTL for compliance with UL 67 after the fabricator installs TVSS modules.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Current Technology; a subsidiary of Danahar Corporation.

2. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

3. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

4. Liebert Corporation.

5. Siemens Energy & Automation, Inc.

6. Square D; a brand of Schneider Electric.

7. <Insert manufacturer's name>.

C. Panelboards:  NEMA PB 1; with factory-installed, integral TVSS; labeled by an NRTL for compliance with UL 67 after installing TVSS.

D. Doors:  Secured with vault-type latch with tumbler lock; keyed alike.

E. Main Overcurrent Protective Devices:  Bolt-on thermal-magnetic circuit breakers.

F. Branch Overcurrent Protective Devices:  Bolt-on thermal-magnetic circuit breakers.

G. Buses:

1. Copper phase and neutral buses; 200 percent capacity neutral bus and lugs.

2. Copper equipment and isolated ground buses.

See the Evaluations in Division 16 Section "Transient Voltage Suppression" for guidance on editing paragraph below.  Selection of options is a matter of ease of maintenance and replacement; coordinate final choices with Owner's maintenance personnel.  Plug-in and modular types offer the quickest maintenance but may come at a slightly higher cost.  Wired-in type offers more safety with a slight reduction in protection and are used for a TVSS installed in a segregated panel extension located above or below the main panel.

H. Surge Protection Device:  IEEE C62.41-compliant, integrally mounted, [plug-in] [wired-in] [bolt-on], solid-state, parallel-connected, [modular (with field-replaceable modules)] [non-modular] type, with sine-wave tracking suppression and filtering modules, short-circuit current rating complying with UL 1449, second edition, and matching or exceeding the panelboard short-circuit rating, redundant suppression circuits, with individually fused metal-oxide varistors.

1. Accessories:

Retain accessories in first 10 subparagraphs below to coordinate with options retained in paragraph above; verify availability and compatibility with manufacturer.

If specifying fuses for connecting TVSS devices to distribution system, verify ability of fuses to withstand surges consistent with ultimate surge current rating of device.

a. Fuses rated at 200-kA interrupting capacity.

b. Fabrication using bolted compression lugs for internal wiring.

Retain first subparagraph below only if a fused switch or circuit breaker is not provided for the TVSS in the panelboard, and the TVSS will not have a direct bus connection.

c. Integral disconnect switch.

d. Redundant suppression circuits.

e. Redundant replaceable modules.

f. Arrangement with wire connections to phase buses, neutral bus, and ground bus.

g. LED indicator lights for power and protection status.

h. Audible alarm, with silencing switch, to indicate when protection has failed.

i. Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of system operation.  Contacts shall reverse position on failure of any surge diversion module or on opening of any current-limiting device.  Coordinate with building power monitoring and control system.

j. [Four] [Six]-digit, transient-event counter set to totalize transient surges.

Select first option in first subparagraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

2. Peak Single-Impulse Surge Current Rating:  [160 kA per mode/320 kA per phase] [120 kA per mode/240 kA per phase] [80 kA per mode/160 kA per phase].

3. Minimum single-impulse current ratings, using 8-by-20-mic.sec. waveform described in IEEE C62.41.2.

a. Line to Neutral:  [70,000] <Insert value> A.

b. Line to Ground:  [70,000] <Insert value> A.

c. Neutral to Ground:  [50,000] <Insert value> A.

Retain first subparagraph below for panelboards located at or near Category C locations.

4. Withstand Capabilities:  12,000 IEEE C62.41, Category C3 (10 kA), 8-by-20-mic.sec. surges with less than 5 percent change in clamping voltage.

Retain one of four subparagraphs below.  Adjust clamping voltages to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage.  Reference to UL 1449 is to its second edition.

5. Protection modes and UL 1449 SVR for grounded wye circuits with [480Y/277] [208Y/120] [600Y/347]-V, three-phase, four-wire circuits shall be as follows:

a. Line to Neutral:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

b. Line to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

c. Neutral to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

6. Protection modes and UL 1449 SVR for 240/120-V, single-phase, three-wire circuits shall be as follows:

a. Line to Neutral:  400 V.

b. Line to Ground:  400 V.

c. Neutral to Ground:  400 V.

7. Protection modes and UL 1449 SVR for 240/120-V, three-phase, four-wire circuits with high leg shall be as follows:

a. Line to Neutral:  400 V, 800 V from high leg.

b. Line to Ground:  400 V.

c. Neutral to Ground:  400 V.

8. Protection modes and UL 1449 SVR for 240-, 480-, or 600-V, three-phase, three-wire, delta circuits shall be as follows:

a. Line to Line:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

b. Line to Ground:  [1500 V for 480 V] [800 V for 240 V] [2500 V for 600 V].

2.6 DISCONNECTING AND OVERCURRENT PROTECTIVE DEVICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Coordinate two paragraphs below with Drawings.  See the "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for guidance on making selections.

C. Molded-Case Circuit Breaker (MCCB):  Comply with UL 489, with [series-connected rating] [interrupting capacity] to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Retain one or more of first four subparagraphs below and coordinate required adjustable settings with Division 16 Section "Overcurrent Protective Device Coordination." See "Electronic rms Trip versus MCCBs" Paragraph in "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional guidance on specifying full- or standard-function features.

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

Retain first subparagraph below for GFCI circuit breakers for personnel ground-fault protection as required by NFPA 70; retain second subparagraph for GFEP circuit breakers (e.g., for self-limiting, heat-trace cables) as required by NFPA 70.  GFCI, GFEP, and AFCI circuit breakers are only available fully rated up to interrupting ratings of 22 kA.  For panelboards subject to fault currents above 22 kA, series ratings must be used.

5. GFCI Circuit Breakers:  Single- and two-pole configurations with Class A ground-fault protection (6-mA trip).

6. Ground-Fault Equipment Protection (GFEP) Circuit Breakers:  Class B ground-fault protection (30-mA trip).

7. Arc-Fault Circuit Interrupter (AFCI) Circuit Breakers:  Comply with UL 1699; 120/240-V, single-pole configuration.

8. Molded-Case Circuit-Breaker (MCCB) Features and Accessories:

Not all accessories and options listed in subparagraphs below are available for every rating and from every listed manufacturer.  Verify availability and unique characteristics with manufacturers selected.

a. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 4 in the Evaluations for guidance on using compression versus mechanical lugs.

b. Lugs:  [Compression] [Mechanical] style, suitable for number, size, trip ratings, and conductor materials.

c. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Select first option in first subparagraph below for solid-state trip units; select second option for thermal-magnetic units.  If selecting second option, also retain "Shunt Trip" Subparagraph below.

d. Ground-Fault Protection:  [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

e. Communication Capability:  [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system specified in Division 16 Section "Electrical Power Monitoring and Control."

For first subparagraph below, 120-V units trip at 55 percent or more of rated voltage; all other voltages trip at 75 percent or more of rated voltage.

f. Shunt Trip:  [120] [24] <Insert voltage>-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

g. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage [without intentional] [with field-adjustable 0.1- to 0.6-second] time delay.

h. Auxiliary Contacts:  [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts and "b" contacts operate in reverse of circuit-breaker contacts.

i. Alarm Switch:  Single-pole, normally open contact that actuates only when circuit breaker trips.

j. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

k. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function with other upstream or downstream devices.

l. Multipole units enclosed in a single housing or factory assembled to operate as a single unit.

m. Handle Padlocking Device:  Fixed attachment, for locking circuit-breaker handle in [on] [off] [on or off] position.

Device defined in subparagraph below is not, and should not be, used as a safety device; it is used for holding the circuit-breaker handle in designated position to avoid accidental interruption of important circuits such as circuits for fire-alarm control panel or emergency lighting.

n. Handle Clamp:  Loose attachment, for holding circuit-breaker handle in on position.

Some manufacturers offer shunt-trip operators for their fused switches; however, most do not recommend using this feature for providing ground-fault protection on switches rated 1000 A and above in panelboards; they recommend using MCCBs or switches specified inDivision 16 Section "Switchboards." Consult manufacturers for availability and limitations if this feature is required.

D. Fused Switch:  NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

1. Fuses, and Spare-Fuse Cabinet:  Comply with requirements specified in Division 16 Section "Fuses."

2. Fused Switch Features and Accessories:  Standard ampere ratings and number of poles.

Accessories and options, in addition to the one in subparagraph below, may be available for some ratings and from some listed manufacturers.  Consult manufacturers for availabilities and unique characteristics.

3. Auxiliary Contacts:  [One] [Two] normally open and normally closed contact(s) that operate with switch handle operation.

2.7 PANELBOARD SUPPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Current Technology; a subsidiary of Danahar Corporation.

2. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

3. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

4. Liebert Corporation.

5. Siemens Energy & Automation, Inc.

6. Square D; a brand of Schneider Electric.

7. <Insert manufacturer's name>.

Retain one of first two paragraphs below.  Comply with manufacturer's written instructions for connecting TVSS devices to distribution system.  See the Evaluations in Division 16 Section "Transient Voltage Suppression" for guidance on editing this article.

C. Surge Protection Device:  IEEE C62.41-compliant, integrally mounted, solid-state, parallel-connected, non-modular type, with sine-wave tracking suppression and filtering modules, UL 1449, second edition, short-circuit current rating matching or exceeding the panelboard short-circuit rating, and with the following features and accessories:

1. Accessories:

Retain accessories in three subparagraphs below to suit Project.

a. LED indicator lights for power and protection status.

b. Audible alarm, with silencing switch, to indicate when protection has failed.

c. One set of dry contacts rated at 5 A and 250-V ac, for remote monitoring of protection status.

Selection of options in first paragraph below is a matter of ease of maintenance and replacement; coordinate final choices with Owner's maintenance personnel.  Plug-in and modular types offer the quickest maintenance but may come at a slightly higher cost.  Wired-in type offers more safety with a slight reduction in protection and are used for a TVSS installed in a segregated panel extension located above or below the main panel.

D. Surge Protection Device:  IEEE C62.41-compliant, integrally mounted, [plug-in] [wired-in] [bolt-on], solid-state, parallel-connected, [modular (with field-replaceable modules)] [non-modular] type, with sine-wave tracking suppression and filtering modules, UL 1449, second edition, short-circuit current rating matching or exceeding the panelboard short-circuit rating, and with the following features and accessories:

1. Accessories:

Retain accessories in 10 subparagraphs below to coordinate with options retained in paragraph above; verify availability and compatibility with manufacturer.

If specifying fuses for connecting TVSS devices to distribution system, verify ability of fuses to withstand surges consistent with ultimate surge current rating of device.

a. Fuses rated at 200-kA interrupting capacity.

b. Fabrication using bolted compression lugs for internal wiring.

Retain first subparagraph below only if a fused switch or circuit breaker is not provided for the TVSS in the panelboard, and the TVSS will not have a direct bus connection.

c. Integral disconnect switch.

d. Redundant suppression circuits.

e. Redundant replaceable modules.

f. Arrangement with wire connections to phase buses, neutral bus, and ground bus.

g. LED indicator lights for power and protection status.

h. Audible alarm, with silencing switch, to indicate when protection has failed.

i. Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of system operation.  Contacts shall reverse position on failure of any surge diversion module or on opening of any current-limiting device. Coordinate with building power monitoring and control system.

j. [Four] [Six]-digit, transient-event counter set to totalize transient surges.

Select first option in first subparagraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

2. Peak Single-Impulse Surge Current Rating:  [160 kA per mode/320 kA per phase] [120 kA per mode/240 kA per phase] [80 kA per mode/160 kA per phase].

3. Minimum single-impulse current ratings, using 8-by-20-mic.sec. waveform described in IEEE C62.41.2.

a. Line to Neutral:  [70,000] <Insert value> A.

b. Line to Ground:  [70,000] <Insert value> A.

c. Neutral to Ground:  [50,000] <Insert value> A.

Retain first subparagraph below for panelboards located at or near Category C locations.

4. Withstand Capabilities:  12,000 IEEE C62.41, Category C3 (10 kA), 8-by-20-mic.sec. surges with less than 5 percent change in clamping voltage.

Retain one of four subparagraphs below.  Adjust clamping voltages to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage.  Reference to UL 1449 is to its second edition.

5. Protection modes and UL 1449 SVR for grounded wye circuits with [480Y/277] [208Y/120] [600Y/347]-V, three-phase, four-wire circuits shall be as follows:

a. Line to Neutral:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

b. Line to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

c. Neutral to Ground:  [800 V for 480Y/277] [400 V for 208Y/120] [1200 V for 600Y/347].

6. Protection modes and UL 1449 SVR for 240/120-V, single-phase, three-wire circuits shall be as follows:

a. Line to Neutral:  400 V.

b. Line to Ground:  400 V.

c. Neutral to Ground:  400 V.

7. Protection modes and UL 1449 SVR for 240/120-V, three-phase, four-wire circuits with high leg shall be as follows:

a. Line to Neutral:  400 V, 800 V from high leg.

b. Line to Ground:  400 V.

c. Neutral to Ground:  400 V.

8. Protection modes and UL 1449 SVR for 240-, 480-, or 600-V, three-phase, three-wire, delta circuits shall be as follows:

a. Line to Line:  [2000 V for 480 V] [1000 V for 240 V] [2500 V for 600 V].

b. Line to Ground:  [1500 V for 480 V] [800 V for 240 V] [2500 V for 600 V].

2.8 ACCESSORY COMPONENTS AND FEATURES

Retain this article for overcurrent protective devices that require items in paragraphs below; delete if these items are specified elsewhere, such as in Division 16 Section "Switchboards."

A. Accessory Set:  Include tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

Retain paragraph below for circuit breakers with solid-state trip devices.

B. Portable Test Set:  For testing functions of solid-state trip devices without removing from panelboard.  Include relay and meter test plugs suitable for testing panelboard meters and switchboard class relays.

PART 3 -  EXECUTION

3.1 EXAMINATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements.  See "Testing and Inspecting" Article in the Evaluations.

A. Receive, inspect, handle, and store panelboards according to [NECA 407] [NEMA PB 1.1].

B. Examine panelboards before installation.  Reject panelboards that are damaged or rusted or have been subjected to water saturation.

C. Examine elements and surfaces to receive panelboards for compliance with installation tolerances and other conditions affecting performance of the Work.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements.  See "Testing and Inspecting" Article in the Evaluations.

A. Install panelboards and accessories according to [NECA 407] [NEMA PB 1.1].

Retain first paragraph below for floor-mounted distribution panelboards.  Even if floor mounted, all panelboard cabinets must still be securely attached to a vertical wall or surface.

B. Equipment Mounting:  Install panelboards on concrete bases, 4-inch (100-mm) nominal thickness.  Comply with requirements for concrete base specified in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For panelboards, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to panelboards.

5. Attach panelboard to the vertical finished or structural surface behind the panelboard.

Retain first paragraph below for large floor-mounted distribution panelboards.

C. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from panelboards.

Retain first paragraph below if seismic controls are required for Project.  Coordinate with Drawings.

D. Comply with mounting and anchoring requirements specified in Division 16 Section "Vibration and Seismic Controls for Electrical Systems."

Ensure that, whatever height is selected for top of trim in first paragraph below, the operating handle of top-most switch or circuit breaker, in on position, is not higher than 79 inches (2000 mm) above finished floor or grade.

E. Mount top of trim [90 inches (2286 mm)] <Insert height> above finished floor unless otherwise indicated.

F. Mount panelboard cabinet plumb and rigid without distortion of box.  Mount recessed panelboards with fronts uniformly flush with wall finish and mating with back box.

G. Install overcurrent protective devices and controllers not already factory installed.

Subparagraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

1. Set field-adjustable, circuit-breaker trip ranges.

H. Install filler plates in unused spaces.

Retain first paragraph below if ceilings are accessible or there are raised floors, or when panelboards are located in spaces that will be finished.

I. Stub four 1-inch (27-GRC) empty conduits from panelboard into accessible ceiling space or space designated to be ceiling space in the future.  Stub four 1-inch (27-GRC) empty conduits into raised floor space or below slab not on grade.

Retain option in first paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

J. Arrange conductors in gutters into groups and bundle and wrap with wire ties[ after completing load balancing].

K. Comply with NECA 1.

3.3 IDENTIFICATION

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with Division 16 Section "Electrical Identification."

Retain option in first paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

B. Create a directory to indicate installed circuit loads[ after balancing panelboard loads]; incorporate Owner's final room designations.  Obtain approval before installing.  Use a computer or typewriter to create directory; handwritten directories are not acceptable.

C. Panelboard Nameplates:  Label each panelboard with a nameplate complying with requirements for identification specified in Division 16 Section"Electrical Identification."

Retain paragraph below if nameplates are required for individual overcurrent devices in distribution panelboards.

D. Device Nameplates:  Label each branch circuit device in distribution panelboards with a nameplate complying with requirements for identification specified in Division 16 Section "Electrical Identification."

3.4 FIELD QUALITY CONTROL

Retain one of first three paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field Quality-Control Reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments, especially if panelboards include zone-selective interlocking.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first two paragraphs below to describe tests and inspections to be performed.

D. Acceptance Testing Preparation:

1. Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

E. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3. Perform the following infrared scan tests and inspections and prepare reports:

a. Initial Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each panelboard.  Remove front panels so joints and connections are accessible to portable scanner.

b. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each panelboard 11 months after date of Substantial Completion.

c. Instruments and Equipment:

1) Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

F. Panelboards will be considered defective if they do not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

G. Prepare test and inspection reports, including a certified report that identifies panelboards included and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.5 ADJUSTING

A. Adjust moving parts and operable component to function smoothly, and lubricate as recommended by manufacturer.

Select first option in first paragraph below if settings are included in the Contract Documents; select second option if indicated Section is included in the Contract Documents.

B. Set field-adjustable circuit-breaker trip ranges [as indicated] [as specified in Division 16 Section "Overcurrent Protective Device Coordination."]

Circuit changes made during load balancing may negate color-coding of phases and circuits.  If load balancing proves undesirable or is to be performed by others, delete paragraph below.

C. Load Balancing:  After Substantial Completion, but not more than 60 days after Final Acceptance, measure load balancing and make circuit changes.

1. Measure as directed during period of normal system loading.

2. Perform load-balancing circuit changes outside normal occupancy/working schedule of the facility and at time directed.  Avoid disrupting critical 24-hour services such as fax machines and on-line data processing, computing, transmitting, and receiving equipment.

3. After circuit changes, recheck loads during normal load period.  Record all load readings before and after changes and submit test records.

4. Tolerance:  Difference exceeding 20 percent between phase loads, within a panelboard, is not acceptable.  Rebalance and recheck as necessary to meet this minimum requirement.

3.6 PROTECTION

A. Temporary Heating:  Apply temporary heat to maintain temperature according to manufacturer's written instructions.

END OF SECTION 16442

PANELBOARDS
16442 - 1

