Copyright 2006 AIA
MASTERSPEC Full Length
03/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16491 - FUSES
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Cartridge fuses rated 600-V ac and less for use in [control circuits] [enclosed switches] [panelboards] [switchboards] [enclosed controllers] [and] [motor-control centers].

2. Plug fuses rated 125-V ac and less for use in plug-fuse-type [enclosed switches] [fuseholders] [and] [panelboards].

Retain first subparagraph below if retaining rejection-base-type plug fuses and if Project contains fuseholders with Edison-base, plug-fuse sockets.

3. Plug-fuse adapters for use in Edison-base, plug-fuse sockets.

4. Spare-fuse cabinets.

1.3 SUBMITTALS

First paragraph below is defined in Division 1 Section "Submittal Procedures" as an "Action Submittal."

A. Product Data:  For each type of product indicated.  Include construction details, material, dimensions, descriptions of individual components, and finishes for spare-fuse cabinets. Include the following for each fuse type indicated:

Retain first subparagraph below if variations in fuse performance due to ambient temperature extremes can affect system performance.

1. Ambient Temperature Adjustment Information:  If ratings of fuses have been adjusted to accommodate ambient temperatures, provide list of fuses with adjusted ratings.

a. For each fuse having adjusted ratings, include location of fuse, original fuse rating, local ambient temperature, and adjusted fuse rating.

b. Provide manufacturer's technical data on which ambient temperature adjustment calculations are based.

2. Dimensions and manufacturer's technical data on features, performance, electrical characteristics, and ratings.

Retain four subparagraphs below if final system short-circuit and coordination studies will be performed by the designer or will be assigned to an independent consultant.  These curves are beneficial to Owner for future additions or reevaluations of settings of overcurrent protective devices.

3. Current-limitation curves for fuses with current-limiting characteristics.

Although some manufacturers no longer offer curves on translucent graph paper, curves can normally be downloaded from manufacturers' Web sites or be obtained, in electronic form, from various coordination software vendors as part of a subscription service.  Retain option in first subparagraph below only if retained manufacturers offer curves on graph paper.

4. Time-current coordination curves (average melt) and current-limitation curves (instantaneous peak let-through current) for each type and rating of fuse.[  Submit on translucent log-log graph paper.]

5. Coordination charts and tables and related data.

Retain subparagraph below if Project includes elevators and fused elevator shunt-trip switches.

6. Fuse sizes for elevator feeders and elevator disconnect switches.

Paragraph below is defined in Division 1 Section "Submittal Procedures" as an "Informational Submittal."

B. Operation and Maintenance Data:  For fuses to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "Operation and Maintenance Data," include the following:

1. Ambient temperature adjustment information.

2. Current-limitation curves for fuses with current-limiting characteristics.

Retain option in first subparagraph below only if retained manufacturers offer curves on graph paper.

3. Time-current coordination curves (average melt) and current-limitation curves (instantaneous peak let-through current) for each type and rating of fuse.[  Submit on translucent log-log graph paper.]

4. Coordination charts and tables and related data.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain fuses, for use within a specific product or circuit, from single source from single manufacturer.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Comply with NEMA FU 1 for cartridge fuses.

D. Comply with NFPA 70.

E. Comply with UL 248-11 for plug fuses.

1.5 PROJECT CONDITIONS

For fuses installed outdoors or in unusual environmental conditions, revise this article to indicate minimum and maximum ambient temperatures and expected humidity range.  See Editing Instruction No. 4 in the Evaluations.

A. Where ambient temperature to which fuses are directly exposed is less than [40 deg F (5 deg C)] <Insert temperature> or more than [100 deg F (38 deg C)] <Insert temperature>, apply manufacturer's ambient temperature adjustment factors to fuse ratings.

1.6 COORDINATION

A. Coordinate fuse ratings with utilization equipment nameplate limitations of maximum fuse size and with system short-circuit current levels.

1.7 EXTRA MATERIALS

Coordinate this article with other Division 16 Sections and Sections in other Divisions specifying fuses, for quantities of spare fuses to include.  Do not include spare fuses in this Section if spare fuses are already specified in other Division 16 Sections or in Sections in other Divisions.

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Fuses:  Equal to [10] <Insert number> percent of quantity installed for each size and type, but no fewer than [two] <Insert number> of each size and type.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain paragraph and list of manufacturers in this article.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Cooper Bussmann, Inc.

2. Edison Fuse, Inc.

3. Ferraz Shawmut, Inc.

4. Littelfuse, Inc.

5. <Insert manufacturer's name>.

2.2 CARTRIDGE FUSES

Fuse "Class" defines fuse performance category, including interrupting rating.  See Editing Instruction No. 2 and "Cartridge Fuses" Article in the Evaluations.  Include current rating and class for cartridge fuses either on Drawings or in "Fuse Applications" Article.

A. Characteristics:  NEMA FU 1, nonrenewable cartridge fuses with voltage ratings consistent with circuit voltages.

2.3 PLUG FUSES

Fuse "Type" defines fuse performance category and base types.  See Editing Instruction No. 3 and "Plug Fuses" Article in the Evaluations.  Include current rating and type designations for plug fuses either on Drawings or in "Fuse Applications" Article.

A. Characteristics:  UL 248-11, nonrenewable plug fuses; 125-V ac.

2.4 PLUG-FUSE ADAPTERS

Retain this article if rejection-base fuse adapters are required to retrofit Edison-base fuseholders or sockets with Type S, rejection-base plug fuses.  See "Plug-Fuse Adapters" Article in the Evaluations.  Adapters are designed to prevent installing wrong size fuses.

A. Characteristics:  Adapters for using Type S, rejection-base plug fuses in Edison-base fuseholders or sockets; ampere ratings matching fuse ratings; irremovable once installed.

2.5 SPARE-FUSE CABINET

A. Characteristics:  Wall-mounted steel unit with full-length, recessed piano-hinged door and key-coded cam lock and pull.

1. Size:  Adequate for storage of spare fuses specified with [15] <Insert number> percent spare capacity minimum.

2. Finish:  Gray, baked enamel.

3. Identification:  "SPARE FUSES" in 1-1/2-inch- (38-mm-) high letters on exterior of door.

4. Fuse Pullers:  For each size of fuse, where applicable and available, from fuse manufacturer.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine fuses before installation.  Reject fuses that are moisture damaged or physically damaged.

B. Examine holders to receive fuses for compliance with installation tolerances and other conditions affecting performance, such as rejection features.

C. Examine utilization equipment nameplates and installation instructions.  Install fuses of sizes and with characteristics appropriate for each piece of equipment.

D. Evaluate ambient temperatures to determine if fuse rating adjustment factors must be applied to fuse ratings.

E. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 FUSE APPLICATIONS

Retain this article if fuse class and type designations are not indicated on Drawings.  Indicate fuse ampere ratings on Drawings.  See Evaluations for discussions of fuse classes and types.  Select fuse classes and types by coordinating required average melt characteristics and peak let-through currents with Division 16 Section "Overcurrent Protective Device Coordination." See "Cartridge versus Plug Fuses" Article in the Evaluations for additional guidance in making selections.

A. Cartridge Fuses:

Class T fuses in first subparagraph below are normally used in main switches ahead of meter banks because of their compact size and excellent current-limiting characteristics.  Their current-limiting feature often allows using circuit breakers with 10-kA interrupting rating at tenant meters.  See "Cartridge Fuses" Article in the Evaluations for additional guidance in making selections.

1. Service Entrance:  [Class L, fast acting] [Class L, time delay] [Class RK1, fast acting] [Class RK1, time delay] [Class J, fast acting] [Class J, time delay] [Class T, fast acting].

2. Feeders:  [Class L, fast acting] [Class L, time delay] [Class RK1, fast acting] [Class RK1, time delay] [Class RK5, fast acting] [Class RK5, time delay] [Class J, fast acting] [Class J, time delay].

3. Motor Branch Circuits:  [Class RK1] [Class RK5], time delay.

4. Other Branch Circuits:  [Class RK1, time delay] [Class RK5, time delay] [Class J, fast acting] [Class J, time delay].

5. Control Circuits:  Class CC, [fast acting] [time delay].

B. Plug Fuses:

NFPA 70 limits types of plug fuses that can be used in new construction and for replacing plug fuses in existing installations.  Limited ampere, voltage, and interrupting ratings and limited availability of fuseholders also reduce the feasibility of plug fuses in most new installations.  Type S, rejection base and Edison base are two types still available in the U.S.  See "Plug Fuses" Article in the Evaluations for additional guidance in making selections.

1. Motor Branch Circuits:  [Edison-base type, dual] [Edison-base type, single] [Type S, dual] [Type S, single]-element time delay.

2. Other Branch Circuits:  [Edison-base type, single-element fast acting] [Edison-base type, dual-element time delay] [Edison-base type, single-element time delay] [Type S, dual-element time delay] [Type S, single-element time delay].

3.3 INSTALLATION

A. Install fuses in fusible devices.  Arrange fuses so rating information is readable without removing fuse.

Retain first paragraph below if Type S, rejection-base plug fuses are required for installation in existing facilities having fuseholders with Edison-base fuse sockets, or when fuseholders with Edison-base fuse sockets are specified for new construction.

B. Install plug-fuse adapters in Edison-base fuseholders and sockets.  Ensure that adapters are irremovable once installed.

C. Install spare-fuse cabinet(s).

3.4 IDENTIFICATION

A. Install labels complying with requirements for identification specified in Division 16 Section "Electrical Identification" and indicating fuse replacement information on inside door of each fused switch and adjacent to each fuse block, socket, and holder.

END OF SECTION 16491

FUSES
16491 - 1

