Copyright 2003 AIA
MASTERSPEC Full Length
06/03 (R 06/06)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16521 - EXTERIOR LIGHTING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 9, "Lighting," sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.  The selection of the lamp and ballast as a system is an important design decision to optimize energy efficiency of the lighting system.

A reduction in lighting energy usage can be combined with other energy-conserving measures to meet the requirements of LEED-NC Credit EA 1.LEED-NC Credit SS 8 requires that exterior lights be provided as needed for "safety and comfort" with the lighting power densities for the exterior areas and the building fa?ade and landscape at a minimum of 20% and 50% less than ASHRAE/IESNA 90.1-2004, respectively.  In addition, the lighting design must eliminate or minimize any "light trespass" from the site and reduce "sky-glow," depending on the zone classification of the site according to IESNA Standard RP33 requirements.  Consider selecting the proper light fixtures, such as low-intensity shielded fixtures, the aiming of the fixtures, and using automatic controllers to turn off nonessential site lighting after a specific hour as defined by this credit.  Credit SS 8 also sets requirements for interior lighting.  See Division 16 Section "Interior Lighting."

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Exterior luminaires with lamps and ballasts.

2. Luminaire-mounted photoelectric relays.

3. Poles and accessories.

4. Luminaire lowering devices.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 16 Section "Interior Lighting" for exterior luminaires normally mounted on exterior surfaces of buildings.

1.3 DEFINITIONS

Retain abbreviations and terms that remain after this Section has been edited.

A. CRI:  Color-rendering index.

B. HID:  High-intensity discharge.

C. Luminaire:  Complete lighting fixture, including ballast housing if provided.

D. Pole:  Luminaire support structure, including tower used for large area illumination.

E. Standard:  Same definition as "Pole" above.

1.4 STRUCTURAL ANALYSIS CRITERIA FOR POLE SELECTION

Retain this Article if manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4.  Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in Part 2 "Requirements for Individual Exterior Lighting Devices" Article or in Exterior Lighting Device Schedule or details on Drawings.  See Editing Instruction No. 1 in the Evaluations.

A. Dead Load:  Weight of luminaire and its horizontal and vertical supports, lowering devices, and supporting structure, applied as stated in AASHTO LTS-4.

Delete paragraph below if Project does not include pole-mounted service platforms.

B. Live Load:  Single load of 500 lbf (2224 N), distributed as stated in AASHTO LTS-4.

Delete paragraph below if Project is outside the area shown in AASHTO LTS-4, Figure 1.2.3.

C. Ice Load:  Load of 3 lbf/sq. ft. (143.6 Pa), applied as stated in AASHTO LTS-4.

See Editing Instruction No. 2 in the Evaluations for discussion of wind-load calculations.

D. Wind Load:  Pressure of wind on pole and luminaire, calculated and applied as stated in AASHTO LTS-4.

1. Wind speed for calculating wind load for poles exceeding 50 feet (15 m) in height is [110 mph (177 km/h)] [70 mph (113 km/h)] <Insert value from AASHTO LTS-4 for this Project>.

2. Wind speed for calculating wind load for poles 50 feet (15 m) or less in height is [110 mph (177 km/h)] [70 mph (113 km/h)] <Insert value from AASHTO LTS-4 for this Project>.

1.5 SUBMITTALS

A. Product Data:  For each luminaire, pole, and support component, arranged in order of lighting unit designation.  Include data on features, accessories, finishes, and the following:

1. Physical description of luminaire, including materials, dimensions, effective projected area, and verification of indicated parameters.

2. Details of attaching luminaires and accessories.

3. Details of installation and construction.

4. Luminaire materials.

5. Photometric data based on laboratory tests of each luminaire type, complete with indicated lamps, ballasts, and accessories.

Retain one of first two subparagraphs below.  Retain first subparagraph if photometric data for one or more luminaires are to be based on independent laboratory tests; coordinate with Exterior Lighting Device Schedule on Drawings or with Part 2 "Requirements for Individual Exterior Lighting Devices" Article to indicate which units are required to meet this requirement.  Retain second subparagraph if photometric data based on testing by accredited manufacturers' laboratories are considered adequate for all exterior luminaires in this Project.  See Evaluations.

a. For indicated luminaires, photometric data shall be certified by a qualified independent testing agency.  Photometric data for remaining luminaires shall be certified by manufacturer.

b. Photometric data shall be certified by manufacturer's laboratory with a current accreditation under the National Voluntary Laboratory Accreditation Program for Energy Efficient Lighting Products.

6. Photoelectric relays.

7. Ballasts, including energy-efficiency data.

8. Lamps, including life, output, and energy-efficiency data.

9. Materials, dimensions, and finishes of poles.

10. Means of attaching luminaires to supports, and indication that attachment is suitable for components involved.

11. Anchor bolts for poles.

Retain subparagraph below if manufactured pole foundations, including screw foundations, are indicated.

12. Manufactured pole foundations.

Retain paragraph and subparagraphs below if foundation-mounted poles are indicated.

B. Shop Drawings:

1. Anchor-bolt templates keyed to specific poles and certified by manufacturer.

Retain first subparagraph below if screw foundations are indicated.

2. Design calculations, certified by a qualified professional engineer, indicating strength of screw foundations and soil conditions on which they are based.

3. Wiring Diagrams:  Power[ and control] wiring.

Retain paragraph below if Samples of exterior luminaires or support components are required for verification purposes.  Revise if sample requirements are indicated in other than Exterior Lighting Device Schedule on Drawings.  As an alternative, add a list of luminaire types for sample submission.

C. Samples for Verification:  For products designated for sample submission in Exterior Lighting Device Schedule.  Each sample shall include lamps and ballasts.

Retain paragraph below if retaining "Structural Analysis Criteria for Pole Selection" Article.  See Editing Instruction No. 1 in the Evaluations.

D. Pole and Support Component Certificates:  Signed by manufacturers of poles, certifying that products are designed for indicated load requirements in AASHTO LTS-4 and that load imposed by luminaire has been included in design.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For agencies providing photometric data for lighting fixtures.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For [luminaires][ and poles] [luminaire lowering devices] to include in emergency, operation, and maintenance manuals.

H. Warranty:  Special warranty specified in this Section.

1.6 QUALITY ASSURANCE

Retain one or both of first two paragraphs below to specify qualifications for laboratories providing photometric data to be submitted for luminaires.

A. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by manufacturers' laboratories that are accredited under the National Volunteer Laboratory Accreditation Program for Energy Efficient Lighting Products.

B. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by an independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. Comply with IEEE C2, "National Electrical Safety Code."

E. Comply with NFPA 70.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Package aluminum poles for shipping according to ASTM B 660.

B. Store poles on decay-resistant-treated skids at least 12 inches (300 mm) above grade and vegetation.  Support poles to prevent distortion and arrange to provide free air circulation.

C. Handle wood poles so they will not be damaged.  Do not use pointed tools that can indent pole surface more than 1/4 inch (6 mm) deep.  Do not apply tools to section of pole to be installed below ground line.

Delete first paragraph below if no fiberglass or laminated wood poles.

D. Retain factory-applied pole wrappings on fiberglass and laminated wood poles until right before pole installation.  Handle poles with web fabric straps.

E. Retain factory-applied pole wrappings on metal poles until right before pole installation.  For poles with nonmetallic finishes, handle with web fabric straps.

1.8 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

See Editing Instruction No. 3 in the Evaluations for discussion of ballast and lamp warranties.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace products that fail in materials or workmanship; that corrode; or that fade, stain, perforate, erode, or chalk due to effects of weather or solar radiation within specified warranty period.  Manufacturer may exclude lightning damage, hail damage, vandalism, abuse, or unauthorized repairs or alterations from special warranty coverage.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period for Luminaires:  [Five] <Insert number> years from date of Substantial Completion.

Coordinate warranty provisions for resistance to corrosion and for color retention with similar warranties for poles and mast arms.  Otherwise, delete first two subparagraphs below.

2. Warranty Period for Metal Corrosion:  [Five] <Insert number> years from date of Substantial Completion.

3. Warranty Period for Color Retention:  [Five] <Insert number> years from date of Substantial Completion.

4. Warranty Period for Lamps:  Replace lamps and fuses that fail within [12] <Insert number> months from date of Substantial Completion; furnish replacement lamps and fuses that fail within the second [12] <Insert number> months from date of Substantial Completion.

5. Warranty Period for Poles:  Repair or replace lighting poles and standards that fail in finish, materials, and workmanship within manufacturer's standard warranty period, but not less than [three] <Insert number> years from date of Substantial Completion.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.  Quantities indicated are examples only.

1. Lamps:  [10 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

2. Glass and Plastic Lenses, Covers, and Other Optical Parts:  [10 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

3. Ballasts:  [10 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

4. Globes and Guards:  [10 for every 20] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Edit this Article with other Part 2 articles or with Exterior Lighting Device Schedule on Drawings in which manufacturers and products are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers," "Manufacturers," and "Basis-of-Design Product" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

Retain paragraph above if luminaires and their supports are described in this Section; retain paragraph below if luminaires and their supports are scheduled on Drawings.  See sample schedule in the Evaluations.

B. In Exterior Lighting Device Schedule where titles below are column or row headings that introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

3. Basis of Design Product:  The design of each item of exterior luminaire and its support is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by one of the other manufacturers specified.

2.2 LUMINAIRES, GENERAL REQUIREMENTS

A. Luminaires shall comply with UL 1598 and be listed and labeled for installation in wet locations by an NRTL acceptable to authorities having jurisdiction.

Retain first paragraph below if some lighting units or luminaires are indicated to have Type I, II, III, IV, or V distribution pattern in "Requirements for Individual Exterior Lighting Devices" Article or in Exterior Lighting Device Schedule or details on Drawings.

B. Comply with IESNA RP-8 for parameters of lateral light distribution patterns indicated for luminaires.

C. Metal Parts:  Free of burrs and sharp corners and edges.

D. Sheet Metal Components:  Corrosion-resistant aluminum, unless otherwise indicated.  Form and support to prevent warping and sagging.

E. Housings:  Rigidly formed, weather- and light-tight enclosures that will not warp, sag, or deform in use.  Provide filter/breather for enclosed luminaires.

F. Doors, Frames, and Other Internal Access:  Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools.  Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position.  Doors shall be removable for cleaning or replacing lenses.  Designed to disconnect ballast when door opens.

G. Exposed Hardware Material:  Stainless steel.

H. Plastic Parts:  High resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

Retain first paragraph below if one or more luminaires require partial shielding of light output to avoid light trespass or to meet other requirements.  Coordinate with Exterior Lighting Device Schedule on Drawings or with "Requirements for Individual Exterior Lighting Devices" Article.

I. Light Shields:  Metal baffles, factory installed and field adjustable, arranged to block light distribution to indicated portion of normally illuminated area or field.

J. Reflecting surfaces shall have minimum reflectance as follows, unless otherwise indicated:

1. White Surfaces:  85 percent.

2. Specular Surfaces:  83 percent.

3. Diffusing Specular Surfaces:  75 percent.

K. Lenses and Refractors Gaskets:  Use heat- and aging-resistant resilient gaskets to seal and cushion lenses and refractors in luminaire doors.

Revise paragraph below to include custom colors.  Coordinate custom-color requirements for luminaires with those for poles and other luminaire support requirements.

L. Luminaire Finish:  Manufacturer's standard paint applied to factory-assembled and -tested luminaire before shipping.  Where indicated, match finish process and color of pole or support materials.

Retain paragraph and subparagraphs below when luminaire material is steel that is not to be field painted and is not required to match finish of pole or support materials.

M. Factory-Applied Finish for Steel Luminaires:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Surface Preparation:  Clean surfaces to comply with SSPC-SP 1, "Solvent Cleaning," to remove dirt, oil, grease, and other contaminants that could impair paint bond.  Grind welds and polish surfaces to a smooth, even finish.  Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1, "White Metal Blast Cleaning," or SSPC-SP 8, "Pickling."

2. Exterior Surfaces:  Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

Retain one of three subparagraphs below.

a. Color:  As selected from manufacturer's standard catalog of colors.

b. Color:  Match Architect's sample of [manufacturer's standard] [custom] color.

c. Color:  As selected by Architect from manufacturer's full range.

Retain paragraph and subparagraphs below when luminaire material is aluminum that is not to be field painted and is not required to match finish of pole or support materials.

N. Factory-Applied Finish for Aluminum Luminaires:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain one of three subparagraphs and associated subparagraph below or revise to suit Project.

2. Natural Satin Finish:  Provide fine, directional, medium satin polish (AA-M32); buff complying with AA-M20; and seal aluminum surfaces with clear, hard-coat wax.

3. Class I, Clear Anodic Finish:  AA-M32C22A41 (Mechanical Finish:  medium satin; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

4. Class I, Color Anodic Finish:  AA-M32C22A42/A44 (Mechanical Finish:  medium satin; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker) complying with AAMA 611.

Retain one color in subparagraph below with any subparagraph above.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black].

2.3 LUMINAIRE-MOUNTED PHOTOELECTRIC RELAYS

A. Comply with UL 773 or UL 773A.

B. Contact Relays:  Factory mounted, single throw, designed to fail in the on position, and factory set to turn light unit on at 1.5 to 3 fc (16 to 32 lx) and off at 4.5 to 10 fc (48 to 108 lx) with 15-second minimum time delay.[  Relay shall have directional lens in front of photocell to prevent artificial light sources from causing false turnoff.]

1. Relay with locking-type receptacle shall comply with NEMA C136.10.

2. Adjustable window slide for adjusting on-off set points.

2.4 FLUORESCENT BALLASTS AND LAMPS

Delete this Article or revise to suit Project.  Verify that lamp, ballast, and luminaire combinations indicated are suitable for low-temperature environment that may be encountered at Project site.  See Editing Instruction No. 5 in the Evaluations for discussion of low-temperature application of fluorescent luminaires, lamps, and ballasts.

A. Low-Temperature Ballast Capability:  Rated by its manufacturer for reliable starting and operation of indicated lamp(s) at temperatures [0 deg F (minus 18 deg C)] [minus 20 deg F (minus 29 deg C)] and higher.

B. Ballast Characteristics:

1. Power Factor:  90 percent, minimum.

2. Sound Rating:  [A] [A, except B for T12/HO ballasts].

See Evaluations for discussion of harmonic distortion in first subparagraph below.

3. Total Harmonic Distortion Rating:  Less than [10] [20] percent.

4. Electromagnetic Ballasts:  Comply with ANSI C82.1, energy-saving, high power factor, Class P, automatic-reset thermal protection.

5. Case Temperature for Compact Lamp Ballasts:  65 deg C, maximum.

6. Transient-Voltage Protection:  Comply with IEEE C62.41 Category A or better.

Coordinate two paragraphs below with Drawings, and indicate lamp type for each fluorescent luminaire in Exterior Lighting Device Schedule on Drawings or in description in this Section.  Where color rendition or color uniformity is important and several types of fluorescent lamps are used, provide consistent manufacturer designations or ANSI lamp designations to define requirements.

For applications at low temperatures, verify that lamp, ballast, and luminaire combinations indicated will start reliably and provide required light output throughout the range of temperatures that may be encountered.

C. Low-Temperature Lamp Capability:  Rated for reliable starting and operation with ballast provided at temperatures [0 deg F (minus 18 deg C)] [minus 20 deg F (minus 29 deg C)] and higher.

Low-mercury lamps in paragraph below may not be available in all lamp categories.  Specifying low-mercury lamps may change the color temperature.  Consult manufacturers.

D. Fluorescent Lamps:  Low-mercury type.  Comply with the EPA's toxicity characteristic leaching procedure test; shall yield less than 0.2 mg of mercury per liter when tested according to NEMA LL 1.

2.5 BALLASTS FOR HID LAMPS

A. Comply with ANSI C82.4 and UL 1029 and capable of open-circuit operation without reduction of average lamp life.  Include the following features, unless otherwise indicated:

1. Ballast Circuit:  Constant-wattage autotransformer or regulating high-power-factor type.

2. Minimum Starting Temperature:  Minus 22 deg F (Minus 30 deg C).

3. Normal Ambient Operating Temperature:  104 deg F (40 deg C).

Retain subparagraph below if ballasts are required to be fused.  See Editing Instruction No. 4 in the Evaluations for discussion of ballast fusing.

4. Ballast Fuses:  One in each ungrounded power supply conductor.  Voltage and current ratings as recommended by ballast manufacturer.

B. Auxiliary, Instant-On, Quartz System:  Factory-installed feature automatically switches quartz lamp on when fixture is initially energized and when momentary power outages occur.  System automatically turns quartz lamp off when HID lamp reaches approximately 60 percent of light output.

C. High-Pressure Sodium Ballasts:  Electromagnetic type with solid-state igniter/starter and capable of open-circuit operation without reduction of average lamp life.  Igniter/starter shall have an average life in pulsing mode of 10,000 hours at an igniter/starter-case temperature of 90 deg C.

If unacceptable for safety, security, or other reasons for high-pressure sodium lamps to be extinguished for a lengthy restrike period by momentary power interruptions, specify dual-arc tube lamps in "High-Pressure Sodium Lamps" Paragraph in "HID Lamps" Article or, for lamps up to 150 W, retain first subparagraph and associated subparagraphs below.

1. Instant-Restrike Device:  Integral with ballast, or solid-state potted module, factory installed within fixture and compatible with lamps, ballasts, and mogul sockets up to 150 W.

a. Restrike Range:  105- to 130-V ac.

b. Maximum Voltage:  250-V peak or 150-V ac RMS.

2. Minimum Starting Temperature:  Minus 40 deg F (Minus 40 deg C).

2.6 HID LAMPS

Coordinate this Article with Drawings.  Where color rendition or color uniformity is important and several types of HID lamps are used, provide consistent manufacturer designations or ANSI designations to define lamp types.

A. High-Pressure Sodium Lamps:  ANSI C78.42, CRI 21 (minimum), color temperature [1900] <Insert value> K, and average rated life of 24,000 hours, minimum.

Consider retaining subparagraph below if extinguishing of high-pressure sodium lamps caused by momentary power interruptions is unacceptable for safety, security, or other reasons.  Instant-restrike device specified in "Ballasts for HID Lamps" Article may also be considered.  Verify availability of individual ratings with manufacturers before scheduling or specifying.

1. Dual-Arc Tube Lamp:  Arranged so only one of two arc tubes is lighted at one time and, when power is restored after an outage, the cooler arc tube, with lower internal pressure, lights instantly, providing an immediate 8 to 15 percent of normal light output.

ANSI has a separate standard for each conventional metal-halide lamp, unlike standards for low- and high-pressure sodium lamps.  Consider including the standard number in Exterior Lighting Device Schedule on Drawings.  Wattage and mean lumen output ratings for each lamp may be included in Exterior Lighting Device Schedule on Drawings or in "Requirements for Individual Exterior Lighting Devices" Article.

B. Metal-Halide Lamps:  ANSI C78.1372, with a minimum CRI [65] <Insert value>, and color temperature [4000] <Insert value> K.

Pulse-start, metal-halide lamps in paragraph below are available in ratings from 30 to 1000 W and provide higher lumen maintenance and reduced color-shift throughout the life of the lamp, compared with basic metal-halide lamps.  This may permit the use of lower-wattage lamps to provide the same maintained illumination level provided by an equal number of conventional metal-halide lamps.  Consult manufacturers to verify compatibility of lamps with ballasts and luminaires.

C. Pulse-Start, Metal-Halide Lamps:  Minimum CRI 65, and color temperature [4000] <Insert value> K.

Ceramic, pulse-start, metal-halide lamps in paragraph below are available in ratings from about 40 to 250 W.  In addition to advantages inherent in pulse-start technology, these lamps have an improved CRI, between 80 and 94, with higher initial and maintained lumen output.

D. Ceramic, Pulse-Start, Metal-Halide Lamps:  Minimum CRI [80] <Insert value>, and color temperature [4000] <Insert value> K.

2.7 POLES AND SUPPORT COMPONENTS, GENERAL REQUIREMENTS

A. Structural Characteristics:  Comply with AASHTO LTS-4.

Retain two subparagraphs below if retaining Part 1 "Structural Analysis Criteria for Pole Selection" Article and manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4.  Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in "Requirements for Individual Exterior Lighting Devices" Article or in Exterior Lighting Device Schedule or details on Drawings.  See Editing Instruction No. 1 in the Evaluations.

1. Wind-Load Strength of Poles:  Adequate at indicated heights above grade without failure, permanent deflection, or whipping in steady winds of speed indicated in Part 1 "Structural Analysis Criteria for Pole Selection" Article, with a gust factor of 1.3.

Retain subparagraph below to help ensure that poles are stiff enough to avoid excessive flexure and vibration.  Alternatively, add requirements for minimum pole wall thickness and other parameters.  See Editing Instruction No. 6 in the Evaluations.

2. Strength Analysis:  For each pole, multiply the actual equivalent projected area of luminaires and brackets by a factor of [1.1] <Insert number> to obtain the equivalent projected area to be used in pole selection strength analysis.

B. Luminaire Attachment Provisions:  Comply with luminaire manufacturers' mounting requirements.  Use stainless-steel fasteners and mounting bolts, unless otherwise indicated.

Coordinate paragraph and subparagraphs below with Drawings.

C. Mountings, Fasteners, and Appurtenances:  Corrosion-resistant items compatible with support components.

1. Materials:  Shall not cause galvanic action at contact points.

2. Anchor Bolts, Leveling Nuts, Bolt Caps, and Washers:  Hot-dip galvanized after fabrication, unless stainless-steel items are indicated.

3. Anchor-Bolt Template:  Plywood or steel.

Coordinate paragraph below with Drawings for indication of concrete foundations suitable for soil conditions and loads imposed by pole, luminaire, and support components.

D. Concrete Pole Foundations:  Cast in place, with anchor bolts to match pole-base flange.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

Retain one or both paragraphs below to suit Project.

E. Power-Installed Screw Foundations:  Factory fabricated by pole manufacturer, with structural steel complying with ASTM A 36/A 36M and hot-dip galvanized according to ASTM A 123/A 123M; and with top-plate and mounting bolts to match pole base flange and strength required to support pole, luminaire, and accessories.

On Drawings, identify poles that require breakaway supports described in paragraph below.  Add description if specific type of breakaway support is required.

F. Breakaway Supports:  Frangible breakaway supports, tested by an independent testing agency acceptable to authorities having jurisdiction, according to AASHTO LTS-4.

If support structures other than poles are used, add an article here to specify structure materials.

2.8 STEEL POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Comply with ASTM A 500, Grade B, carbon steel with a minimum yield of 46,000 psig (317 MPa); 1-piece construction up to 40 feet (12 m) in height with access handhole in pole wall.

1. Shape:  [Round, tapered] [Round, straight] [Square, tapered] [Square, straight].

Coordinate subparagraph below with Drawings.

2. Mounting Provisions:  Butt flange for bolted mounting on foundation or breakaway support.

B. Steel Mast Arms:  [Single-arm] [Truss] [Davit] type, continuously welded to pole attachment plate.  Material and finish same as pole.

Indicate span and rise of mast arms in paragraph above and luminaire brackets in first paragraph below on Drawings.  Delete paragraph above and first paragraph and subparagraphs below if items are adequately described in "Requirements for Individual Exterior Lighting Devices" Article or in Exterior Lighting Device Schedule or details on Drawings.

C. Brackets for Luminaires:  Detachable, cantilever, without underbrace.

1. Adapter fitting welded to pole and bracket, then bolted together with [stainless] [galvanized]-steel bolts.

2. Cross Section:  Tapered oval, with straight tubular end section to accommodate luminaire.

3. Match pole material and finish.

D. Pole-Top Tenons:  Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

E. Steps:  Fixed steel, with nonslip treads, positioned for 15-inch (381-mm) vertical spacing, alternating on opposite sides of pole; first step at elevation 10 feet (3 m) above finished grade.

Usually delete first paragraph below for poles 90 feet (27 m) or less in height.

F. Intermediate Handhole and Cable Support:  Weathertight, 3-by-5-inch (76-by-127-mm) handhole located at midpoint of pole with cover for access to internal welded attachment lug for electric cable support grip.

G. Grounding and Bonding Lugs:  Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Division 16 Section "Grounding and Bonding," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

H. Cable Support Grip:  Wire-mesh type with rotating attachment eye, sized for diameter of cable and rated for a minimum load equal to weight of supported cable times a 5.0 safety factor.

Coordinate paragraph below with Drawings, manufacturer's standard details, and Project's structural engineer.

I. Platform for Lamp and Ballast Servicing:  Factory fabricated of steel with finish matching that of pole.

Retain any combination of three paragraphs and associated subparagraphs below that applies to steel poles or other steel support components for this Project.  Specify field-painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field-applied coats.

J. Prime-Coat Finish:  Manufacturer's standard prime-coat finish ready for field painting.

K. Galvanized Finish:  After fabrication, hot-dip galvanize complying with ASTM A 123/A 123M.

Retain paragraph above for plain galvanized finish; retain paragraph and subparagraphs below for factory-painted finish.

L. Factory-Painted Finish:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Surface Preparation:  Clean surfaces to comply with SSPC-SP 1, "Solvent Cleaning," to remove dirt, oil, grease, and other contaminants that could impair paint bond.  Grind welds and polish surfaces to a smooth, even finish.  Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1, "White Metal Blast Cleaning," or SSPC-SP 8, "Pickling."

2. Interior Surfaces of Pole:  One coat of bituminous paint, or otherwise treat for equal corrosion protection.

3. Exterior Surfaces:  Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

a. Color:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

2.9 ALUMINUM POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Seamless, extruded structural tube complying with ASTM B 429, Alloy 6063-T6 with access handhole in pole wall.

Retain paragraph above or first paragraph and subparagraphs below.  Retain below for aluminum poles up to 40 feet (12 m) in nominal mounting height and if higher strength or resistance to vibration is required.

B. Poles:  ASTM B 209 (ASTM B 209M), 5052-H34 marine sheet alloy with access handhole in pole wall.

1. Shape:  [Round, tapered] [Round, straight] [Square, tapered] [Square, straight].

2. Mounting Provisions:  Butt flange for bolted mounting on foundation or breakaway support.

C. Pole-Top Tenons:  Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

D. Grounding and Bonding Lugs:  Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Division 16 Section "Grounding and Bonding," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

Revise paragraph and subparagraphs below to suit Project or delete if items are adequately described in Exterior Lighting Device Schedule or details on Drawings.  Indicate span and rise of luminaire brackets on Drawings.

E. Brackets for Luminaires:  Detachable, with pole and adapter fittings of cast aluminum.  Adapter fitting welded to pole and bracket, then bolted together with stainless-steel bolts.

1. Tapered oval cross section, with straight tubular end section to accommodate luminaire.

2. Finish:  Same as [pole] [luminaire].

Retain one of two paragraphs and associated subparagraphs below.  Specify field-painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field-applied coats.

F. Prime-Coat Finish:  Manufacturer's standard prime-coat finish ready for field painting.

G. Aluminum Finish:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain one of four subparagraphs and associated subparagraph below or revise to suit Project.

2. Natural Satin Finish:  Provide fine, directional, medium satin polish (AA-M32); buff complying with AA-M20; and seal aluminum surfaces with clear, hard-coat wax.

3. Class I, Clear Anodic Finish:  AA-M32C22A41 (Mechanical Finish:  medium satin; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

4. Class I, Color Anodic Finish:  AA-M32C22A42/A44 (Mechanical Finish:  medium satin; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker) complying with AAMA 611.

5. <Insert finish.>

Retain one color in subparagraph below with any subparagraph above.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As selected by Architect from manufacturer's full range].

2.10 FIBERGLASS POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Comply with ANSI C136.20, with access handhole in pole wall.

Retain one of two subparagraphs below.

1. Mounting:  Embedded.

2. Mounting Provisions:  Butt flange for bolted mounting on foundation or breakaway support.

B. Resin Color:  [Dark bronze] <Insert color>; provide uniform coloration throughout entire wall thickness.

C. Surface Finish:  Pigmented polyurethane, with a minimum dry film thickness of 1.5 mils (0.04 mm).

2.11 DECORATIVE POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.  Show plan and elevation views of decorative poles on Drawings.

A. Pole Material:

Retain one or more materials in subparagraphs below.  If retaining more than one, indicate specifics on Drawings.  Delete materials not used.

1. Cast ductile iron.

2. Cast gray iron, according to ASTM A 48/A 48M, Class 30.

3. Cast aluminum.

4. Cast concrete.

5. Spun concrete.

6. Steel tube, covered with closed-cell polyurethane foam, with a polyethylene exterior.

7. <Insert material.>

B. Mounting Provisions:

1. Bolted to concrete foundation.

2. Embedded.

C. Fixture Brackets:

1. Cast ductile iron.

2. Cast gray iron.

3. Cast aluminum.

D. Pole Finish:  <Insert finish.>

2.12 LAMINATED WOOD POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.  Show plan and elevation views of laminated wood poles on Drawings.

A. Species and Grades for Structural Glulam Timber:  Engineer and fabricate structural laminated wood poles, complying with AITC 190.1.  Use [southern pine] [Douglas fir] [Alaska cedar] [any species listed in AITC 117 - MANUFACTURING] to withstand indicated structural loads without exceeding allowable design working stresses according to AITC 117 - DESIGN.

B. Features:  Include [wood bracket] [wood crossarm] [pole-top adapter] <Insert other items> for mounting luminaire(s), [metal pole cap, ]and concealed raceway path connected to access handhole.

C. Mounting Provisions:  [Embedded] <Insert description of other mounting, unless detailed on Drawings>.

D. Appearance Grade:  Architectural appearance grade complying with AITC 110.

Waterborne preservatives are not recommended for treating laminated wood poles.  Consult fabricator for approved treatment if wood poles are treated after lamination.

E. Preservative Treatment:  Pressure treat lumber before gluing according to AWPA C28 for waterborne preservatives.  After dressing and end-cutting each member to final size and shape, apply a field-treatment preservative to comply with AWPA M4 to surfaces cut to a depth of more than 1/16 inch (1.6 mm).

F. Adhesive:  Wet-use type complying with ASTM D 2559.

G. End Sealer:  Manufacturer's standard, transparent, colorless wood sealer that is effective in retarding the transmission of moisture at cross-grain cuts and is compatible with indicated finish.

H. Penetrating Sealer:  Manufacturer's standard, transparent, penetrating wood sealer that is compatible with indicated finish.

I. Finish:  [Natural, unstained wood] [Semitransparent stain applied after erection] [Semitransparent stain applied at factory], color as selected by Architect.

2.13 WOOD POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  [Douglas fir] [Southern yellow pine], [machine trimmed by turning, ]complying with ANSI O5.1 and with AWPA C4 for wood species used; and bored, roofed, and gained before treatment.

1. Mounting Provisions:  Embedded.

B. Preservative Treatment:  Pressure treat poles with [creosote] [pentachlorophenol] [ammoniacal copper arsenate] according to AWPA C1 and AWPA C4.

Indicate rise and span of brackets on Drawings.

C. Luminaire Brackets:  Comply with ANSI C136.13.

2.14 PRESTRESSED CONCRETE POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Manufactured [by centrifugal spin-casting process] [of cast concrete].

1. Shape:  [Round, tapered] [Round, straight] [Square, tapered] [Square, straight].

2. Mounting Provisions:  [Steel butt flange for bolted mounting to foundation or breakaway support] [Embedded].

3. Finishing:  Capped at top and plugged at bottom.  Seat each steel reinforcing strand with epoxy adhesive.

4. Grounding:  Continuous copper ground wire cast into pole.  Terminate at top of pole[ and attach to 24-inch (610-mm) lightning rod].

B. Cure with wet steam and age for a minimum of 15 days before installation.

C. Fabricate poles with a hard, nonporous surface that is resistant to water, frost, and road and soil chemicals and that has a maximum water-absorption rate of 3 percent.

D. Cast aluminum nameplate into pole wall at approximately 5 feet (1.5 m) above ground line, listing name of manufacturer, Project identifier, overall height, and approximate weight.

E. Pole Brackets:  Comply with ANSI C136.13.

Coordinate selections in two paragraphs and associated subparagraphs below with standard finish colors and textures offered by manufacturers.

F. Finish Color:  Provided by color material complying with ASTM C 979, uniformly impregnated throughout the pole concrete.  Color material shall provide a uniform, stable, permanent <Insert other adjectives> color and be as follows:

1. Inert, and carbon free.

2. Unaffected by environmental conditions and contaminants including, but not limited to, UV solar radiation, salts, and alkalis.

G. Finish Texture:  [Standard form] [Polished exposed aggregate] [Etched exposed aggregate].

1. Exposed aggregate shall be of <Insert aggregate type selected from manufacturers' lists> type.

2.15 POLE ACCESSORIES

Revise this Article to suit Project, safety codes, and luminaire servicing methods.  Add requirement for removable steps if necessary.  Coordinate with Exterior Lighting Device Schedule on Drawings or with "Requirements for Individual Exterior Lighting Devices" Article.

A. Duplex Receptacle:  120 V, 20 A in a weatherproof assembly complying with Division 16 Section "Wiring Devices" for ground-fault circuit-interrupter type.

1. [Surface mounted] [Recessed], [12 inches (300 mm)] <Insert other mounting height> above finished grade.

2. Nonmetallic polycarbonate plastic or reinforced fiberglass cover, <Insert color to match pole,> that when mounted results in NEMA 250, Type [3R] [4X] enclosure.

3. With cord opening.

4. With lockable hasp and latch that complies with OSHA lockout and tag-out requirements.

B. Minimum 1800-W transformer, protected by replaceable fuses, mounted behind access cover.

Coordinate two paragraphs below with "Breakaway Supports" Paragraph in Part 2 "Poles and Support Components, General Requirements" Article.

C. Base Covers:  Manufacturers' standard metal units, arranged to cover pole's mounting bolts and nuts.  Finish same as pole.

D. Transformer Type Base:  Same material and color as pole.  Coordinate dimensions to suit pole's base flange and accept [ballast(s)] [indicated accessories].

Accessories in paragraph and subparagraphs below are usually selected for decorative poles only; verify availability for other types of poles.

E. Decorative accessories, supplied by decorative pole manufacturer, include the following:

1. Banner Arms:  <Insert material.>

2. Flag Holders:  <Insert material.>

3. Ladder Rests:  <Insert material.>

2.16 LOWERING SYSTEM FOR LUMINAIRES

Retain this Article to specify lowering system for either ring- or carriage-mounted, high-mast luminaire assemblies or individual pole-mounted luminaires.

A. Arrange system to lower luminaire[ assembly] to a servicing position within 36 inches (900 mm) of finished grade in winds up to 30 mph (49 km/h) and to provide for manual plug connection to electrical power in the lowered position for testing.

B. Coordinate with luminaire and pole manufacturers for assembly details, wind-load and vibration analysis, and compatibility of materials for electrolysis-free attachment and connection for luminaire mounting assembly, lowering device, lowering cable, and portable winch.

C. Structural and Mechanical Design:  Use a minimum safety factor of 5.0 for static and dynamic loads of load-bearing components, including cable.

Retain one of two paragraphs and associated subparagraphs below to specify basic features and general arrangement of lowering system.  Coordinate with Drawings.

D. Luminaire Mounting and Disconnect Arrangement:  Multiple [ring] [carriage]-mounted luminaires, arranged for lowering and raising as a group.

Retain one of two subparagraphs below to select method of disconnecting normal electrical operating power for luminaire assembly.  First subparagraph is method used for group disconnect for luminaire assemblies.  Second subparagraph is method used for both individual luminaires and luminaire assemblies.

1. Electrical cable for normal operating power to luminaires manually disconnects inside pole base, using weatherproof multipin connector, and shall be arranged to move within the pole during lowering and raising of luminaire assembly.

2. Electrical cable for normal operating power to luminaires automatically disconnects at a weatherproof multipin connector within the pole-top lowering head at the beginning of the lowering cycle and reconnects when luminaire or luminaire assembly is raised to the operating position.

E. Lowering Device:  Weatherproof, cast-aluminum housing and multiple mechanical latches.  Moving parts of latching assembly shall be located in the portion of the unit that is lowered to the servicing position.  Positive latching in the operating position shall be indicated to the operator at the base of the pole by a clear visual signal, or by other means acceptable to Owner or authorities having jurisdiction.

Stainless-steel cable in paragraph below may be standard with some manufacturers.  Specify stainless-steel cable for corrosive environments.

F. Lowering Cable:  [Zinc-electroplated-] [Stainless-] [Zinc-electroplated- or stainless-]steel aircraft cable.

Coordinate paragraph and subparagraphs below with Drawings.

G. Portable Winch:  [Manual] [120 V electric] type.  [One] <Insert number> required.

Retain two subparagraphs below if winch is electric.

1. Winch Power Connection:  Cord and plug.

2. Winch Raise-Lower Control:  Remote-control station with [15 feet (5 m)] <Insert length> of cable.

Retain paragraph below if a pole lighting circuit rated above 120 V is used to power electric winch.

H. Winch Transformer:  Portable, totally enclosed, encapsulated, single-phase, dry type.  Primary rated at lighting-circuit voltage; secondary rated at 120 V.  Permanent, primary and secondary, twist-locking plug connectors on pigtails shall match pole-base power outlet and winch plug.

2.17 REQUIREMENTS FOR INDIVIDUAL EXTERIOR LIGHTING DEVICES

Delete this Article if exterior luminaires and their supports are scheduled on Drawings.  Retain and revise to suit Project if each exterior lighting device is specified in detail here instead of scheduling on Drawings.  See Editing Instruction No. 7 in the Evaluations for discussion of schedules.  Refer to Exterior Lighting Device Schedule at the end of the Evaluations for use on Drawings.

Copy paragraph and subparagraphs below and re-edit for each type of exterior lighting device in Project.  Assign a unique designation for each type specified, and use these designations on Drawings to show where each unit is required.

A. Exterior Lighting Device Type <Insert drawing designation>:

Retain "Basis-of-Design Product" Subparagraph and list below with "Basis-of-Design Product" Subparagraph in Part 2 "Manufacturers" Article.

1. Basis-of-Design Product:  <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Delete subparagraph above or below.  Retain list of manufacturers with either subparagraph.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

2. [Available ]Manufacturers:

a. <Insert, in separate subparagraphs, manufacturer's name.>

Revise subparagraphs and associated subparagraphs below to list detailed specifications for exterior lighting device being described.  Delete inapplicable subparagraphs; add others to suit description needs.

3. Voltage:  [120] [277] [480]-V ac.

4. Nominal Dimensions:  <Insert nominal dimensions.>

5. Lamps:  <Insert quantity and description if not indicated elsewhere.>

6. Ballast Types and Features:  <Insert type.>

7. Photoelectric Control:  Integrally mounted.

8. Lens:  <Describe types, materials, and features not indicated elsewhere.>

9. Reflector:  <Insert description.>

10. Focusing and Aiming Provisions:  <Insert description.>

11. IESNA Lateral Distribution Class:  [I] [II] [III] [IV] [V].

12. IESNA Cutoff Category:  [Cutoff] [Semicutoff] [Noncutoff].

13. Nominal Beam Spread for Floodlights:  <Insert horizontal degrees times vertical degrees.>

If retaining first subparagraph below, coordinate with Drawings to indicate area to be shielded.

14. Internal Light Shield:  <Insert description.>

15. Photometric Performance of Installed Units:

Retain applicable subparagraphs below and revise to define required photometric performance.  If performance for more than one application is required for same exterior lighting device, copy this material for each instance, labeling each application, and repeat the editing process.

a. Spot Intensity:  Minimum initial [horizontal] [vertical] illumination [at grade] [on subject being illuminated] shall be <Insert fc (lx)> at a point <Insert location of test point>.

b. Average Intensity:  Minimum average initial [horizontal] [vertical] illumination [at grade in the illuminated area] [on subject being illuminated] shall be <Insert fc (lx)>.

c. Uniformity:  For a spacing between adjacent fixtures in parallel rows of <Insert spacing distance>, fixture to fixture and row to row, the maximum-to-minimum initial [horizontal] [vertical] point illumination between any pair of adjacent lighting units, including those in parallel rows, shall be not greater than <Insert ratio>.

d. Cutoff:  Maximum initial [horizontal] [vertical] illumination shall not exceed <Insert fc (lx)> at a point <Insert location of test point>.

See Editing Instruction No. 8 in the Evaluations for discussion of ballast factor.

16. Ballast Factor:  <Insert value.>

See Editing Instruction No. 9 in the Evaluations for discussion of luminaire efficacy rating.

17. Minimum Luminaire Efficacy Rating:  <Insert value.>

Retain subparagraph and associated subparagraphs below if lighting unit includes a pole or other supporting components.

18. Pole Description:

a. Material or Type:  [Steel] [Aluminum] [Fiberglass] [Decorative] [Laminated wood] [Wood] [Prestressed concrete].

b. Luminaire Support Components and Accessories:  [Mast arms] [Metal pole bracket] [Pole-top tenons] [Steps] [Intermediate handhole and cable support] [Grounding and bonding lug] [Cable support grip] <Insert option>.

c. Mounting Provisions:  [Concrete foundation] [Screw foundation] [Embedded].

Delete subparagraph below if mounting heights are defined by other specified material or are indicated on Drawings.

d. Luminaire Mounting Height above Finished Grade:  <Insert dimension.>

PART 3 -  EXECUTION

3.1 LUMINAIRE INSTALLATION

A. Install lamps in each luminaire.

B. Fasten luminaire to indicated structural supports.

Retain subparagraph below if seismic restraint is required by local code or authorities having jurisdiction.  See Evaluations.

1. Use fastening methods and materials selected to resist seismic forces defined for the application and approved by manufacturer.

C. Adjust luminaires that require field adjustment or aiming.[  Include adjustment of photoelectric device to prevent false operation of relay by artificial light sources.]

3.2 POLE INSTALLATION

Retain paragraph below if luminaire alignment for desired light distribution depends on alignment of pole.

A. Align pole foundations and poles for optimum directional alignment of luminaires and their mounting provisions on the pole.

Coordinate paragraph and subparagraphs below with Drawings and revise to suit Project.

B. Clearances:  Maintain the following minimum horizontal distances of poles from surface and underground features, unless otherwise indicated on Drawings:

1. Fire Hydrants and Storm Drainage Piping:  [60 inches (1520 mm)] <Insert dimension>.

2. Water, Gas, Electric, Communication, and Sewer Lines:  [10 feet (3 m)] <Insert dimension>.

3. Trees:  [15 feet (5 m)] <Insert dimension>.

4. <Insert features and clearance dimensions.>

Coordinate first five paragraphs and associated subparagraphs below with Drawings.  See Evaluations for structural- and soil- engineering coordination.

C. Concrete Pole Foundations:  Set anchor bolts according to anchor-bolt templates furnished by pole manufacturer.  Concrete materials, installation, and finishing requirements are specified in Division 3 Section "Cast-in-Place Concrete."

D. Foundation-Mounted Poles:  Mount pole with leveling nuts, and tighten top nuts to torque level recommended by pole manufacturer.

Retain first subparagraph below if seismic restraint is required by local code or authorities having jurisdiction.  See Evaluations.

1. Use anchor bolts and nuts selected to resist seismic forces defined for the application and approved by manufacturer.

2. Grout void between pole base and foundation.  Use nonshrink or expanding concrete grout firmly packed to fill space.

3. Install base covers, unless otherwise indicated.

4. Use a short piece of 1/2-inch- (13-mm-) diameter pipe to make a drain hole through grout.  Arrange to drain condensation from interior of pole.

Retain one of two paragraphs and associated subparagraphs below for embedded poles and coordinate with Drawings.

E. Embedded Poles with Tamped Earth Backfill:  Set poles to depth below finished grade indicated on Drawings, but not less than one-sixth of pole height.

1. Dig holes large enough to permit use of tampers in the full depth of hole.

2. Backfill in 6-inch (150-mm) layers and thoroughly tamp each layer so compaction of backfill is equal to or greater than that of undisturbed earth.

F. Embedded Poles with Concrete Backfill:  Set poles in augered holes to depth below finished grade indicated on Drawings, but not less than one-sixth of pole height.

1. Make holes 6 inches (150 mm) in diameter larger than pole diameter.

2. Fill augered hole around pole with air-entrained concrete having a minimum compressive strength of 3000 psi (20 MPa) at 28 days, and finish in a dome above finished grade.

3. Use a short piece of 1/2-inch- (13-mm-) diameter pipe to make a drain hole through concrete dome.  Arrange to drain condensation from interior of pole.

4. Cure concrete a minimum of 72 hours before performing work on pole.

For projects in seismic areas, retain first paragraph below to minimize possible concentration of horizontal forces during seismic events where poles or pole foundations meet the finished grade.

G. Poles and Pole Foundations Set in Concrete Paved Areas:  Install poles with minimum of 6-inch- (150-mm-) wide, unpaved gap between the pole or pole foundation and the edge of adjacent concrete slab.  Fill unpaved ring with [pea gravel] <Insert material> to a level 1 inch (25 mm) below top of concrete slab.

H. Raise and set poles using web fabric slings (not chain or cable).

3.3 BOLLARD LUMINAIRE INSTALLATION

A. Align units for optimum directional alignment of light distribution.

Retain paragraph below if bollards require protection from damage at base due to landscaping maintenance or snow removal operations.  Coordinate with Drawings.

B. Install on concrete base with top [4 inches (100 mm)] <Insert height> above finished grade or surface at bollard location.  Cast conduit into base, and shape base to match shape of bollard base.  Finish by troweling and rubbing smooth.  Concrete materials, installation, and finishing are specified in Division 3 Section "Cast-in-Place Concrete."

3.4 INSTALLATION OF INDIVIDUAL GROUND-MOUNTING LUMINAIRES

Coordinate this Article with Drawings.  Delete if installation is detailed on Drawings.

A. Install on concrete base with top [4 inches (100 mm)] <Insert height> above finished grade or surface at luminaire location.  Cast conduit into base, and finish by troweling and rubbing smooth.  Concrete materials, installation, and finishing are specified in Division 3 Section "Cast-in-Place Concrete."

3.5 CORROSION PREVENTION

A. Aluminum:  Do not use in contact with earth or concrete.  When in direct contact with a dissimilar metal, protect aluminum by insulating fittings or treatment.

B. Steel Conduits:  Comply with Division 16 Section "Raceways and Boxes." In concrete foundations, wrap conduit with 0.010-inch- (0.254-mm-) thick, pipe-wrapping plastic tape applied with a 50 percent overlap.

3.6 GROUNDING

Coordinate first paragraph and subparagraphs below with Drawings.

A. Ground metal poles and support structures according to Division 16 Section "Grounding and Bonding."

1. Install grounding electrode for each pole, unless otherwise indicated.

2. Install grounding conductor pigtail in the base for connecting luminaire to grounding system.

B. Ground nonmetallic poles and support structures according to Division 16 Section "Grounding and Bonding."

1. Install grounding electrode for each pole.

2. Install grounding conductor and conductor protector.

3. Ground metallic components of pole accessories and foundations.

3.7 FIELD QUALITY CONTROL

A. Inspect each installed fixture for damage.  Replace damaged fixtures and components.

B. Illumination Observations:  Verify normal operation of lighting units after installing luminaires and energizing circuits with normal power source.

1. Verify operation of photoelectric controls.

Retain first paragraph and subparagraphs below if specific illumination performance is indicated.

C. Illumination Tests:

1. Measure light intensities at night.  Use photometers with calibration referenced to NIST standards.  Comply with the following IESNA testing guide(s):

Retain one or more of five subparagraphs below.

a. IESNA LM-5, "Photometric Measurements of Area and Sports Lighting."

b. IESNA LM-50, "Photometric Measurements of Roadway Lighting Installations."

c. IESNA LM-52, "Photometric Measurements of Roadway Sign Installations."

d. IESNA LM-64, "Photometric Measurements of Parking Areas."

e. IESNA LM-72, "Directional Positioning of Photometric Data."

D. Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results.  If adjustments are made to lighting system, retest to demonstrate compliance with standards.

3.8 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain luminaire lowering devices.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 16521END OF SECTION 16521

EXTERIOR LIGHTING
16521 - 1

