Copyright 2002 AIA
MASTERSPEC
03/02 (R 06/03)

Copyright 2003 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16785 - MASTER ANTENNA TELEVISION SYSTEM
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Master antenna television systems using [cable television service] [direct broadcast satellite service] [off-air antenna system] as the signal source.

2. Broadband coaxial cabling for distributing television signal to interface points.

1.3 DEFINITIONS

Retain acronyms, definitions, and terms that remain after this Section has been edited.

A. Agile Receiver:  A broadband receiver that can be tuned to any desired channel.

B. Broadband:  For the purposes of this Section, wide bandwidth equipment or systems that can carry signals occupying in the frequency range of 54 to 1002 MHz.  A broadband communication system can simultaneously accommodate television, voice, data, and many other services.

C. Carrier:  A pure-frequency signal that is modulated to carry information.  In the process of modulation, it is spread out over a wider band.  The carrier frequency is the center frequency on any television channel.

D. CATV:  Community antenna television; a communication system that simultaneously distributes several different channels of broadcast programs and other information to customers via a coaxial cable.

E. CCTV:  Closed-circuit television.

F. CEA:  Consumer Electronics Association.

G. dBmV:  Decibels relative to 1 mV across 75 ohms.  Zero dBmV is defined as 1 mV across 75 ohms.  dBmV = 20 log 10(V1/V2) where V1 is the measurement of voltage at a point having identical impedance to V2 (0.001 V across 75 ohms).

H. Headend:  The control center of the master antenna television system, where incoming signals are amplified, converted, processed, and combined into a common cable along with any locally originated television signals, for transmission to user-interface points.  It is also called the "Central Retransmission Facility."

I. MATV:  Master antenna television; a small television antenna distribution system usually restricted to one or two buildings.

J. RF:  Radio frequency.

K. User Interface:  End point of Contractor's responsibility for Work of this Section.  User interfaces are the [terminal blocks to which the end user may connect coaxial cabling] [75-ohm terminals on device plates] <Define user-interface points>.

1.4 SYSTEM DESCRIPTION

Revise this Article if locally originated television programs or CATV signals are to be added to headend.

A. System shall consist of [off-air signal reception] [direct broadcast satellite service] [cable television service] and a coaxial cable distribution system.

Retain one of first three paragraphs below.  Revise to specify off-air signal reception and direct broadcast satellite service.

B. Headend equipment shall consist of receiving antennas and associated signal amplification and equalization.

C. Distribution of direct broadcast satellite service signals, which includes coordinating with Owner's selected service provider for installation of its dish-type antennas and processing the signals as needed to provide specified services combined into a single-feed point ready for connection into the distribution system.  Obtain signal levels, and noise and distortion characteristics from service provider as the point of departure for system layout and final equipment selection.

D. Distribution of cable television service signals, which includes coordinating with Owner's selected service provider for installation of cable to the service point ready for connection into the distribution system.  Obtain signal levels, and noise and distortion characteristics from service provider as the point of departure for system layout and final equipment selection.

E. Cable distribution system consisting of coaxial cables, user interfaces, signal taps and splitters, RF amplifiers, signal equalizers, power supplies, and required hardware complying with IEEE 802.7 and resulting in performance parameters specified in this Section.  System shall be capable of distributing television channels as follows, according to EIA 542:

1. 12 VHF Channels and FM:  2 through 6 low-band VHF, FM band; and 7 through 13 high-band VHF.

2. 21 CATV Channels:  2 through I (22) low, mid, and high band.

3. 35 CATV Channels 2 through W (36) low, mid, high, and super band.

4. 40 CATV Channels 2 through EE (41) low, mid, high, and super band.

5. 52 CATV Channels 2 through PP (52) low, mid, high, and ultra band.

6. 60 CATV Channels 2 through YY (61) low, mid, high, super, and ultra band.

F. Hardware Requirements:  Use modular, plug-in, solid-state electronic components.  Mount amplifiers and other powered equipment in standard 19-inch (480-mm) cabinet complying with EIA 310.

See Editing Instruction No. 2 in the Evaluations for discussion of data required for off-air stations.

G. Off-Air Stations:  Install antennas for the reception and distribution of scheduled stations.

1.5 PERFORMANCE REQUIREMENTS

A. Minimum acceptable distribution system performance at all user-interface points shall be as follows:

1. RF Video Carrier Level:  Between 3 and 12 dBmV.

2. Relative Video Carrier Level:  Within 3 dB to adjacent channel.

3. Carrier Level Stability, Short Term:  Level shall not change more than 0.5 dB during a 60-minute period.

4. Carrier Level Stability, Long Term:  Level shall not change more than 2 dB during a 24-hour period.

5. Channel Frequency Response:  Across any 6-MHz channel in 54- to 220-MHz frequency range, referenced to video , signal amplitude shall be plus or minus 1 dB, maximum.

6. Carrier-to-Noise Ratio:  45 dB or more.

7. RF Visual Signal-to-Noise Ratio:  43 dB or more.

Tests listed below require more expensive equipment than is required for tests listed above.  Retain tests considered to be necessary.

8. Cross Modulation:  Less than minus 50 dB.

9. Carrier-to-Echo Ratio:  More than 40 dB.

10. Composite Triple Beat:  Less than minus 53 dB.

11. Second Order Beat:  Less than minus 60 dB.

12. Terminal Isolation from Television to Television:  25 dB, minimum.

13. Terminal Isolation between Television and FM:  35 dB, minimum.

14. Hum Modulation:  2 percent, maximum.

Retain three subparagraphs below if FM reception capability is required.

15. RF FM Carrier Level:  13 to 17 dB below video carrier level.

16. FM Frequency Response:  More than the 88- to 108-MHz frequency range, signal amplitude is plus or minus 0.75 dB, maximum.

17. FM Carrier-to-Noise Ratio:  More than 24 dB.

1.6 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Show fabrication and installation details for television equipment.

1. Include plans, elevations, sections, details, and attachments to other work.

2. For coaxial cable, include the following installation data for each type used:

a. Nominal OD.

b. Minimum bending radius.

c. Maximum pulling tension.

Retain first two subparagraphs below if custom equipment, such as operator panels and consoles, is specified in this Section.  Edit to suit Project and coordinate with Drawings.

3. Functional Block Diagram:  Show single-line interconnections between components for headend and distribution system to user-interface points.  Show cable types and sizes.

4. Dimensioned plan and elevations of headend equipment.  Show access and workspace requirements.

5. Wiring Diagrams:  Power, signal, and control wiring; and grounding.

Delete subparagraph below if signal attenuation budget and losses are indicated on Drawings or if signal strength to user interfaces is indicated.

6. Design Calculations:  Calculate signal attenuation budget and show calculated line and equipment losses for the system based on the functional block diagram, to show that proposed system layout can be expected to perform up to specification.  Calculate signal strength from sources to headend input points for each antenna and CATV grouping.  Allowable losses between components and User Interface shall be used to determine size and type of coaxial cable.

C. Equipment List:  Include every piece of equipment by model number, manufacturer, serial number, location, and date of original installation.  Add testing record of each piece of adjustable equipment, listing name of person testing, date of test, and description of as-left set points.

D. Source quality-control test reports on coaxial cable sweep tests.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For headend and distribution system to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "[Closeout Procedures] [Operation and Maintenance Data]," include the following:

1. Lists of spare parts and replacement components recommended to be stored at the site for ready access.

Retain subparagraph below if Drawings do not include details of equipment layouts or if Project involves unusual coordination requirements.

2. Include dimensioned plan and elevation views of components and enclosures.  Show access and workspace requirements.

Retain paragraph below if device plate appearance coordination is required.

G. Samples:  Full size, for each outlet and finish plate, for colors and textures required.

1.7 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NECA 1.

C. Comply with NFPA 70.

1.8 PROJECT CONDITIONS

A. Environmental Limitations:  System components shall be equipped and rated for the environments where installed.

B. Environmental Conditions:  Capable of withstanding the following environmental conditions without mechanical or electrical damage or degradation of operating capability:

Select from and revise conditions in three subparagraphs below and specify features required to provide satisfactory service.

1. Interior, Controlled Environment:  System components, except central-station control unit, installed in [air-conditioned] [temperature-controlled] interior environments shall be rated for continuous operation in ambient conditions of [36 to 122 deg F (2 to 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, noncondensing.  NEMA 250, Type 1 enclosures.

2. Interior, Uncontrolled Environment:  System components installed in non-[air-conditioned] [temperature-controlled] interior environments shall be rated for continuous operation in ambient conditions of [0 to 122 deg F (minus 18 to plus 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, noncondensing.  NEMA 250, Type [3R] [4] [12] [12K] enclosures.

3. Exterior Environment:  System components installed in locations exposed to weather shall be rated for continuous operation in ambient conditions of [minus 30 to plus 122 deg F (minus 34 to plus 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, condensing.  Rate for continuous operation when exposed to rain as specified in NEMA 250, winds up to [85 mph (137 km/h)] [and snow cover up to 24 inches (610 mm) thick].  NEMA 250, Type [3] [3R] [3S] [4] [4X] enclosures.

1.9 COORDINATION

A. Coordinate size and location of raceway system, and provisions for electrical power to equipment of this Section.

Retain first paragraph below if Work of this Section is required to interface with CATV service providers.

B. Coordinate Work of this Section with requirements of [off-air signal reception] [direct broadcast satellite] [cable television] service provider.

C. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

D. Coordinate installation of curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.10 MAINTENANCE SERVICE

Consider deleting this Article for light or residential use; consider including a provision for submitting a continuing maintenance agreement proposal.  Revise starting date if required.

A. Initial Maintenance Service:  Beginning at Substantial Completion, provide [three] [six] [nine] [12] months' full maintenance by skilled employees of MATV system Installer.  Include quarterly adjusting as required for optimum system performance.

1.11 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.  Normally, extra materials can be limited to videotape cassettes.

A. Furnish extra materials described below, before installation begins, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.  Provide no fewer than one of each item listed below.  Deliver extra materials to Owner.

Quantities indicated for items below are examples only.  Coordinate with systems specified.  Revise to suit Project.

1. Fuses:  One for every 10; each type and rating.

2. Splitters:  One for every 10 installed.

3. MATV Distribution Power Amplifiers:  One for every 10; each type installed.

4. MATV Signal Traps:  One for every 10; each type used.

5. MATV Attenuators:  One for every 10; each type used.

6. Cable:  100 feet (30 m); each type used.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 SYSTEMS REQUIREMENTS

A. Components:  Modular plug-in, heavy-duty, industrial- or commercial-grade units.

B. Equipment:  Silicon-based, solid-state, integrated circuit devices.

C. Power Supply Characteristics:  Devices shall be within specified parameters for ac supply voltages within the range of 105 to 130 V.

D. Protect signal cables and connected components against transient-voltage surges by suppressors and absorbers designed specifically for the purpose.  Comply with Division 16 Section "Transient Voltage Suppression."

E. Provide ac-powered equipment with integral surge suppressors, complying with UL 1449.

F. RF and Video Impedance Matching:  Signal-handling components, including connecting cable, shall have end-to-end impedance-matched signal paths.  Match and balance devices used at connections where it is impossible to avoid impedance mismatch or mismatch of balanced circuits to unbalanced circuits.

2.3 MATV EQUIPMENT

A. Description:  Signal-source components, signal-processing and amplifying equipment, distribution components, and interconnecting wiring.  System shall receive signals from sources, amplify and process them, and distribute them to outlets for receiving sets.  Equipment shall translate UHF channels to VHF channels before distribution to outlets.

Clear descriptions of signal sources used and program channels distributed are critical to obtaining meaningful Contractor response to MATV system requirements.  See the MATV Signal Source and Channel Schedule in the Evaluations.  Include FM stations as needed.  Delete paragraph and subparagraph below if scheduled on Drawings.  Coordinate with Drawings.

B. Identification of Signal Sources and Channels Distributed:

1. <Insert signal source and basic channel selection.>

Revise both paragraphs below to provide functional and operational descriptions to suit Project.

C. MATV System Qualitative Performance Requirements:  Reception quality of color-television program transmissions at each system outlet from each designated channel and source shall be equal to or superior than that obtained with performance checks specified in Part 3 "Field Quality Control" Article, using a standard, commercial, cable-ready, color-television receiver.

D. MATV System Quantitative Performance Requirements:  Level and quality of signal at each outlet from each designated channel and source shall comply with Specifications below when tested according to 47 CFR 76.

2.4 OFF-AIR ANTENNAS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Channel Master, Inc.

2. RadioShack Corporation.

3. Terk Technologies.

4. Winegard Company.

5. <Insert manufacturer's name.>

B. Antennas shall be tested, marked, and packaged, complying with EIA 774, EIA CEB 6, and EIA CEB 7.  Antennas shall be labeled complying with CEA antenna mapping program.

Edit wind velocity in paragraph below to suit conditions at Project site and manufacturers' standard ratings.

C. Off-Air, Mast-Mounted Antennas:  Weatherproof single-channel or broadband type, constructed of high-strength anodized aluminum and rated to survive in a 100-mph (160-km/h) wind, minimum.

1. Elements:  Internally dampened against such mechanical vibration as may occur in service.

2. Ends of Crossarms and Elements:  Sealed.

3. Mounting and Connecting Hardware:  Corrosion proof.

4. Frequency Range:  Matched to source frequencies.

See Editing Instruction No. 3 in the Evaluations for discussion of CEA antenna reception pattern options and scheduling.  Delete subparagraph below if reception patterns are scheduled on Drawings.

5. CEA Reception Patterns:  <Insert reception pattern and number of antennas>.

Delete subparagraph below if FM distribution is not specified or if FM signal is to be obtained from a broadband antenna.

6. FM Antenna:  Separate from the broadband antenna and [omnidirectional] [directional] type, with 2-dB minimum gain.

Coordinate paragraph and subparagraphs below with Drawings.  Revise wind requirement for Project location.

D. Antenna-Supporting Structures:  Prefabricated, hot-dip galvanized-steel units.

1. Strength of Structure and Attachments:  Adequate to withstand 100-mph (160-km/h) winds while supporting installed antennas.

2. Comply with 47 CFR 17 and TIA/EIA 222.

Retain obstruction lighting requirements in subparagraph below if applicable.

3. Comply with FAA AC 70/7460-1.

2.5 MATV HEADEND COMPONENTS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Blonder Tongue Laboratories, Inc.

2. Canare Corporation of America.

3. Channel Master, Inc.

4. Leviton Voice & Data Division.

5. Motorola Broadband Communications Sector.

6. Quality RF Services, Inc.

7. Scientific-Atlanta, Inc.

8. <Insert manufacturer's name.>

B. Headend Equipment:  [Channel mixers, processors for channel translation] [Broadband amplifier] [Single-channel amplifiers] [Combining networks] for receiving off-air television and FM signals and outputting the signals to cable distribution system.  Equip coaxial down leads of the off-air antennas with preamplifiers to send signals at strength required by headend.  Headend component performance specified in this Article is minimum acceptable; better performance may be required to meet minimum acceptable system performance standard in Part 1.

1. House units in standard 19-inch (483-mm) electronic equipment cabinet complying with EIA 310.

C. Antenna Combiner:  Directional coupler design network, combining up to eight antenna signals into a single output.  Frequency response of the device shall be 5 to 400 MHz, and the insertion loss between input ports shall be not less than 40 dB.

D. Down-Lead Preamplifiers:  Antenna mast-mounted preamplifier designed to boost antenna signal, contained in weatherproof housing, single-channel or broadband type.  Install power supplies indoors at headend equipment, connected through power inserters to provide power to preamplifiers through the coaxial down-lead cable.

1. Frequency Response:  Plus or minus 0.75 dB.

2. Minimum Input:  Minus 20 dBmV.

3. Return Loss:  14 dB.

4. I/O Impedance:  75 ohms.

E. Channel Mixers:  Use for nonadjacent channels only.

1. Insertion Loss (Maximum 54 to 216 MHz):  2.5 dB.

2. Return Loss:  14 dB.

3. Out-of-Band Rejection:  12 dB.

4. I/O Impedance:  75 ohms.

F. Processors:  One for each channel to be translated.

1. Bandwidth:  6 MHz.

2. Return Loss:  16 dB, within the 6-MHz bandwidth.

3. Noise:  Not more than 10 dB at maximum gain.

4. Input Level Range, VHF:  Minus 20 to plus 30 dBmV.

5. Input Level Range, UHF:  Minus 20 to plus 25 dBmV.

6. Output Level Range:  50 to 60 dBmV.

7. Carrier-to-Noise Ratio:  Minus 57 dB at plus 10-dBmV input.

8. Automatic Gain Control:  Plus or minus 1-dB output variation for rated input level range variation.

9. Frequency Stability:  Plus or minus 10 KHz over the operational temperature range.

10. Spurious Output:  60 dB below the video carrier with video carrier output level at plus 60 dBmV and audio carrier level at plus 45 dBmV.

11. Adjacent Channel Rejection:  Not less than 60 dB.

12. I/O Impedance:  75 ohms.

G. Broadband Amplifier:

1. Frequency Range:  [54 to 108, 174 to 220] [54 to 220] MHz.

2. Frequency Response:  Plus or minus 1.0 dB across passband.

3. Maximum Noise:  10 dB.

4. Minimum Return Loss:  16 dB.

5. I/O Impedance:  75 ohms.

H. Single-Channel Amplifiers:

1. Frequency Range:  6 MHz for specified channel.

2. Frequency response:  Plus or minus 0.5 dB.

3. Minimum Return Loss:  14 dB.

4. Maximum Noise:  10 dB.

5. Automatic Gain Control:  Plus or minus 1-dB output variation for rated input level range variation.

6. Skirt Rejection:  Minus 26 dB at plus or minus 5 MHz from channel center.

7. Sound Trap:  Adjustable to 10 VdB of attenuation of the sound carrier.

8. Impedance:  75 ohms for input and output terminals.

Retain first paragraph and associated subparagraphs below if single-station FM receiver modules are required.

I. FM Module:  One RF processor module for each station listed.

1. Frequency:  Between 88 to 108 MHz.

2. Output Level:  52 dBmV.

3. Output Level Control:  Plus or minus 10 dB.

4. Stability:  0.005 percent, crystal controlled.

5. Sensitivity:  3 mV for 30-dB quieting.

6. Input Level:  60 mV, stereo.

7. Image Rejection:  901 dB.

8. Passband:  200 kHz.

Adjust selectivity in subparagraph below if indicated.

9. Selectivity:  Plus or minus 150 kHz or less, at 30 dB down.  Plus or minus 250 kHz or less, at 50 dB down.

J. Combining network (mixer) shall be used to combine the off-air TV [FM] [and] [CATV] signals into a single-broadband output.  With an output test point, 75-ohm television jack, mixer output step attenuator dual-pilot insertion network, and a removable mixer-to-trunk jumper.

1. Passband:  As required by system performance.

2. Distortion:  Not more than plus or minus 0.1 dB over any 6-MHz segment.

3. Distortion:  Not more than plus or minus 0.5 dB over the 54- to 216-MHz frequency range.

4. Nominal Insertion Loss:

a. 15 dB maximum, channel input to single-system output.

b. 13 dB maximum, channel input to mixer output.

c. 20 dB maximum at test point, e.g., loss from trunk output.

5. Isolation between any Two Inputs:  30 dB.

6. Impedance:  70 ohms for input and output terminals.

2.6 DISTRIBUTION COMPONENTS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Canare Corporation of America.

2. Leviton Voice & Data Division.

3. Motorola Broadband Communications Sector.

4. Quality RF Services, Inc.

5. Scientific-Atlanta, Inc.

6. <Insert manufacturer's name.>

B. Distribution components shall be for signal processing and distribution downstream from headend equipment.

C. Signal Power Splitters and Isolation Taps:  Metal-enclosed directional couplers with brass connector parts.  Where installed in signal circuits used to supply cable-powered amplifiers, power throughput capacity shall exceed load by at least 25 percent.

1. Return Loss:  17 dB.

2. RFI Shielding:  100 dB.

3. Isolation:  25 dB.

4. Impedance:  75 ohms for input and output terminals.

5. Electrically powered components shall be UL labeled.

D. Distribution System Amplifiers:  Powered by coaxial cable system, equipped with surge protection device and external test points to allow convenient signal monitoring.

E. Cable System Power Supplies:  Plug-in modular construction, with surge, short circuit, and overload protection.

F. Signal Traps:  Packaged filters tuned to interference frequencies encountered in Project.

G. Attenuators:  Passive, of fixed value, used to balance signal levels.

H. Terminating Resistors:  Enclosed units rated 0.5 W and matched for coaxial impedance.

Coordinate paragraph and subparagraphs below with Drawings.

I. User-Interface Device:  Flush, female-type outlets, designed to mimic power duplex outlet, for mounting in standard outlet box, with metallic parts of anodized brass, beryllium copper, or phosphor bronze.  Cable connector mounting shall be semirecessed so its protrusion is flush with the plane of device plate.[ Feedthrough-type cable connection shall not be used] [, except in area housing a single tenant] [, except within a single-dwelling unit].

1. Cable Connector:  Female, Type F.

2. Wall Plates:  Match materials and finish of power outlets in same space.

3. Attenuation:  Less than 0.1 dB.

4. Voltage Standing-Wave Ratio:  Less than 1.15 to 1.

2.7 CABLES

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alpha Wire Company.

2. Belden Inc.; Electronics Division.

3. Coleman Cable.

4. CommScope Properties, LLC.

5. Helix/HiTemp Cables, Inc.; Draka USA.

6. West Penn Wire/CDT; a division of Cable Design Technologies, Inc.

7. <Insert manufacturer's name.>

See Evaluations for discussion of coaxial cables.  Indicate types on Drawings.

B. Cable Characteristics:  Broadband type, recommended by cable manufacturer specifically for broadband MATV applications.  Coaxial cable and accessories shall have 75-ohm nominal impedance with a return loss of 20 dB minimum from 7 to 806 MHz, and shall be listed to comply with NFPA 70, Articles 810 and 820.

Cables in five paragraphs below are typical; revise to suit Project.  Show cable types on Drawings.

C. RG-11/U, Outdoor Antenna Lead-In Cable:  No. 14 AWG, solid, copper-covered steel conductor; gas-injected foam-PE insulation.  Double shielded with 100 percent aluminum polyester tape, and 60 percent aluminum braid.  Jacketed with sunlight-resistant black PVC or PE.  Suitable for outdoor installations in ambient temperatures ranging from minus 40 to plus 85 deg C; NFPA 70, Type CATV.

D. RG59/U, Indoor Headend Cable:  No. 20 AWG, solid, silver-plated, copper-covered steel conductor; gas-injected foam-PE insulation.  Triple shielded with 100 percent aluminum polyester tape, 95 percent aluminum braid; covered by aluminum foil with grounding strip.  Color-coded PVC jacket.  NFPA 70, Type CATVR.

E. RG-6/U, Indoor Riser Cable:  No. 16 AWG, solid, copper-covered steel conductor; gas-injected foam-PE insulation.  Double shielded with 100 percent aluminum-foil shield, 60 percent aluminum braid.  Jacketed with black PVC or PE.  Suitable for indoor installations; NFPA 70, Type CATV or CM.

F. RG59/U, Indoor Distribution Cable:  No. 20 AWG, solid, copper-covered steel conductor; gas-injected foam-PE insulation.  Double shielded with 100 percent aluminum polyester tape, 40 percent aluminum braid.  PVC jacket.  NFPA 70, Type CATV.

G. RG59/U, Plenum-Rated Indoor Distribution Cable:  No. 20 AWG, solid, copper-covered steel conductor; foam fluorinated ethylene propylene insulation.  Double shielded with 100 percent aluminum-foil shield, 65 percent aluminum braid.  Copolymer jacket.  NFPA 70, Type CATV and UL 910.

2.8 CABLE CONNECTORS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Amphenol Corporation.

2. B&L Coaxial Connections, Ltd.

3. Connect-Tech Products.

4. Leviton Voice & Data Division.

5. <Insert manufacturer's name.>

B. MATV Coaxial Cable Connectors:  Type F, 75 ohms.

C. Patch Panels:  Standard electrical enclosures, with NEMA 250 type suitable for environmental conditions at the installed location, with bulkheads and Type F connectors for splicing and patching coaxial cable.

2.9 SOURCE QUALITY CONTROL

A. Cable products shall be sweep tested at the factory before shipping at frequencies from 5 MHz to 1 GHz.  Sweep test shall test the frequency response, or attenuation over frequency, of a cable by generating a voltage whose frequency is varied through the specified frequency range and graphing the results.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine pathway elements intended for coaxial cable installation.  Check raceways, cables, trays, and other elements for compliance with accessibility for installation and maintenance, and other conditions affecting installation.

B. Examine roughing-in for antenna to verify actual locations of cable connections before antenna installation.

C. Examine walls, floors, roofs, equipment bases, and roof supports for suitable conditions where television equipment is to be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install signal line surge suppressors on coaxial cables entering headend equipment space and at antenna mounted amplifiers.  Comply with Division 16 Section "Transient Voltage Suppression."

B. Support and anchor antenna towers, masts, and mountings.

1. Concrete Foundations:  Reinforced concrete complying with Division 3 Section "Cast-in-Place Concrete."

2. Steel Anchorage Components:  Galvanized-steel shapes and plates complying with Division 5 Section "Structural Steel."

3.3 GENERAL WIRING

Delete first two paragraphs below if wiring method is indicated on Drawings; otherwise, retain one of the two.

A. Wiring Method:  Install cables in raceways except in accessible indoor ceiling spaces, attics,[ in hollow gypsum-board partitions,] and as otherwise indicated.  Conceal raceways and wiring except in unfinished spaces.

B. Wiring Method:  Install cables concealed in accessible ceilings, walls, and floors where possible.

C. Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.  Provide and use lacing bars and distribution spools.

D. Splices, Taps, and Terminations:  For power and control wiring, use numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

E. Grounding:  According to recommendations in IEEE 142 and IEEE 1100.

3.4 COAXIAL CABLE INSTALLATION

A. Cold-Weather Installation:  Bring cable to room temperature before dereeling.  Heat lamps may not be used for heating.

B. Cable may not be installed in same raceway with power cable.

C. Coaxial cable shall not be spliced except on plywood backboards in wire closets, or in cabinets designated for the purpose.

D. Outdoor connections shall be installed in enclosures meeting NEMA 250, Type 4X.  Connectors shall be corrosion resistant with properly designed O-rings to keep out moisture.

E. Do not use water-based cable pulling lubricants with PVC-jacketed cable.

F. Do not exceed manufacturer's recommended minimum bending radiuses

G. Attach antenna lead-in cable to support structure at intervals not exceeding 3 feet (1 m).

H. Pulling Cable:  Do not exceed manufacturer's recommended pulling tensions.  Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

Delete first paragraph below if required to coordinate with indicated wiring method.

I. Exposed Cable:  Install parallel to building lines, follow surface contours, and support cable according to manufacturer's written instructions.  Do not run adjacent and parallel to power or data cables.

J. Cable Support:  Install supports at intervals recommended in writing by cable manufacturer.  Install supports within 6 inches (150 mm) of connector so no weight of cable is carried by connector.  Use no staples or wire ties, pull tie-wrap snug, and do not over tighten.

K. Signal Equalization:  Where system performance may be degraded in certain operating modes, revise component connections and install distribution amplifiers and attenuators as required, providing a balanced signal across the system.

L. Install passive circuit devices, such as splitters and attenuators, in wire closets or cabinets.  Do not install attenuators as part of user-interface device outlets.

3.5 ANTENNA AND HEADEND INSTALLATION

Coordinate this Article with Drawings.

A. Mount headend equipment in electronic equipment cabinets recommended by manufacturer.  Group related items in methodical sequence.

B. Arrange equipment to facilitate access for maintenance and to preserve headroom and passage space.  Parts that require periodic service or maintenance shall be readily accessible.  Headend components that require tuning adjustments shall be accessible from the front of equipment cabinets.

C. Align antenna elements to achieve maximum signal level and quality.

D. Antenna-Supporting Structure:  Increase antenna height as required to obtain signal strength needed for specified system performance.

Retain one or both of first two subparagraphs below.  Delete both if Drawings detail attachment.  Revise bolt sizes as recommended by structural engineer.

1. Attachment to Building:  Use 0.375-inch- (10-mm-) minimum expansion anchors for masonry, and place anchors clear of grout or mortar joints.

2. Attachment to Building:  Use 0.375-inch- (10-mm-) minimum lag bolts for attachment to wood.

3. Grounding:  As a minimum, comply with NFPA 780, "Installation of Lightning Protection Systems."

E. Antenna Cable Entrance:  Use entrance fittings, seal, and waterproof penetrations of the building envelope.

3.6 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals according to Division 16 Section "Electrical Identification."

3.7 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Inspection:  Verify that units and controls are properly installed, connected, and labeled, and that interconnecting wires and terminals are identified.

C. Pretesting:  Align and adjust system and pretest components, wiring, and functions to verify that they comply with specified requirements.  Replace malfunctioning or damaged items.  Retest until satisfactory performance and conditions are achieved.  Prepare television equipment for acceptance and operational testing as follows:

Retain applicable subparagraphs below and edit to provide performance criteria consistent with signal sources used in Project.

1. Use an agile receiver and signal strength meter or spectrum analyzer for testing.

2. Off-Air, Mast-Mounted Antenna Sources:  Connect receiver to the down lead of a 10-element, single-channel antenna, tuned and oriented to optimize reception for the channel and placed at system antenna's location.  Alternatively, connect receiver to a single-channel video amplifier connected to the down lead of the above single-channel antenna.

3. CATV Sources:  Connect receiver to an agile demodulator or CATV set-top converter at CATV service entrance to the facility.

4. Satellite Earth-Station System Sources:  Adapt receiver to the output of satellite-TV receiver.

5. CCTV Sources:  Connect receiver to the output of each CCTV signal source or the distribution amplifier associated with it.

D. Test Schedule:  Schedule tests after pretesting has successfully been completed and system has been in normal functional operation for at least 14 days.  Provide a minimum of 10 days' notice of test schedule.

E. Operational Tests:  Perform operational system tests to verify that system complies with Specifications.  Include all modes of system operation.  Test equipment for proper operation in all functional modes.

F. Distribution System Acceptance Tests:

1. Field-Strength Instrument:  Rated for minus 40-dBmV measuring sensitivity and a frequency range of 54 to 812 MHz, minimum.  Provide documentation of recent calibration against recognized standards.

2. Signal Level and Picture Quality:  Use a field-strength meter or spectrum analyzer, and a standard TV receiver to measure signal levels and check picture quality at [all] [random sampling of 25 percent of outlets] <Insert number or percentage>.  User-interface outlets.

a. Test the signal strength in dBmV at 55[, 151, 547,] and 750 MHz.

b. Minimum acceptable signal level is 0 dBmV (1000 mV).

c. Maximum acceptable signal level over the entire bandwidth is 15 dBmV.

d. Television receiver shall show no evidence of cross-channel intermodulation, ghost images, or beat interference.

3. Signal-to-Noise-Ratio Test:  Use a field-strength meter to make a sequence of measurements at the output of the last distribution amplifier or of another agreed-on location in system.  With system operating at normal levels, tune meter to the picture carrier frequency of each of the designated channels in turn and record the level.  With signal removed and input to corresponding headend amplifier terminated at 75 ohms, measure the level of noise at same tuning settings.  With meter correction factor added to last readings, differences from first set must not be less than 45 dB.

Retain first paragraph and associated subparagraphs below if required for Project.

G. Qualitative and Quantitative Performance Tests:  Demonstrate reception quality of color-television program transmissions at each user interface from each designated channel and source.  Quality shall be equal to or superior than that obtained with performance checks specified below, using a standard, commercial, cable-ready, color-television receiver.  Level and quality of signal at each outlet and from each designated channel and source shall comply with the following Specifications when tested according to 47 CFR 76:

1. RF video-carrier level.

2. Relative video-carrier level.

3. Carrier level stability, 60-minute and 24-hour periods.

4. Broadband frequency response.

5. Channel frequency response.

6. Carrier-to-noise ratio.

7. RF visual signal-to-noise ratio.

Tests listed below require more expensive equipment than is required for tests listed above.  Select tests considered to be necessary.

8. Cross modulation.

9. Carrier-to-echo ratio.

10. Composite triple beat.

11. Second order beat.

12. Terminal isolation.

13. Terminal isolation between television and FM.

14. Hum modulation.

Delete subparagraphs below if FM reception capability is not desired.

15. RF FM carrier level.

16. FM frequency response.

17. FM carrier-to-noise ratio.

H. Record test results.

I. Retest:  Correct deficiencies identified by tests and observations and retest until requirements specified in Part 1 are met.

3.8 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain MATV equipment.

1. Train Owner's maintenance personnel on procedures and schedules for troubleshooting, servicing, and maintaining equipment.

2. Demonstrate methods of determining optimum alignment and adjustment of components and settings for system controls.

3. Demonstrate programming and tuning of satellite receivers.

4. Refer to Division 1 Section "Demonstration and Training."

Revise number of training hours in paragraph below to suit Project.  Coordinate with Division 1 Sections.

B. Conduct a minimum of six hours' training as specified in instructions to Owner's employees in Division 1 Section "Closeout Procedures."

END OF SECTION 16785

MASTER ANTENNA TELEVISION SYSTEM
16785 - 1

