Copyright 1997 AIA
GSA VERSION MASTERSPEC(
06/97 (GSA 03/03)


Copyright 1997 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15081 - DUCT INSULATION
PART 1 -  GENERAL

This Section uses the term Architect.  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project’s Specifications; Section titles may have changed.

1.1 RELATED DOCUMENTS

A. Drawings, and the general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.  

1.2 SUMMARY

A. This Section includes semirigid and flexible duct, plenum, and breeching insulation; insulating cements; field-applied jackets; accessories and attachments; and sealing compounds.

B. Related Sections include the following:

List below only projects, construction, and equipment that the reader might expect to find in this Section, but are specified elsewhere.

1. Division 7 Section "Firestopping" for firestopping materials and requirements for penetrations through fire and smoke barriers.

2. Division 15 Section “Mechanical – General Conditions” for additional submittal and procedural requirements.

3. Division 15 Section "Equipment Insulation" for insulation materials and application for pumps, tanks, hydronic specialties, and other equipment.

4. Division 15 Section "Pipe Insulation" for insulation for piping systems.

5. Division 15 Section "Metal Ducts" for duct liner.

6. Division 15 Section “Basic Materials and Methods” for additional material specifications.

C. In conformance with ASHRAE, MBtu or MBh, intended to mean 1000 Btu and 1000 Btu/hr, respectively, will not be used in this section.  Instead k will indicate 1000 and M, if used, will indicate 1,000,000 or 106.

1.3 SUBMITTALS

A. Product Data:  Identify thermal conductivity, thickness, and jackets (both factory and field applied, if any), for each type of product indicated.

Detailed Shop Drawings are a cost factor for Contractor and require considerable time for review.  Require them only if Drawings do not show enough detail or for complex areas.  List those areas.

B. Shop Drawings:  Show fabrication and installation details for the following:

1. Removable insulation sections at access panels.

2. Application of field-applied jackets.

3. Applications of insulation at linkages for control devices.

4. Application of insulation on irregular shapes.

5. Application of insulation on fire and smoke dampers.

C. Samples:  Provide samples for each type of insulation and field-applied jacket.  Identify each Sample, describing product and intended use.  Submit 300-mm- (12-inch-) square sections of each sample material.

1. Manufacturer's Color Charts:  Show the full range of colors available for each type of field-applied finish material indicated.

2. Example of edge and corner treatment on rectangular duct.

D. Material Test Reports:  Submit data from a qualified testing agency acceptable to the authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealants, attachments, cements, and jackets with requirements indicated in Section 6 - Heating, Ventilating, and Air Conditioning, Section 7 - Service Water Heating, of ASHRAE/IESNA Standard 90.1, including related tables shown at the end of this section.  Include dates of tests.

E. Installer Certificates:  Submit a letter, signed by the Contractor certifying that the installers and materials comply with the requirements of this and other applicable specifications.

F. Warranty: 

1. Submit a sample of the warranty that will be signed by the Contractor certifying that the installation and materials comply with the requirements of this and other applicable specifications. 

2. Provide special warranty as specified in this section.
1.4 QUALITY ASSURANCE

A. ASHRAE/IESNA Compliance:
All insulation characteristics shall comply with the requirements of ASHRAE Standard 90.1, including related tables contained therein.  Insulation characteristics shall comply with all applicable requirements of ASHRAE Standard 90.1.  All supply ductwork with the exception of buried ductwork and ductwork located in indirectly conditioned spaces shall be insulated in accordance with ASHRAE Standard 90.1.  All supply duct insulation shall have a vapor barrier jacket.  The vapor barrier jacket shall cover the duct system with a continuous, unbroken vapor seal.  All return and exhaust air distribution systems shall be insulated in accordance with ASHRAE Standard 90.1. 

B. Code of Federal Regulations Compliance: All insulation characteristics shall comply with the requirements of the Code of Federal Regulations 10 CFR-435.107 including related tables shown therein and shown at the end of this section.

C. General Services Administration (GSA) Compliance: All insulation characteristics shall comply with the requirements of the Codes and Standards published in the GSA document Facilities Standards for the Public Buildings including related tables shown therein and at the end of this section.

D. General Compliance:
Where the requirements for a description of insulation characteristics or performance ratings defined in a publication or standard referenced herein conflict, the most restrictive shall apply.

E. Installer Qualifications: Insulation shall be installed by skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the U.S. Department of Labor, Bureau of Apprenticeship and Training.

F. Fire-Test-Response Characteristics:  As determined by testing materials identical to those specified in this Section according to ASTM E 84, NFPA 255 and UL 723 by a testing and inspecting agency acceptable to authorities having jurisdiction.  Accessories such as adhesives, mastics, cements, tapes, etc., shall have the same or better fire and smoke hazard ratings as that identified for the insulation materials.  Factory label insulation and jacket materials and sealer and cement material containers with appropriate markings of applicable testing and inspecting agency.

1. Insulation Installed Indoors:  Flame-spread rating of 25 or less, and smoke-developed rating of 50 or less.

2. Insulation Installed Outdoors:  Flame-spread rating of 75 or less, and smoke-developed rating of 150 or less.

G. Mockups:  Before beginning the actual installation of the insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes.  Mockups shall be located and displayed at the project site until directed otherwise by the Government.  Build mockups according to the following requirements, using materials indicated for the completed Work:

1. Include the following mockups:

a. One 3 m (10 foot) section of rectangular straight duct.

b. One 90-degree square elbow and one 90-degree rectangular radius elbow.

c. One 90 degree round, radius type elbow.

d. One rectangular and one round branch takeoff.

e. One transition fitting.

f. Four support hangers.

g. One 10 foot (3 m) 3 foot (1 m) section adjacent to a fire damper.

2. Mockups shall be built with cutaway sections to allow observation of application details for insulation materials, mastics, attachments, and jackets.

3. Build mockups in the location indicated or, if not indicated, as directed by the Government.

4. Notify the Government seven days in advance of the dates and times when mockups will be constructed.

5. Obtain Government's approval of mockups before starting insulation application.

6. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

7. Mockups shall remain the property of the Contractor but shall only be removed from the project site when directed by the Government.

Retain below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 1, Section “Quality Requirements” for demolishing and removing mockups when directed, unless otherwise indicated.

8. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Packaging:  Ship insulation materials in containers marked by the insulation manufacturer with appropriate ASTM specification designation, type and grade, and maximum use temperature.

1.6 COORDINATION

A. Coordinate carefully with trades to ensure that the necessary clearance requirements are maintained for proper installation of the insulation.

1.7 SCHEDULING 

A. Installation of the insulation shall begin only after testing of the duct systems.  Insulation application may begin on segments of ducts that have satisfactory test results.

1.8 WARRANTY

A. Special Warranty:  The system herein specified shall be free from defects in workmanship and material under normal use and service.  If within [12] [24] [  ] months from the date of acceptance by the Owner/Architect, equipment or software herein described is proven to be defective in workmanship or material, it shall be adjusted, repaired, or replaced free of charge.  This system warranty shall also include each software program, upgrade and maintenance.

B. Warranty Period for <insert equipment name>:  [Two] <insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instructions in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other part 2 articles in which manufacturers are named.  See Division 1 Section “Product Requirements” for an explanation of the terms. “Available Manufacturers,” and “Manufacturers,” and the effect these terms have on “Comparable Product” and “Product Substitution” requirements.

A. Available Manufacturers:  Subject to compliance with these specifications, manufacturers offering products that may be incorporated into the Work include, but are not limited to, those listed below:

B. Manufacturers:  Subject to compliance with these specifications, provide products by one of the following:

1. Mineral Fiber Insulation:

a. CertainTeed Manson.

b. Knauf FiberGlass GmbH.

c. Owens-Corning Fiberglas Corp.

d. Schuller International, Inc.

e. <Insert manufacturer's name.>
f. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

2. Flexible Elastomeric Thermal Insulation:

a. Armstrong World Industries, Inc.

b. Rubatex Corp.

c. <Insert manufacturer's name.>
d. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

3. Closed-Cell Phenolic-Foam Insulation:

a. Kooltherm Insulation Products, Ltd.

b. <Insert manufacturer's name.>
c. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

4. Calcium Silicate Insulation:

a. Owens-Corning Fiberglas Corp.

b. Pabco.

c. Schuller International, Inc.

d. <Insert manufacturer's name.>
e. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

Most ducts are constructed in fabrication shops and often assembled on site.  Some manufactured products are available; listing these may increase quality control of Product.

2.2 INSULATION MATERIALS

A. Mineral Fiber Board Thermal Insulation:  Insulation shall consist of glass fibers bonded with a thermosetting resin.  Insulation shall comply with ASTM C 612, Type IB, without facing and with all-service type jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

B. Mineral Fiber Blanket Thermal Insulation:  Insulation shall consist of glass fibers bonded with a thermosetting resin.  Insulation shall comply with ASTM C 553, Type II, without facing and with all-service jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

C. Flexible Elastomeric Thermal Insulation:  Insulation shall consist of closed-cell, sponge or expanded rubber materials.  Insulation shall comply with ASTM C 534, Type II for sheet materials.

Coordinate first subparagraph and list below with Part 2 “Manufacturers” article.  Retain “Available” for nonproprietary and delete for semi-proprietary specifications.

1. Adhesive:  Adhesive shall be as recommended by the insulation material manufacturer and as approved by the Government.

2. Ultraviolet Protective Coating:  Coating shall be as recommended by the insulation manufacturer and as approved by the Government. 

D. Closed-Cell Phenolic Foam Insulation:  Block type insulation composed of a rigid, expanded, closed-cell structure.  Insulation shall comply with ASTM C 1126, Type II, Grade 1.

E. Calcium Silicate Insulation:  Insulation shall be configured in flat, curved, and/or grooved block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement.  Insulation shall comply with ASTM C 533, Type I.

2.3 FIELD APPLIED JACKETS

A. General:  Jackets shall comply with ASTM C 921, Type 1, unless otherwise indicated.

B. Foil and Paper Jacket:  Jacket shall consist of laminated, glass-fiber-reinforced, flame-retardant kraft paper and aluminum foil.

C. PVC Jacket:  Jacket shall consist of high impact, ultraviolet-resistant PVC; [0.5 mm (20 mils)] thick; roll stock ready for shop or field cutting and forming.

1. PVC Jacket Color:  Custom color selected by the Government.

D. Aluminum Jacket:  Jacket shall consist of deep corrugated sheets manufactured from aluminum alloy complying with ASTM B 209M (ASTM B 209), and shall have an integrally bonded moisture barrier over the entire surface in contact with the insulation.  Metal thickness and corrugation dimensions are scheduled at the end of this Section.

1. [Finish:  Smooth finish.]
2. [Finish:  Cross-crimp corrugated finish.]
3. [Finish:  Stucco-embossed finish.]
4. [Finish:  Factory-painted finish.]
5. Moisture Barrier:  Barrier shall be a minimum of 0.025 mm (1 mil) thick, heat-bonded polyethylene and kraft paper.

E. Stainless-Steel Jacket:  Jacket shall consist of deep corrugated sheets of stainless steel complying with ASTM A 666, Type 304 or 316; 2.5 mm (0.10 inch) thick; and be in roll stock configuration, ready for shop or field cutting and forming to the indicated sizes.

1. [Moisture Barrier:  0.025 mm (1 mil) thick, heat-bonded polyethylene and kraft paper.]

2. [Moisture Barrier:  0.075-mm (3 mil) thick, heat-bonded polyethylene and kraft paper.]

3. Jacket Bands:  Bands shall be stainless steel, Type 304, 19 mm (3/4 inch) wide.

2.4 ACCESSORIES AND ATTACHMENTS

Verify attachment selection and spacing with structural engineer.

A. Glass Cloth and Tape:  Cloth and tape shall comply with MIL-C-20079H, Type I for cloth and Type II for tape, respectively.  Woven glass-fiber fabrics shall be plain weave and pre-sized to a minimum of 270 g/sq. m (8 oz./sq. yd.).

1. Tape Width:  100 mm (4 inches).

B. Bands:  Provide 19 mm (3/4 inch) wide, in one of the following materials compatible with jacket:

1. Stainless Steel:  ASTM A 666, Type 304; 0.5 mm (0.020 inch) thick.

2. Galvanized Steel:  0.13 mm (0.005 inch) thick.

3. Aluminum:  0.18 mm (0.007 inch) thick.

4. Brass:  0.25 mm (0.010 inch) thick.

5. Nickel Copper Alloy:  0.13 mm (0.005 inch) thick.

C. Wire:  Wire shall be 2.0-mm (0.080-inch), nickel-copper alloy; 1.6-mm (0.062-inch), soft-annealed, stainless steel; or 1.6-mm (0.062-inch), soft-annealed, galvanized steel.

D. Weld-Attached Anchor Pins and Washers:  Pins and washers shall be a copper-coated steel pin for capacitor-discharge welding and galvanized speed washer, respectively.  Pin length shall be sufficient for insulation thickness indicated.

1. Welded Pin Holding Capacity:  45 kg (100 lb) for direct pull perpendicular to the attached surface.

E. Adhesive-Attached Anchor Pins and Speed Washers:  Pins and washers shall consist of a galvanized steel plate, pin, and washer manufactured for attachment to duct and plenum with adhesive.  Pin length shall be sufficient for the insulation thickness indicated.

1. Adhesive:  Adhesive shall be as recommended by the anchor pin manufacturer as appropriate for surface temperatures of ducts, plenums, and breechings; and to achieve a holding capacity of 45 kg (100 lb) for direct pull perpendicular to the adhered surface.

2. Trimming:  Excess pin lengths shall be field-cut so as not to present a hazard to installers or maintenance personnel.

F. Self-Adhesive Anchor Pins and Speed Washers:  Pins and washers shall consist of a galvanized steel plate, pin, and washer manufactured for attachment to a duct and/or plenum with adhesive.  Pin length shall be sufficient for the insulation thickness indicated.

1. Adhesive:  Adhesive shall be as recommended by the anchor pin manufacturer as appropriate for surface temperatures of ducts, plenums, and breechings; and to achieve a holding capacity of 45 kg (100 lb) for direct pull perpendicular to the adhered surface.

2. Trimming:  Excess pin lengths shall be field-cut so as not to present a hazard to installers or maintenance personnel.

2.5 VAPOR RETARDANTS

A. Mastics:  Mastic type materials shall be as recommended by the insulation material manufacturer and shall be compatible with the insulation materials, jackets, and substrates.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and field conditions for compliance with the insulation material manufacturers’ requirements for installation and other conditions affecting performance of the insulation application.

B. Proceed with the installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Surface Preparation:  Clean and dry surfaces scheduled or specified to receive insulation.  Remove materials that might adversely affect the insulation application.

3.3 GENERAL APPLICATION REQUIREMENTS

A. Prior to installation of insulation, all ductwork must be sealed as described in the requirements of Section 6, Heating, Ventilation, and Air Conditioning, of ASHRAE Standard 90.1, including the tables at the end of this section.

B. Apply insulation materials, accessories, and finishes in accordance with the manufacturer's written instruction.  Finished insulation surfaces shall be smooth, straight, and even surfaces, and free of voids throughout the entire length of the ducts and fittings.

C. Refer to the schedules at the end of this Section for materials, forms, jackets, and thickness of insulation required for each duct system.

D. Accessories shall be compatible with the insulation materials and suitable for the intended service.  Use accessories that will not corrode, soften, or otherwise attack the insulation or jacket in either a wet or a dry state.

E. Multiple layers of insulation shall be applied with lateral, longitudinal and end seams staggered.

F. Joints and seams shall be sealed with a vapor-retarding mastic on insulation indicated to have or receive a vapor retardant.

G. Keep insulation materials dry during application and finishing. Materials that show signs of having been wet, shall be replaced with materials at no additional cost to the Government.

H. Apply insulation with tight lateral and longitudinal seams and end joints.  Bond seams and joints with an adhesive recommended by the insulation material manufacturer.

I. Apply insulation with the least number of joints practical.

J. Apply insulation over fittings and specialties, with continuous thermal and vapor-retardants integrity, unless otherwise specifically indicated.

K. Hangers and Anchors:  

1. On ducts specified to have a vapor retardant barrier, the hangers shall be configured so the duct, insulation and vapor retardant barrier are supported by the hanger without interruption or penetration of the vapor retardant barrier.  Ducts indicated as not requiring vapor retardant barrier, which have hangers penetrating the insulation, the hangers shall be sealed with vapor retardant mastic.

2. Where anchors penetrate the insulation on ducts specified to have a vapor retardant barrier, the anchor material shall be insulated and sealed with vapor retardant mastic to a distance sufficient to prevent condensation.  On ducts not indicated as requiring a vapor retardant barrier, anchor penetration shall be sealed at the insulation surface with a vapor retardant mastic.

L. Insulation Terminations: For insulation applications where vapor retardants are indicated, seal ends with a compound recommended by the insulation material manufacturer to maintain the integrity of the vapor retardant.  Sealant characteristics and applications shall comply with the requirements of ASHRAE Standard 90.1.

M. Insulation that is subject to reduction in thermal resistivity if wetted shall be enclosed with a vapor seal such as a vapor barrier jacket. All insulation and vapor barrier jackets shall comply with the requirements of ASHRAE Standard 90.1, including related tables shown at the end of this section.  Insulation characteristics shall comply with all applicable requirements of ASHRAE Standard 90.1.

N. Provide vapor barrier jacket as described by the requirements of ASHRAE Standard 90.1.  Apply insulation with integral jackets as follows:

1. Placement:  pull jacket tight and smooth.

2. Joints and Seams:  Cover joints and seems with tape and vapor retardant as recommended by insulation material manufacturer to maintain a vapor seal.

3. Vapor Retarding Mastics:  Where vapor retardants are indicated, apply mastic on seams and joints and at the ends adjacent to duct flanges and fittings.

O. Cut insulation in accordance with the manufacturer's written instructions to prevent compressing the insulation to less than 75 percent of its nominal thickness.

P. Insulation that is subject to reduction in thermal resistivity if wetted shall be enclosed with a vapor seal such as a vapor barrier jacket.  Install vapor-retardant mastic on ducts and plenums scheduled to receive the vapor retardants.

1. Ducts with Vapor Retardants:  Overlap insulation facing at seams and seal with vapor retarding mastic and a pressure sensitive tape having the same facing as the insulation.  Repair punctures, tears, and penetrations with tape and/or mastic to maintain the vapor retardant seal.

2. Ducts without Vapor Retardants:  Overlap insulation facing at seams and secure with outward clinching staples and pressure-sensitive tape having the same facing as the insulation.

Q. Roof Penetrations:  Apply insulation for interior applications to a point even with the top of the roof flashing.

1. Seal penetrations with vapor-retardant mastic.

2. Apply insulation appropriate for exterior applications tightly joined to the interior insulation ends.

3. Seal insulation to roof flashing with exterior-type vapor-retarding mastic.

R. Interior Wall and Partition Penetrations:  Apply insulation continuously through walls and partitions, except fire-rated walls and partitions.  Ducts and insulation shall pass uninterrupted through prepared openings in interior walls and partitions.  Refer to Section “Metal Ducts” for specifications on prepared openings.

S. Fire-Rated Wall and Partition Penetrations:  See Duct insulation terminating at fire dampers, shall be continuous over the damper collar and retaining angle of fire dampers, which are exposed to unconditional air and which may be prone to condensate formation.  Vapor retardant materials shall be applied to form a complete unbroken vapor seal over the insulation.

T. Floor Penetrations:  Terminate insulation at underside of floor assembly and at floor support at top of floor.

1. For insulation indicated to have vapor retardants, taper termination and seal insulation ends with vapor-retarding mastic.

U. Air Distribution Devices:  Duct insulation and vapor retardant shall cover the collar, neck and uninsulated surfaces of diffusers, registers and grills.  See Duct insulation terminating at fire dampers, shall be continuous over the damper collar and retaining angle of fire dampers, which are exposed to unconditional air and which may be prone to condensate formation.  

V. Metal ducts with duct liner:  Duct liner permitted only at ductwork to and from courtrooms, judges chambers, jury rooms, prisoner consulting rooms, and prisoner detention areas and only if required for acoustic purposes.  Materials used for internal insulation exposed to the air stream in ducts shall be in accordance with UL 181 or ASTM C 1071 erosion tests, and shall not promote or support the growth of fungi or bacteria, in accordance with UL 181 and ASTM G21 and G22.

3.4 MINERAL-FIBER INSULATION APPLICATION

A. Blanket Applications for Ducts and Plenums:  Blanket insulation shall be secured with adhesive, and anchor pins with speed washers in accordance with the following:

1. Apply adhesives according to the manufacturer's recommended coverage rates per square foot, to attain 100 percent coverage of duct and plenum surfaces.

2. Apply adhesive to entire circumference of ducts and to surfaces of fittings and transitions.

3. Install anchor pins and speed washers on sides and bottom of horizontal ducts and sides of vertical ducts as follows:

a. On duct sides with dimensions 450 mm (18 inches) and smaller, along longitudinal centerline of duct.  Space 75 mm (3 inches) maximum from insulation end joints, and 400 mm (16 inches) o.c.

b. On duct sides with dimensions larger than 450 mm (18 inches).  Space 400 mm (16 inches) o.c. each way, and 75 mm (3 inches) maximum from insulation joints.  Apply additional pins and clips to hold insulation tightly against surface at cross bracing.

c. Anchor pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

d. Do not over compress insulation during installation of speed washers.

4. Impale insulation over anchors and attach speed washers.

5. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface.  Cover exposed pins and washers with tape matching insulation facing.

6. Create a facing lap for longitudinal seams and end joints with insulation by removing 50 mm (2 inches) from one edge and one end of insulation segment.  Secure laps to adjacent insulation segment with 13 mm (1/2 inch) outward clinching staples, 25 mm (1 inch) o.c., and cover with pressure-sensitive tape having same facing as insulation.

7. Overlap unfaced blankets a minimum of 50 mm (2 inches) on longitudinal seams and end joints.  Secure with steel band at end joints and spaced a maximum of 450 mm (18 inches) o.c.

8. Apply insulation on rectangular duct elbows and transitions with a full insulation segment for each surface.  Apply insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

9. Insulate duct stiffeners, hangers, and flanges that protrude beyond the insulation surface with 150 mm (6 inch) wide strips of the same material used to insulate duct.  Secure on alternating sides of stiffener, hanger, and flange with anchor pins spaced 150 mm (6 inches) o.c.

10. Apply vapor-retarding mastic to open joints, breaks, and punctures for insulation indicated to receive a vapor retardant.

B. Board Applications for Ducts and Plenums:  Board insulation shall be secured with adhesive and anchor pins and speed washers in accordance with the following:

1. Apply adhesives according to the manufacturer's recommended coverage rates per square foot, to attain 100 percent coverage of duct and plenum surfaces.

2. Apply adhesive to entire circumference of ducts and to surfaces of fittings and transitions.

3. Space anchor pins as follows:

a. On duct sides with dimensions 450 mm (18 inches) and smaller, along longitudinal centerline of duct.  Space 75 mm (3 inches) maximum from insulation end joints, and 400 mm (16 inches) o.c.

b. On duct sides with dimensions larger than 450 mm (18 inches).  Space 400 mm (16 inches) o.c. each way, and 75 mm (3 inches) maximum from insulation joints. Apply additional pins and clips to hold insulation tightly against surface at cross bracing.

c. Anchor pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

d. Do not over compress insulation during installation of speed washers.

4. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface.  Cover exposed pins and washers with tape matching insulation facing.

5. Create a facing lap for longitudinal seams and end joints with insulation by removing 50 mm (2 inches) from one edge and one end of insulation segment.  Secure laps to adjacent insulation segment with 13 mm (1/2 inch) outward clinching staples, 25 mm (1inch) o.c., and cover with pressure-sensitive tape having same facing as insulation.

6. Apply insulation on rectangular duct elbows and transitions with a full insulation segment for each surface.  Groove and score insulation to fit as closely as possible to outside and inside radius of elbows.  Apply insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

7. Insulate duct stiffeners, hangers, and flanges that protrude beyond the insulation surface with 150 mm (6 inch) wide strips of the same material used to insulate duct.  Secure on alternating sides of stiffener, hanger, and flange with anchor pins spaced 150 mm (6 inches) o.c.

8. Apply vapor retarding mastic to open joints, breaks, and punctures for insulation indicated to receive vapor retardant.

3.5 FLEXIBLE ELASTOMERIC THERMAL INSULATION APPLICATION

A. Apply insulation to ducts and plenums as follows:

1. Follow the manufacturer's written instructions for applying insulation.

2. Seal longitudinal seams and end joints with manufacturer's recommended adhesive.  Apply cement in a manner to prevent openings in the insulation that might allow passage of air to the duct and plenum surfaces.

3.6 CLOSED-CELL PHENOLIC-FOAM INSULATION APPLICATION

A. Apply insulation as follows:

1. Secure each layer of insulation to the duct with stainless-steel bands at 300 mm (12 inch) intervals and tighten without deforming the insulation materials.

2. Apply two-layer insulation with joints tightly butted and staggered at least 75 mm (3 inches).  Secure inner layer with 1.6 mm (0.062 inch), soft-annealed, stainless steel wire spaced at 300 mm (12 inch) intervals.  Secure outer layer with stainless-steel bands at 300 mm (12 inch) intervals.

3. On exposed applications, finish insulation with a skim coat of mineral-fiber, hydraulic-setting cement to surface of installed insulation.  When dry, apply flood coat of lagging adhesive and press on one layer of glass cloth or tape.  Overlap edges at least 25 mm (1 inch).  Apply finish coat of lagging adhesive over glass cloth or tape.  Thin the finish coat to achieve a smooth finish.

3.7 CALCIUM SILICATE INSULATION APPLICATION

A. Apply insulation according to the manufacturer's written instructions and as follows:

1. Secure single layer of insulation to duct with stainless-steel bands.  Tighten bands without deforming the insulation material.

2. Apply two-layer insulation with joints tightly butted and staggered at least 75 mm (3 inches).  Secure inner layer with 1.6 mm (0.062 inch), soft-annealed, stainless steel wire.  Secure outer layer with stainless steel bands.

3. On exposed applications, without metal jacket, finish insulation with a skim coat of mineral fiber, hydraulic-setting cement to surface of installed insulation.  When dry, apply flood coat of lagging adhesive and press on one layer of glass cloth or tape.  Overlap edges at least 25 mm (1 inch).  Apply finish coat of lagging adhesive over glass cloth or tape.  Thin the finish coat to achieve smooth finish.

3.8 FIELD APPLIED JACKET APPLICATION

A. Apply glass cloth jacket, where indicated, directly over bare insulation or insulation with factory-applied jackets.

1. Apply jacket smooth and tight to surface with 50 mm (2 inch) overlap at seams and joints.

2. Embed glass cloth between two 1.6 mm (0.062 inch) thick coats of jacket manufacturer's recommended adhesive.

3. Completely encapsulate insulation with jacket, leaving no exposed raw insulation.

3.9 FINISHES

A. Glass Cloth Jacketed Insulation:  Paint insulation finished with glass-cloth jacket as specified in Division 9 Section "Painting."

B. Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

C. Color:  Final color shall be as selected by the Government.  Vary the color or the first and second coats to allow visual inspection of the completed Work.

3.10 DUCT SYSTEM APPLICATIONS

A. Insulation materials and thickness are specified in schedules at the end of this Section.

B. Insulate the following plenums and duct systems:

1. Indoor concealed supply, return, and outside air ductwork.

2. Indoor exposed supply, return, and outside air ductwork.

3. Outdoor exposed supply and return ductwork.

4. [Indoor exposed range-hood exhaust ductwork.]
5. Indoor concealed range-hood exhaust ductwork.

6. [Indoor exposed oven and dishwasher exhaust ductwork.]
7. Indoor concealed oven and dishwasher ductwork.

C. Items Not Insulated:  Unless otherwise indicated, do not apply insulation to the following systems, materials, and equipment:

1. Fibrous glass ducts.

2. Metal ducts with duct liner.  [Duct liner permitted only at ductwork to and from courtrooms, judges chambers, jury rooms, prisoner consulting rooms, and prisoner detention areas and only if required for acoustic purposes.]  Materials used for internal insulation exposed to the air stream in ducts shall be in accordance with UL 181 or ASTM C 1071 erosion tests, and shall not promote or support the growth of fungi or bacteria, in accordance with UL 181 and ASTM G21 and G22.

3. Factory insulated flexible ducts.

4. Factory insulated plenums, casings, terminal boxes, and filter boxes and sections.

5. Flexible connectors.

6. Vibration control devices.

7. Testing agency labels and stamps.

8. Nameplates and data plates.

9. Factory insulated access panels and doors in air distribution systems.

3.11 INDOOR DUCT AND PLENUM APPLICATION SCHEDULE

A. Service:  Round, supply air ducts, concealed.

1. Material:  [Mineral-fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed-cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

B. Service:  Round, return-air ducts, concealed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

C. Service:  Round, outside-air ducts, concealed.

1. Material:  [Mineral-fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed-cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

D. Service:  Rectangular, supply-air ducts, concealed.

1. Material:  [Mineral fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

E. Service:  Rectangular, return-air ducts, concealed.

1. Material:  [Mineral-fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

F. Service:  Rectangular, outside air ducts, concealed.

1. Material:  [Mineral-fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

G. Service:  Round, supply-air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

H. Service:  Round, return-air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral-fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

I. Service:  Round, outside air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

J. Service:  Rectangular, supply-air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

K. Service:  Rectangular, return air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

L. Service:  Rectangular, outside air ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field-Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

M. Service:  Rectangular, range hood exhaust ducts, concealed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

N. Service:  Rectangular, range hood exhaust ducts, exposed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

O. Service:  Rectangular, dishwasher exhaust ducts, concealed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

P. Service:  Rectangular, dishwasher exhaust ducts, exposed.

1. Material:  [Mineral fiber board] [Mineral fiber blanket] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. Field Applied Jacket:  [Glass cloth] [Foil and paper] [PVC].

5. Vapor Retardant Required:  [Yes] [No].

3.12 OUTDOOR DUCT AND PLENUM APPLICATION SCHEDULE

A. Service:  Round, supply air ducts.

1. Material:  [Mineral fiber board] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]
5. [Field Applied Jacket:  Foil and paper.]
6. [Field Applied Jacket:  PVC.]
7. [Field Applied Jacket:  Aluminum.]
a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]
a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

B. Service:  Round, return air ducts.

1. Material:  [Mineral fiber board] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]
5. [Field Applied Jacket:  Foil and paper.]
6. [Field Applied Jacket:  PVC.]
7. [Field Applied Jacket:  Aluminum.]
a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

C. Service:  Rectangular, supply air ducts.

1. Material:  [Mineral fiber board] [Flexible elastomeric] [Closed cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

D. Service:  Rectangular, return air ducts.

1. Material:  [Mineral fiber board] [Flexible elastomeric] [Closed-cell phenolic foam].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

3.13 BOILER BREECHING AND CONNECTOR APPLICATION SCHEDULE

A. Service:  Round, exposed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

6. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

7. Vapor Retardant Required:  [Yes] [No].

B. Service:  Round, concealed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

6. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

7. Vapor Retardant Required:  [Yes] [No].

C. Service:  Rectangular, exposed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

6. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

7. Vapor Retardant Required:  [Yes] [No].

D. Service:  Rectangular, concealed.

1. Material:  [Mineral fiber board] [Calcium silicate].

2. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)] [50 mm (2 inches)].

3. Number of Layers:  [One] [Two].

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

6. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

7. Vapor Retardant Required:  [Yes] [No].

END OF SECTION 15081

DUCT INSULATION
15081 - 21

