Copyright 1997 AIA
GSA VERSION MASTERSPEC(
6/97 (GSA 03/03)


Copyright 1997 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.
SECTION 15082 - EQUIPMENT INSULATION
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings, and the general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes blanket, board, and block insulation; insulating cements; field-applied jackets; accessories and attachments; and sealing compounds.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Duct Insulation" for insulation materials and application for ductwork.

2. Division 15 Section "Pipe Insulation" for insulation for piping systems.

3. Division 15 Section “Basic Materials and Methods” for additional material specifications.

1.3 DEFINITIONS

A. k:
Thousand (1000) units

B. M:
Million (1,000,000) units

1.4 SUBMITTALS

A. Product Data:  Identify thermal conductivity, thickness, and jackets (both factory and field applied, if any), for each type of product indicated.

B. Shop Drawings:  Show fabrication and installation details for the following:

1. Field application for each equipment type.

2. Removable insulation sections at access panels.

3. Application of field-applied jackets.

4. Special shapes for cellular-glass insulation.

C. Samples:  Provide samples for each type of insulation and field-applied jacket.  Identify each Sample, describing product and intended use.  Submit 300-mm- (12-inch-)  square sections of each sample material.

1. Manufacturer's Color Charts:  Show the full range of colors available for each type of field-applied finish material indicated.

Surface-burning characteristics specified in "Quality Assurance" Article should be verified by an independent testing agency.  Where critical, require test report Submittals.  Delete test reports below if not required.

D. Material Test Reports:  Submit data from a qualified testing agency acceptable to the authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealants, attachments, cements, and jackets with requirements indicated in Section 6 - Heating, Ventilating, and Air Conditioning, Section 7 - Service Water Heating, of ASHRAE/IESNA Standard 90.1, including related tables shown at the end of this section.  Include dates of tests.  Include dates of tests.

Retain below if "Installer Qualifications" Paragraph is retained in "Quality Assurance" Article.

E. Installer Certificates:  Submit a letter signed by the Contractor certifying that the installers and materials comply with these specifications.

F. Warranty: 

1. Submit a sample of the warranty that will be signed by the Contractor certifying that the installation and materials comply with the requirements of this and other applicable specifications. 

2. Submit special warranty as specified in this section.
1.5 QUALITY ASSURANCE

Delete paragraph below if not required or available at Project location.  Apprenticeship programs are usually associated with union shops.  Other craft training programs are available.

A. ASHRAE/IESNA Compliance:
All insulation characteristics shall comply with the requirements of ASHRAE Standard 90.1, including related tables contained therein.  Insulation characteristics shall comply with applicable requirements of ASHRAE Standard 90.1. Supply ductwork with the exception of buried ductwork and ductwork located in indirectly conditioned spaces shall be insulated in accordance with ASHRAE Standard 90.1. Supply duct insulation shall have a vapor barrier jacket.  The vapor barrier jacket shall cover the duct system with a continuous, unbroken vapor seal.  Return and exhaust air distribution systems shall be insulated in accordance with ASHRAE Standard 90.1. 

B. Code of Federal Regulations Compliance: Insulation characteristics shall comply with the requirements of the Code of Federal Regulations 10 CFR-435.107 including related tables shown therein and shown at the end of this section.

C. General Services Administration (GSA) Compliance: Insulation characteristics shall comply with the requirements of the Codes and Standards published in the GSA document Facilities Standards for the Public Buildings including related tables shown therein and at the end of this section.

D. General Compliance:
Where the requirements for a description of insulation characteristics or performance ratings defined in a publication or standard referenced herein conflict, the most restrictive shall apply.

E. Installer Qualifications: Insulation shall be installed by skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the U.S. Department of Labor, Bureau of Apprenticeship and Training.

F. Fire Test Response Characteristics: As determined by testing materials identical to those specified in this Section according to ASTM E 84, NFPA 255 and UL 723 by a testing and inspecting agency acceptable to authorities having jurisdiction.  Accessories such as adhesives, mastics, cements, tapes, etc., shall have the same or better fire and smoke hazard ratings as that identified for the insulation materials.

1. Insulation Installed Indoors:  Flame spread rating of 25 or less, and smoke developed rating of 50 or less.

2. Insulation Installed Outdoors:  Flame spread rating of 75 or less, and smoke developed rating of 150 or less.

Delete paragraph below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserting specific information in paragraph and subparagraphs below.  Revise wording if only one mockup is required.

G. Mockups:  Before beginning the actual installation of the insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes.  Mockups shall be located and displayed at the project site until directed otherwise by the Government.  Build mockups according to the following requirements, using materials indicated for the completed Work:

1. Include the following mockups:

a. One chilled-water centrifugal pump.

b. One small tank or vessel.

2. Mockups shall be built with cutaway sections to allow observation of application details for insulation materials, mastics, attachments, and jackets.

3. Build mockups in the location indicated or, if not indicated, as directed by the Government.

4. Notify the Government seven days in advance of the dates and times when   mockups will be constructed.

5. Obtain Government's approval of mockups before starting insulation application.

6. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

7. Mockups shall remain the property of the Contractor but shall only be removed from the project site when directed by the Government.

Delete subparagraph above or below.  Below is applicable only if mockups are erected as part of building rather than separately.

8. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

H.
Mineral Fiber insulation shall not be installed at an equipment application involving liquid carriers such as piping, coils, tanks and liquid related accessories and appurtenances.  

1.6 DELIVERY, STORAGE, AND HANDLING

Container marking is an option in ASTM standards; the default condition does not include the marking below unless specified in the Contract.

A. Packaging:  Ship insulation materials in containers marked by the insulation manufacturer with appropriate ASTM specification designation, type and grade, and maximum use temperature.

1.7 COORDINATION

A. Coordinate carefully with   trades to ensure that the necessary clearance requirements are maintained for proper installation of the insulation.

1.8 SCHEDULING 

A. Installation of the insulation shall begin only after testing of the duct systems.  Insulation application may begin on segments of ducts that have satisfactory test results.

1.9 WARRANTY

A. Special Warranty:  The system herein specified shall be free from defects in workmanship and material under normal use and service.  If within [12] [24] <insert number> months from the date of acceptance by the Owner/Architect, equipment or software herein described is proven to be defective in workmanship or material, it shall be adjusted, repaired, or replaced free of charge.  This system warranty shall also include each software program, upgrade and maintenance.

B. Warranty Period for <insert equipment name>:  [Two] <insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with these specifications, manufacturers offering products that may be incorporated into the Work include, but are not limited to, those listed below:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with these specifications, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Mineral Fiber Insulation:

a. CertainTeed Manson.

b. Knauf FiberGlass GmbH.

c. Owens-Corning Fiberglas Corp.

d. Schuller International, Inc.

e. <Insert manufacturer's name.>

f. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

2. Cellular Glass Insulation:

a. Pittsburgh-Corning Corp.

b. <Insert manufacturer's name.>

c. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

3. Flexible Elastomeric Thermal Insulation:

a. Armstrong World Industries, Inc.

b. Rubatex Corp.

c. <Insert manufacturer's name.>

d. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

4. Closed Cell Phenolic Foam Insulation:

a. Kooltherm Insulation Products, Ltd.

b. <Insert manufacturer's name.>

c. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

5. Calcium Silicate Insulation:

a. Owens-Corning Fiberglas Corp.

b. Pabco.

c. Schuller International, Inc.

d. <Insert manufacturer's name.>

e. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

2.2 INSULATION MATERIALS

For operating temperatures higher than 850 deg F (454 deg C), change insulation below to ASTM C 612, Type III.

A. Mineral Fiber Board Thermal Insulation:  Insulation shall consist of glass fibers bonded with a thermosetting resin.  Insulation shall comply with ASTM C 612, Type IB, without facing and with all-service type jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

B. Mineral Fiber Blanket Thermal Insulation:  Insulation shall consist of glass fibers bonded with a thermosetting resin.  Insulation shall comply with ASTM C 553, Type II, without facing and with all-service jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

C. Cellular Glass Insulation:  Insulation shall consist of inorganic, foamed or cellulated glass, and annealed, rigid, hermetically sealed cells that are totally incombustible.  Insulation shall comply with the following:

If retaining more than one type of insulation below, indicate where each type applies in one of the insulation application schedules at the end of this Section.

1. Block Insulation:  ASTM C 552, Type I.

2. Special-Shaped Insulation:  ASTM C 552, Type III.

3. Board Insulation:  ASTM C 552, Type IV.

Flexible elastomeric thermal insulation is not suitable for temperatures lower than minus 70 deg F (minus 57 deg C) and higher than 220 deg F (104 deg C).

D. Flexible Elastomeric Thermal Insulation:  Insulation shall consist of closed-cell, sponge or expanded rubber materials.  Insulation shall comply with ASTM C 534, Type II for sheet materials.

1. Adhesive:  Adhesive shall be as recommended by the insulation material manufacturer and as approved by the Government.

2. Ultraviolet Protective Coating:  Coating shall be as recommended by the insulation manufacturer and as approved by the Government. 

Closed-cell phenolic-foam insulation is available in Grades 1 and 2.  Grade 1 has a lower thermal conductivity than Grade 2.

E. Closed Cell Phenolic Foam Insulation:  Block type insulation composed of a rigid, expanded, closed cell structure.  Insulation shall comply with ASTM C 1126, Type II, Grade 1.

F. Calcium Silicate Insulation:  Insulation shall be configured in flat, curved, and/or grooved block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement.  Insulation shall comply with ASTM C 533, Type I.

2.3 FIELD-APPLIED JACKETS

Insulation jackets below are for field applications.  Delete below if jackets are factory applied.  ASTM C 921, Type 1, is for use over insulation on ducts operating below ambient temperatures at least part of the time or for where a vapor retarder is required.  ASTM C 921, Type II, is for use over insulation on ducts operating above ambient temperatures or for where a vapor retarder is not required.

A. General:  Jackets shall comply with ASTM C 921, Type 1, unless otherwise indicated.

B. Foil and Paper Jacket:  Jacket shall consist of laminated, glass fiber reinforced, flame retardant kraft paper and aluminum foil.

C. PVC Jacket:  Jacket shall consist of high-impact, ultraviolet-resistant PVC; 0.5 mm (20 mils) thick; roll stock ready for shop or field cutting and forming.

1. PVC Jacket Color:  Custom color selected by the Government.

D. Aluminum Jacket:  Jacket shall consist of deep corrugated sheets manufactured from aluminum alloy complying with ASTM B 209M (ASTM B 209), and shall have an integrally bonded moisture barrier over the entire surface in contact with the insulation.  Metal thickness and corrugation dimensions are scheduled at the end of this Section.

1. [Finish:  Smooth finish.]

2. [Finish:  Cross-crimp corrugated finish.]

3. [Finish:  Stucco embossed finish.]

4. [Finish:  Factory painted finish.]

5. Moisture Barrier:  Barrier shall be a minimum of 0.025 mm (1 mil) thick, heat bonded polyethylene and kraft paper.

E. Stainless Steel Jacket:  Jacket shall consist of deep corrugated sheets of stainless steel complying with ASTM A 666, Type 304 or 316; 2.5 mm (0.10 inch) thick; and be in roll stock configuration, ready for shop or field cutting and forming to the indicated sizes.

1. [Moisture Barrier:  0.025 mm (1 mil) thick, heat-bonded polyethylene and kraft paper.]

2. [Moisture Barrier:  0.075 mm (3 mil) thick, heat bonded polyethylene and kraft paper.]
3. Jacket Bands:  Bands shall be stainless steel, Type 304, 19 mm (3/4 inch) wide.

2.4 ACCESSORIES AND ATTACHMENTS

A. Glass Cloth and Tape:  Cloth and tape shall comply with MIL-C-20079H, Type I for cloth and Type II for tape, respectively.  Woven glass-fiber fabrics shall be plain weave and pre-sized to a minimum of 270 g/sq. m (8 oz./sq. yd.).

1. Tape Width:  100 mm (4 inches).

B. Bands:  Provide 19 mm (3/4 inch) wide, in one of the following materials compatible with jacket:

1. Stainless Steel:  ASTM A 666, Type 304; 0.5 mm (0.020 inch) thick.

2. Galvanized Steel:  0.13 mm (0.005 inch) thick.

3. Aluminum:  0.18 mm (0.007 inch) thick.

4. Brass:  0.25 mm (0.010 inch) thick.

5. Nickel-Copper Alloy:  0.13 mm (0.005 inch) thick.

C. Wire:  Wire shall be 2.0-mm (0.080-inch), nickel-copper alloy; 1.6-mm (0.062-inch), soft-annealed, stainless steel; or 1.6-mm (0.062-inch), soft-annealed, galvanized steel.

D. Weld-Attached Anchor Pins and Washers:  Pins and washers shall be a copper-coated steel pin for capacitor-discharge welding and galvanized speed washer, respectively.  Pin length shall be sufficient for insulation thickness indicated.

1. Welded Pin Holding Capacity:  45 kg (100 lb) for direct pull perpendicular to the attached surface.

E. Adhesive-Attached Anchor Pins and Speed Washers:  Pins and washers shall consist of a galvanized steel plate, pin, and washer manufactured for attachment to duct and plenum with adhesive.  Pin length shall be sufficient for the insulation thickness indicated.

1. Adhesive:  Adhesive shall be as recommended by the anchor pin manufacturer as appropriate for surface temperatures of ducts, plenums, and breechings; and to achieve a holding capacity of 45 kg (100 lb) for direct pull perpendicular to the adhered surface.

2. Trimming:  Excess pin lengths shall be field-cut so as not to present a hazard to installers or maintenance personnel.

F. Self-Adhesive Anchor Pins and Speed Washers:  Pins and washers shall consist of a galvanized steel plate, pin, and washer manufactured for attachment to a duct and/or plenum with adhesive.  Pin length shall be sufficient for the insulation thickness indicated.

1. Adhesive:  Adhesive shall be as recommended by the anchor pin manufacturer as appropriate for surface temperatures of ducts, plenums, and breechings; and to achieve a holding capacity of 45 kg (100 lb) for direct pull perpendicular to the adhered surface.

2. Trimming:  Excess pin lengths shall be field cut so as not to present a hazard to installers or maintenance personnel.

2.5 VAPOR RETARDANTS

Products with a perm rating of 1.0 are considered vapor retarders.  Ambient conditions and operating temperatures must be considered when selecting a vapor retarder.

A. Mastics:  Mastic type materials shall be as recommended by the insulation material manufacturer and shall be compatible with the insulation materials, jackets, and substrates.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and field conditions for compliance with the insulation material manufacturers’ requirements for installation and other conditions affecting performance of the insulation application.

B. Proceed with the installation only after  unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Surface Preparation:  Clean and dry surfaces scheduled or specified to receive insulation.  Remove materials that might adversely affect the insulation application.

3.3 GENERAL APPLICATION REQUIREMENTS

A. Apply insulation materials, accessories, and finishes in accordance with the manufacturer's written instruction.  Finished insulation surfaces shall be smooth, straight, and even surfaces; and free of voids throughout the entire length of the ducts and fittings.

B. Refer to the schedules at the end of this Section for materials, forms, jackets, and thickness of insulation required for each duct system.

C. Accessories shall be compatible with the insulation materials and suitable for the intended service.  Use accessories that will not corrode, soften, or otherwise attack the insulation or jacket in either a wet or a dry state.

D. Multiple layers of insulation shall be applied with lateral, longitudinal and end seams staggered.

E. Joints and seams shall be sealed with vapor-retarding mastic on insulation indicated to have or receive a vapor retardant.

F. Keep insulation materials dry during application and finishing.  Materials that show signs of having been wet, shall be replaced with materials at no additional cost to the Government.

G. Apply insulation with tight lateral and longitudinal seams and end joints.  Bond seams and joints with an adhesive recommended by the insulation material manufacturer.

H. Apply insulation with the least number of joints practical.

I. Apply insulation over fittings and specialties, with continuous thermal and vapor retardants integrity, unless otherwise specifically indicated.

J. Hangers and Anchors:  

1. On equipment specified to have a vapor retardant barrier, hangers and supports shall be configured so the equipment, insulation and vapor retardant barrier are not penetrated by the hanger or support.  Equipment indicated as not requiring vapor retardant barrier, which have hangers or supports penetrating the insulation, the hangers or supports shall be sealed with a vapor retardant mastic.

2. Where anchors penetrate the insulation at equipment specified to have a vapor retardant barrier, the anchor material shall be insulated and sealed with a vapor retardant mastic to a distance sufficient to prevent condensation.  On equipment not indicated as requiring a vapor retardant barrier, anchor penetration shall be sealed at the insulation surface with a vapor retardant mastic.

K. Insulation Terminations: For insulation applications where vapor retardants are indicated, seal ends with a compound recommended by the insulation material manufacturer to maintain the integrity of the vapor retardant.  Sealant characteristics and applications shall comply with the requirements of ASHRAE Standard 90.1.

L. Insulation that is subject to reduction in thermal resistivity if wetted shall be enclosed with a vapor seal such as a vapor barrier jacket.  Insulation and vapor barrier jackets shall comply with the requirements of ASHRAE Standard 90.1, including related tables shown at the end of this section.  Insulation characteristics shall comply with applicable requirements of ASHRAE Standard 90.1.

M. Provide vapor barrier jacket as described by the requirements of ASHRAE Standard 90.1.  Apply insulation with integral jackets as follows:

1. Placement:  pull jacket tight and smooth.

2. Joints and Seams:  Cover joints and seems with tape and vapor retardant as recommended by insulation material manufacturer to maintain a vapor seal.

3. Vapor-Retarding Mastics:  Where vapor retardants are indicated, apply mastic on seams and joints and at the ends adjacent to duct flanges and fittings.

N. Cut insulation in accordance with the manufacturer's written instructions to prevent compressing the insulation to less than 75 percent of its nominal thickness.

O. Install vapor retarding mastic on equipment scheduled to receive vapor retardants.  Overlap insulation facing at seams and seal with an approved vapor-retarding mastic and a pressure-sensitive tape having the same facing as the insulation.  Repair punctures, tears, and penetrations with tape or mastic to maintain a continuous vapor retarding seal.

Edit lists below to suit Project.

P. Insulate the following indoor equipment:

1. Chilled water air separators.

2. Chilled water compression tanks.

3. Chilled water centrifugal pump housings.

4. Aboveground, thermal (ice) storage tanks that are not factory insulated.

5. Low temperature brine tanks.

6. Domestic hot water storage tanks that are not factory insulated.

7. Heating water air separators.

8. Heating water compression tanks.

9. Hot water centrifugal pump housings.

10. Heating water heat exchangers.

11. Steam-to-heating or domestic water converters that are not factory insulated.

12. Condensate receivers that are not factory insulated.

13. Deaerators that are not factory insulated.

Q. Insulate the following outdoor equipment:

1. Aboveground domestic and/or water storage tanks.

2. Aboveground fuel storage tanks.

R. Omit insulation from the following:

1. Vibration control devices.

2. Testing agency and warning labels and stamps.

3. Nameplates and data plates.

4. Manholes.

5. Handholes.

6. Cleanouts.

S. Provide temporarily removable and resealing portions of insulation at the following:

1. Grease ports.

2. Oil Ports.

3. Access doors.

4. Parts of equipment requiring service or maintenance.

3.4 INDOOR TANK AND VESSEL INSULATION APPLICATION

A. Blankets, Board, and Block Applications for Tanks and Vessels:  Insulation shall be secured with adhesive and anchor pins and speed washers in accordance with the following:

1. Apply adhesives according to the manufacturer's recommended coverage rates per square foot, to attain 100 percent coverage of tank and vessel surfaces.

2. Groove and score insulation materials to fit as closely as possible to the equipment, including contours.  Bevel insulation edges for cylindrical surfaces for tight joint.  Stagger lateral, longitudinal and end joints.

3. Protect exposed corners with secured corner angles.

4. Install adhesive attached or self-adhesive anchor pins and speed washers on sides of tanks and vessels as follows:

a. Do not weld anchor pins to ASME-labeled pressure vessels.

b. On tank and vessel, 75 mm (3 inches) maximum from insulation end joints, and 400 mm (16 inches) o.c. in both directions.

c. Do not over compress insulation during installation.

d. Cut and miter insulation segments to fit curved sides and dome heads of tanks and vessels.

5. Impale insulation over anchor pins and attach speed washers.

6. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface.  Cover exposed pins and washers with tape matching insulation facing

7. Secure each layer of insulation with stainless-steel bands.

8. Stagger joints between insulation layers at least 75 mm (3 inches).

9. Apply insulation in removable segments on equipment access doors and other elements that require frequent removal for service.

10. Bevel and seal insulation ends around manholes, handholes, ASME stamps, and nameplates.

11. Apply vapor retarding mastic to open joints, breaks, and punctures for insulation indicated to receive vapor retardant.

B. Flexible Elastomeric Thermal Insulation Applications for Tanks and Vessels:  Apply insulation over entire surface of tanks and vessels according to the manufacturer's written instructions.

1. Apply 100 percent coverage of adhesive to surface with manufacturer's recommended adhesive.

2. Seal longitudinal seams and end joints.

3.5 FIELD-APPLIED JACKET APPLICATION

A. Apply glass cloth jacket where indicated, directly over bare insulation or insulation with factory applied jackets.

1. Apply jacket smooth and tight to surface with 50 mm (2 inch) overlap at seams and joints.

2. Embed glass cloth between two 1.6 mm (0.062 inch) thick coats of jacket manufacturer's recommended adhesive.

3. Completely encapsulate insulation with jacket, leaving no exposed raw insulation.

B. Foil and Paper Jackets:  Apply foil and paper jackets where indicated.

1. Draw jacket material smooth and tight.

2. Apply lap or joint strips with the same material as jacket.

3. Secure jacket to insulation with manufacturer's recommended adhesive.

4. Apply jackets with 40 mm (1-1/2-inch) laps at longitudinal seams and 75 mm (3 inch) wide joint strips at end joints.

5. Seal openings, punctures, and breaks in vapor-retardant jackets and exposed insulation with vapor-retarding mastic.

C. PVC Jackets:  Apply jacket with longitudinal seams along top and bottom of tanks and vessels for horizontal applications.  Secure and seal seams and end joints with manufacturer's welding adhesive.

1. Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along the seam and joint edge.

D. Aluminum Jackets:  Secure jackets according to jacket manufacturer's written instructions.

E. Stainless-Steel Jackets:  Secure jackets according to jacket manufacturer's written instructions.

3.6 FINISHES

Coordinate paragraph below with Division 9 Section "Painting."

A. Glass Cloth Jacketed Insulation:  Paint insulation finished with glass-cloth jacket as specified in Division 9 Section "Painting."

B. Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

C. Color:  Final color shall be as selected by the Government.  Vary the color or the first and second coats to allow visual inspection of the completed Work.

3.7 FIELD QUALITY CONTROL

A. [Inspection:  The Government intends to engage a qualified inspection agency to perform the following field quality control inspection, after installing insulation materials, jackets, and finishes, to determine compliance with these specifications:]

B. [Inspection:  The Contractor shall engage a qualified inspection agency to perform the following field quality control inspections, after installing insulation materials, jackets, and finishes, to determine compliance with these specifications:]

C. [Inspection:  The Contractor shall perform the following field quality-control inspections, after installing insulation materials, jackets, and finishes, to determine compliance with the specifications:]

1. Inspect pumps and tanks randomly selected by Government.

2. Remove insulation and covers from two-chilled water pumps or one percent of the chilled water pumps, whichever is greater.

3. Remove insulation and covers from two small tanks or one percent of small tanks, whichever is greater.

D. Insulation applications will be considered defective if sample inspection reveals noncompliance with these specifications.  Remove defective Work and replace with new materials according to these Specifications.

E. Reinstall insulation and covers on pumps and tanks uncovered for inspection according to these Specifications.

3.8 EQUIPMENT APPLICATIONS

A. All insulation characteristics shall comply with the requirements of ASHRAE Standard 90.1, including related tables contained therein and shown at the end of this section. 

3.9 INTERIOR TANK AND VESSEL INSULATION APPLICATION SCHEDULE

A. Equipment:  Chilled-water pumps, air separators and compression tanks.

1. Operating Temperature:  2 to 24 deg C (35 to 75 deg F).
2. Insulation Material: [Flexible elastomeric] [Closed-cell phenolic foam].
3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

B. Equipment:  Aboveground, thermal (ice) storage and low-temperature brine tanks, not factory insulated.

1. Operating Temperature:  0 to 24 deg C (32 to 75 deg F).

2. Insulation Material: [Flexible elastomeric] [Closed-cell phenolic foam].

3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

C. Equipment:  Domestic hot-water storage tanks, not factory insulated.

1. Operating Temperature:  13 to 60 deg C (55 to 140 deg F).

2. Insulation Material: [Flexible elastomeric] [Closed-cell phenolic foam].

3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

D. Equipment:  Heating water pumps, air separators and compression tanks.

1. Operating Temperature:  38 to 93 deg C (100 to 200 deg F).

2. Insulation Material: [Flexible elastomeric] [Closed-cell phenolic foam].

3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

E. Equipment:  Heating water heat exchangers and steam-to-water converters.

1. Operating Temperature:  38 to 232 deg C (100 to 450 deg F).

2. Insulation Material:  [Mineral fiber] [Calcium silicate].

3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].

b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

F. Equipment:  Heating water heat exchangers, steam-to-water converters, and deaerators.

1. Operating Temperature:  38 to 232 deg C (100 to 450 deg F).

2. Insulation Material:  [Mineral fiber] [Calcium silicate].

3. Insulation Thickness:  <Insert Thickness>

4. [Field Applied Jacket:  Glass cloth.]

5. [Field Applied Jacket:  Foil and paper.]

6. [Field Applied Jacket:  PVC.]

7. [Field Applied Jacket:  Aluminum.]

a. Aluminum Thickness:  [0.6 mm (0.024 inch)] [0.8 mm (0.032 inch)] [1.0 mm (0.040 inch)].
b. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

8. [Field Applied Jacket:  Stainless steel.]

a. Corrugation Dimension:  [32 by 6 mm (1-1/4 by 1/4 inch)] [64 by 16 mm (2-1/2 by 5/8 inch)].

9. Vapor Retardant Required:  [Yes] [No].

10. Finish:  [Painted] [None].

3.10 INTERIOR FLAT-SURFACE EQUIPMENT INSULATION APPLICATION SCHEDULE

A. Equipment:  Steam condensate receivers, not factory insulated.

1. Operating Temperature:  38 to 232 deg C (100 to 450 deg F).

2. Insulation Material:  [Mineral fiber] [Calcium silicate].

3. Insulation Thickness:  <Insert Thickness>

4. Field Applied Jacket:  [Foil and paper] [Aluminum] [Stainless steel].  <Insert Other Type>

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

END OF SECTION 15082

EQUIPMENT INSULATION
15082 - 1

