Copyright 1997 AIA
GSA VERSION MASTERSPEC(
6 /97 (GSA 03/03)


Copyright 1997 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15083 - PIPE INSULATION
PART 1 -  GENERAL

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

1.1 RELATED DOCUMENTS

A. Drawings, and the general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section. 

1.2 
SUMMARY

B. This Section includes preformed, rigid and flexible pipe insulation; insulating cements; field-applied jackets; accessories and attachments; and sealing compounds.

C. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Hydronic Distribution" for loose-fill pipe insulation in underground piping outside the building.

2. Division 2 Section "Steam Distribution" for loose-fill pipe insulation in underground piping outside the building.

3. Division 7 Section "Firestopping" for firestopping materials and requirements for penetrations through fire and smoke barriers.

4. Division 15 Section “Basic Materials and Methods” for additional material specifications.

5. Division 15 Section "Duct Insulation" for insulation for ducts and plenums.

6. Division 15 Section "Equipment Insulation" for insulation materials and application for pumps, tanks, hydronic specialties, and other equipment.

7. Division 15 Section "Hangers and Supports" for pipe insulation shields and protection saddles.

1.2 DEFINITIONS

A. k:
Thousand (1000) units

B. M:
Million (1,000,000) units

1.3 SUBMITTALS

A. Product Data:  Identify thermal conductivity, thickness, and jackets (both factory and field applied), for each type of product indicated.

B. Shop Drawings:  Show fabrication and installation details for the following:

1. Application of protective shields, saddles, and inserts at pipe hangers for each type of insulation and hanger.

2. Attachment and covering of heat tracing installed inside the insulation.

3. Insulation application at pipe expansion joints for each type of insulation.

4. Insulation application at elbows, fittings, flanges, valves, and specialties for each type of insulation.

5. Removable insulation at piping specialties and equipment connections.

6. Application of field-applied jackets.

C. Samples:  Provide samples for each type of insulation and jacket.  Identify each Sample, describing product and intended use.  Submit Samples in the following sizes:

7. Preformed Pipe Insulation Materials:  300 mm (12 inches) long by DN50 (NPS 2).

8. Sheet Form Insulation Materials:  300 mm (12 inches) square.

9. Jacket Materials:  300 mm (12 inches) long by DN50 (NPS 2).

10. Manufacturer's Color Charts:  Show the full range of colors available for each type of field-applied finish material indicated.

Surface-burning characteristics specified in "Quality Assurance" Article should be verified by an independent testing agency.  Where critical, require test report Submittals.  Delete test reports below if not required.

C. Material Test Reports:  From a qualified testing agency acceptable to authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealers, attachments, cements, and jackets with requirements indicated in Section 6 - Heating, Ventilating, and Air Conditioning, Section 7 - Service Water Heating, of ASHRAE/IESNA Standard 90.1, including related tables shown at the end of this section.  Include dates of tests.

Retain below if "Installer Qualifications" Paragraph is retained in "Quality Assurance" Article.

D. Installer Certificates:  Signed by the Contractor certifying that installers comply with requirements.

E. Warranty: 

1. Submit a sample of the warranty that will be signed by the Contractor certifying that the installation and materials comply with the requirements of this and other applicable specifications. 
2. Special warranty specified in this section.
1.4  
QUALITY ASSURANCE

Delete paragraph below if not required or available at Project location.  Apprenticeship programs are usually associated with union shops.  Other craft training programs are available.

F. ASHRAE/IESNA Compliance:
All insulation characteristics shall comply with the requirements of ASHRAE Standard 90.1, including related tables contained therein.  Insulation characteristics shall comply with applicable requirements of ASHRAE Standard 90.1.  Supply ductwork with the exception of buried ductwork and ductwork located in indirectly conditioned spaces shall be insulated in accordance with ASHRAE Standard 90.1. Supply duct insulation shall have a vapor barrier jacket.  The vapor barrier jacket shall cover the duct system with a continuous, unbroken vapor seal. Return and exhaust air distribution systems shall be insulated in accordance with ASHRAE Standard 90.1. 

G. Code of Federal Regulations Compliance: Insulation characteristics shall comply with the requirements of the Code of Federal Regulations 10 CFR-435.107 including related tables shown therein and shown at the end of this section.

H. General Services Administration (GSA) Compliance: Insulation characteristics shall comply with the requirements of the Codes and Standards published in the GSA document Facilities Standards for the Public Buildings including related tables shown therein and at the end of this section.

I. General Compliance:  Where the requirements for a description of insulation characteristics or performance ratings defined in a publication or standard referenced herein conflict, the most restrictive shall apply.

J. General Compliance:
Installer Qualifications:  Insulation shall be installed by skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the U.S. Department of Labor, Bureau of Apprenticeship and Training.

K. Fire-Test-Response Characteristics:  As determined by testing materials identical to those specified in this Section according to ASTM E 84, NFPA 255 and UL 723 by a testing and inspecting agency acceptable to authorities having jurisdiction.  Accessories such as adhesives, mastics, cements, tapes, etc., shall have the same or better fire and smoke hazard ratings as that identified for the insulation materials.

Revise subparagraphs below to suit Project and products selected.

1. Insulation Installed Indoors:  Flame-spread rating of 25 or less, and smoke-developed rating of 50 or less.

2. Insulation Installed Outdoors:  Flame-spread rating of 75 or less, and smoke-developed rating of 150 or less.

Delete paragraph below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserting specific information in paragraph and subparagraphs below.  Revise wording if only one mockup is required.

L. Mockups:  Before beginning the actual installation of the insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes.  Mockups shall be located and displayed at the project site until directed otherwise by the Owner.  Build mockups according to the following requirements, using materials indicated for the completed Work:

1. Include the following mockups:

a. One 3-m (10-foot) section of DN50 (NPS 2) straight pipe.

b. One 90-degree elbow.

c. One tee fitting.

d. One DN50 (NPS 2) valve.

e. Four support hangers, including hanger shield and insert.

f. One strainer with removable portion of insulation.

g. One reducer.

h. One expansion joint.

2. Mockups shall be built with cutaway sections to allow observation of application details for insulation materials, mastics, attachments, and jackets.

3. Build mockups in the location indicated or, if not indicated, as directed by the Engineer.

4. Notify the Engineer seven days in advance of the dates and times when mockups will be constructed.

5. Obtain Architect's approval of mockups before starting insulation application.

6. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

7. Mockups shall remain the property of the Contractor but shall only be removed from the project site when directed by the Owner.

Delete subparagraph above or below.  Below is applicable only if mockups are erected as part of building rather than separately.

8. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

1.5 
DELIVERY, STORAGE, AND HANDLING

A. Container marking is an option in ASTM standards; the default condition does not include the marking below unless specified in the Contract.

1. Packaging:  Ship insulation materials in containers marked by the insulation manufacturer with appropriate ASTM specification designation, type and grade, and maximum use temperature.

1.6  
COORDINATION

M. Coordinate carefully the size and location of supports, hangers, and insulation shields specified in Division 15 Section "Hangers and Supports."

N. Coordinate carefully with trades to ensure that the necessary clearance requirements are maintained for proper installation of the insulation.

O. Coordinate the installation and testing of steam or electric heat tracing before applying insulation.

1.3 SCHEDULING

A. Installation of the insulation shall begin only after testing of the piping systems and, where required, after installing and testing heat-tracing systems.  Insulation application may begin on segments of piping that have satisfactory test results.

1.4 WARRANTY

A. Special Warranty:  The system herein specified shall be free from defects in workmanship and material under normal use and service.  If within [12] [24] <insert number> months from the date of acceptance by the Owner/Architect, equipment or software herein described is proven to be defective in workmanship or material, it shall be adjusted, repaired, or replaced free of charge.  This system warranty shall also include each software program, upgrade and maintenance.

Verify available warranties for units and components and insert number below.

B. Warranty Period for <insert equipment name>:  [Two] <insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with these specifications, manufacturers offering products that may be incorporated into the Work include, but are not limited to, those listed below:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with these specifications, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Cellular-Glass Insulation:

a. Pittsburgh-Corning Corp. 

b. <Insert manufacturer's name.>

c. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

2. Flexible Elastomeric Thermal Insulation:

a. Armstrong World Industries, Inc.

b. Rubatex Corp.

c. <Insert manufacturer's name.>

d. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

3. Polyolefin Insulation:

a. Armstrong World Industries, Inc.

b. IMCOA.

c. <Insert manufacturer's name.>

d. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

4. Closed-Cell Phenolic-Foam Insulation:

a. Kooltherm Insulation Products, Ltd.

b. <Insert manufacturer's name.>

c. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

5. Calcium Silicate Insulation:

a. Owens-Corning Fiberglas Corp.

b. Pabco.

c. Schuller International, Inc.

d. <Insert manufacturer's name.>

e. Manufacturers that have obtained prior approval from the reviewing agency in accordance with Section “Submittals.”

2.2 INSULATION MATERIALS

A. Mineral-Fiber Insulation:  Insulation shall consist of glass fibers bonded with a thermosetting resin complying with the following:

For operating temperatures higher than 850 deg F (454 deg C), change insulation below to ASTM C 547, Type II.

1. Preformed Pipe Insulation:  Insulation shall comply with ASTM C 547, Type 1, with factory-applied, all-purpose, vapor-retarding jacket.

ASTM C 553, Type IV, has similar properties to ASTM C 547, Type I.  For operating temperatures higher than 850 deg F (454 deg C), change insulation below to ASTM C 553, Type V.

2. Blanket Insulation:  Insulation shall comply with ASTM C 553, Type II, without facing.

Military Specification referenced below is the only standard now available.  Mil-A-3316C was last updated in October 1989.

3. Fire-Resistant Adhesive:  Adhesive shall comply with MIL-A-3316C in the following classes and grades:

a. Class 1, Grade A for bonding glass cloth and tape to unfaced glass-fiber insulation, for sealing edges of glass-fiber insulation, and for bonding lagging cloth to unfaced glass-fiber insulation.

b. Class 2, Grade A for bonding glass-fiber insulation to metal surfaces.

4. Vapor-Retarding Mastics:  Mastics shall be fire- and water-resistant, vapor-retarding mastic for indoor applications.  Mastics shall comply with MIL-C-19565C, Type II.

Mineral fiber is suitable for temperatures from 100 to 1600 deg F (38 to 871 deg C).  Vermiculite is suitable for temperatures from 100 to 1800 deg F (38 to 982 deg C).

5. Mineral-Fiber Insulating Cements:  Comments shall comply with ASTM C 195.

6. Expanded or Exfoliated Vermiculite Insulating Cements:  Comments shall comply with ASTM C 196.

Hydraulic-setting, mineral-fiber cement is suitable for temperatures from 100 to 1200 deg F (38 to 649 deg C) and for a smooth surface.

7. Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement:  Comments shall comply with ASTM C 449/C 449M.

B. Cellular-Glass Insulation:  Insulation shall consist of inorganic, foamed or cellulated glass, annealed, rigid, hermetically sealed cells, and be incombustible.

If retaining both types of insulation below, indicate where each type applies in one of the insulation application schedules at the end of this Section.

1. Preformed Pipe Insulation, without Jacket:  Insulation shall comply with ASTM C 552, Type II, Class 1.

2. Preformed Pipe Insulation, with Jacket:  Insulation shall comply with ASTM C 552, Type II, Class 2.

Flexible elastomeric thermal insulation is not suitable for temperatures lower than minus 70 deg F (minus 57 deg C) and higher than 220 deg F (104 deg C).

C. Flexible Elastomeric Thermal Insulation:  Insulation consisting of closed-cell, sponge- or expanded-rubber materials.  Insulation shall comply with ASTM C 534, Type I for tubular materials and Type II for sheet materials.

1. Adhesive:  Adhesive shall be as recommended by insulation material manufacturer and as specified herein.

2. Ultraviolet-Protective Coating:  Coating shall be as recommended by the insulation manufacturer.

Verify surface-burning characteristics of polyolefin insulation by an independent testing agency.  Require test report Submittals where fire-performance characteristics are critical.  Include test date and test methods.

Polyolefin insulation is not suitable for temperatures lower than minus 165 deg F (minus 109 deg C) and higher than 210 deg F (99 deg C).

D. Polyolefin Insulation:  Insulation shall consist of unicellular polyethylene thermal plastic, and be configured as preformed pipe insulation.  Insulation shall comply with ASTM C 534, Type I, except for density.

1. Adhesive:  Adhesive shall be as recommended by insulation material manufacturer and as specified herein.

Closed-cell phenolic-foam insulation is available in Grades 1 and 2.  Grade 1 has a lower thermal conductivity than Grade 2.

E. Closed-Cell Phenolic-Foam Insulation:  Insulation shall be configured as preformed pipe insulation, and consist of rigid, expanded, closed-cell phenolic foam structure.  Comply with ASTM C 1126, Type III, Grade 1.

For temperatures higher than 1200 deg F (649 deg C), change insulation below to ASTM C 533, Type II.  Type II is suitable for temperatures up to 1700 deg F (927 deg C).

F. Calcium Silicate Insulation:  Insulation shall be configured in reformed pipe sections and consist of noncombustible, inorganic, hydrous calcium silicate with a nonasbestos fibrous reinforcement.  Insulation shall conform with ASTM C 533, Type I.

G. Prefabricated Thermal Insulating Fitting Covers:  Covers shall conform with ASTM C 450 for dimensions used in preforming insulation to cover valves, elbows, tees, and flanges.

2.3 FIELD-APPLIED JACKETS

Insulation jackets below are for field applications.  Delete below if jackets are factory applied.  ASTM C 921, Type 1, is for use over insulation on pipes operating below ambient temperatures at least part of the time or for where a vapor retarder is required.  ASTM C 921, Type II, is for use over insulation on pipes operating above ambient temperatures or for where a vapor retarder is not required.

A. General:  Jackets shall comply with ASTM C 921, Type 1, unless otherwise indicated.

A properly sealed foil, scrim, kraft-paper (FSK) jacket, common with most forms of factory-applied jackets for mineral-fiber insulation, meets vapor-retarder requirements of ASTM C 921, Type I.

B. Foil and Paper Jacket:  Jacket shall consist of laminated, glass-fiber-reinforced, flame-retardant kraft paper and aluminum foil.

Although other thicknesses for PVC jackets are available, 25/50 flame-spread/smoke-developed ratings apply only to thicknesses of 20 mils (0.5 mm) and less.

C. PVC Jacket:  Jacket shall consist of high-impact, ultraviolet-resistant PVC; 0.5 mm (20 mils) thick; roll stock ready for shop or field cutting and forming.

1. Adhesive:  As recommended by insulation material manufacturer.

PVC jackets are available in several colors.  Colored jackets may be used to replace field painting.  Ultraviolet rays fade colors in exterior applications.  Some colors (black, gray, and white) do not fade as quickly as other colors (red, orange, and green).

Retain one of two subparagraphs below.

2. PVC Jacket Color:  White or gray.

3. PVC Jacket Color:  Color-code piping jackets based on materials contained within the piping system.

D. Heavy PVC Fitting Covers:  Covers shall be factory-fabricated fitting covers manufactured from 0.75-mm- (30-mil-) thick, high-impact, ultraviolet-resistant PVC.

1. Shapes:  Shapes shall include 45- and 90-degree, short- and long-radius elbows, tees, valves, flanges, reducers, end caps, soil-pipe hubs, traps, mechanical joints, and P-trap and supply covers for lavatories for the disabled.

2. Adhesive:  Adhesive shall be as recommended by insulation material manufacturer and as specified herein.

E. Standard PVC Fitting Covers:  Covers shall be factory-fabricated fitting covers manufactured from 0.5-mm- (20-mil-) thick, high-impact, ultraviolet-resistant PVC.

1. Shapes:  Shapes shall include 45- and 90-degree, short- and long-radius elbows, tees, valves, flanges, reducers, end caps, soil-pipe hubs, traps, mechanical joints, and P-trap and supply covers for lavatories for the disabled.

2. Adhesive:  Adhesive shall be as recommended by insulation material manufacturer and as specified herein.

Select one of two paragraphs below.

F. Aluminum Jacket:  Jacket shall be factory cut and rolled to indicated sizes.  Comply with ASTM B 209 (ASTM B 209M), 3003 alloy, H-14 temper.

G. Aluminum Jacket:  Jacket shall be from aluminum roll stock, ready for shop or field cutting and forming to indicated sizes.  Comply with ASTM B 209M (ASTM B 209), 3003 alloy, H-14 temper.

Select finish and thickness from subparagraphs below.  Other thicknesses are available.  Verify with manufacturer.

1. [Finish and Thickness:  Smooth finish, 0.25 mm (0.010 inch) thick.]

2. [Finish and Thickness:  Corrugated finish, 0.25 mm (0.010 inch) thick.]

3. [Finish and Thickness:  Stucco-embossed finish, 0.40 mm (0.016 inch) thick.]

4. [Finish and Thickness:  Painted finish, 0.40 mm (0.016 inch) thick.]

Verify that moisture barrier in subparagraph below is adequate for corrosive atmospheres.

5. Moisture Barrier:  0.025-mm- (1-mil-) thick, heat-bonded polyethylene and kraft paper.

6. Elbows:  Preformed, 45- and 90-degree, short- and long-radius elbows; same material, finish, and thickness as jacket.

Select one of two paragraphs below.

H. Stainless-Steel Jacket:  Jacket shall be from ASTM A 666, Type 304 or 316; 2.5 mm (0.10 inch) thick; and factory cut and rolled to indicated sizes.

I. Stainless-Steel Jacket:  Jacket shall be from ASTM A 666, Type 304 or 316; 2.5 mm (0.10 inch) thick; and roll stock ready for shop or field cutting and forming to indicated sizes.

Select from two moisture barriers below.  Features are from Pabco jackets.  The first moisture barrier is standard and is for corrosive atmospheres; the second moisture barrier is optional and produces lower flame-spread and smoke-developed ratings.

1. [Moisture Barrier:  0.025-mm- (1-mil-) thick, heat-bonded polyethylene and kraft paper.]

2. [Moisture Barrier:  0.075-mm- (3-mil-) thick, heat-bonded polyethylene and kraft paper.]

3. Elbows:  Gore type, for 45- and 90-degree elbows in same material, finish, and thickness as jacket.

4. Jacket Bands:  Stainless steel, Type 304, 19 mm (3/4 inch) wide.

2.4 ACCESSORIES AND ATTACHMENTS

A. Glass Cloth and Tape:  Cloth and tape shall comply with MIL-C-20079H, Type I for cloth and Type II for tape, respectively.  Woven glass-fiber fabrics shall be plain weave and pre-sized to a minimum of 270 g/sq. m (8 oz./sq. yd.).

1. Tape Width:  100 mm (4 inches).

B. Bands:  Provide 19 mm (3/4 inch) wide, in one of the following materials compatible with jacket:

1. Stainless Steel:  ASTM A 666, Type 304; 0.5 mm (0.020 inch) thick.

2. Galvanized Steel:  0.13 mm (0.005 inch) thick.

3. Aluminum:  0.18 mm (0.007 inch) thick.

4. Brass:  0.25 mm (0.010 inch) thick.

5. Nickel-Copper Alloy:  0.13 mm (0.005 inch) thick.

C. Wire:  Wire shall be 2.0-mm (0.080-inch), nickel-copper alloy; 1.6-mm (0.062-inch), soft-annealed, stainless steel; or 1.6-mm (0.062-inch), soft-annealed, galvanized steel.

2.5 VAPOR RETARDANTS

Products with a perm rating of 1.0 are considered vapor retarders.  Ambient conditions and operating temperatures must be considered when selecting a vapor retarder.

A. Mastics:  Mastic type materials shall be as recommended by the insulation material manufacturer and shall be compatible with the insulation materials, jackets, and substrates.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and field conditions for compliance with the insulation material manufacturers’ requirements for installation and other conditions affecting performance of the insulation application.

B. Proceed with the installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Surface Preparation:  Clean and dry surfaces scheduled or specified to receive insulation.  Remove materials that might adversely affect the insulation application.

3.3 GENERAL APPLICATION REQUIREMENTS

A. Apply insulation materials, accessories, and finishes in accordance with the manufacturer's written instructions.  Finished insulation surfaces shall be smooth, straight, and even, and shall be free of voids throughout the length of piping, including fittings, valves, and specialties.

B. Refer to schedules at the end of this Section for materials, forms, jackets, and thickness required for each piping system.

C. Accessories shall be compatible with the insulation materials and suitable for the intended service.  Use accessories that will not corrode, soften, or otherwise attack the insulation or jacket in either a wet or a dry state.

D. Apply insulation with tight longitudinal seams at the top and the bottom of horizontal pipe runs.  Stagger longitudinally seams 180 degrees on vertical pipe runs. 

E. Multiple layers of insulation shall be applied with lateral, longitudinal and end seams staggered.

F. Do not weld brackets, clips, or other attachment devices to piping, fittings, and specialties.

G. Joints and seams shall be sealed with a vapor-retarding mastic on insulation indicated to have or receive a vapor retardant.

H. Keep insulation materials dry during application and finishing.  Materials that show signs of having been wet, shall be replaced with materials at no additional cost to the Owner.

I. Apply insulation with tight longitudinal seams and end joints.  Bond seams and joints with adhesive recommended by the insulation material manufacturer.

J. Apply insulation with the least number of joints practical.

K. Apply insulation over fittings, valves, and specialties, with continuous thermal and vapor-retardant integrity, unless otherwise specifically indicated.  Refer to special instructions for applying insulation over fittings, valves, and specialties.

L. Hangers and Anchors:  Where vapor retardant is indicated, seal penetrations in insulation at hangers, supports, anchors, and other projections with vapor-retarding mastic.

1. Apply insulation continuously through hangers and around anchor attachments.

2. For insulation application where vapor retardants are indicated, extend insulation on anchor legs at least 300 mm (12 inches) from point of attachment to pipe and taper insulation ends.  Seal tapered ends with a compound recommended by the insulation material manufacturer to maintain vapor retardant.

3. Install insert materials and apply insulation to tightly join the insert.  Seal insulation to insulation inserts with adhesive or sealing compound recommended by the insulation material manufacturer.

4. Cover inserts with jacket material matching adjacent pipe insulation.  Install shields over jacket, arranged to protect the jacket from tear or puncture by the hanger, support, and shield.

M. Insulation Terminations:  For insulations application where vapor retardants are indicated, taper insulation ends.  Seal tapered ends with a compound recommended by the insulation material manufacturer to maintain vapor retardant.  Sealant characteristics and applications shall comply with the requirements of ASHRAE Standard 90.1.

N. Insulation that is subject to reduction in thermal resistivity if wetted shall be enclosed with a vapor seal such as a vapor barrier jacket. Insulation and vapor jackets shall comply with the requirements of ASHRAE 90.1, including related tables shown at the end of this section.

O. Apply adhesives and mastics at not less than the manufacturer's recommended coverage rate.

P. Provide vapor barrier jacket as described by the requirements of ASHRAE Standard 90.1.  Apply insulation with integral jackets as follows:

1. Placement:  Pull jacket tight and smooth.

2. Circumferential Joints:  Cover joints and seams with 75-mm- (3-inch-) wide strips, of the same material as the insulation jacket.  Secure the strips with adhesive and outward clinching staples along both edges of the strip and spaced 100 mm (4 inches) o.c.

3. Longitudinal Seams:  Overlap jacket seams at least 40 mm (1-1/2 inches).  Apply insulation with seams located as specified above.  Clean and dry surface to receive the self-sealing lap.  Staple laps with outward clinching staples along edge at 100 mm (4 inches) o.c.

a. Exception:  Do not staple longitudinal laps on insulation having a vapor retardant.

4. Vapor-Retarding Mastics:  Where vapor retardants are indicated, apply mastic on seams and joints and at ends adjacent to flanges, unions, valves, and fittings.

5. At penetrations in jackets for thermometers and pressure gages, fill and seal voids with vapor-retarding mastic.

Q. Roof Penetrations:  Apply insulation for interior applications to a point even with top of roof flashing.

1. Seal penetrations with vapor-retarding mastic.

2. Apply insulation appropriate for exterior applications tightly joined to interior insulation ends.

3. Extend metal jacket of exterior insulation outside of the roof flashing at least 50 mm (2 inches) below top of roof flashing.

4. Seal metal jacket to roof flashing with vapor-retarding mastic.

Select one of two paragraphs below.

R. Exterior Wall Penetrations:  For penetrations of below-grade exterior walls, terminate insulation flush with mechanical sleeve seal.  Seal terminations with vapor-retarding mastic.

Coordinate requirements in two paragraphs below with Division 7 Section "Joint Sealants."

S. Interior Wall and Partition Penetrations:  Apply insulation continuously through walls and floors.

T. Fire-Rated Wall and Partition Penetrations:  Apply insulation continuously through penetrations of fire-rated walls and partitions.

1. Firestopping and fire-resistive joint sealers are specified in Division 7 Section "Firestopping."

U. Floor Penetrations:  Apply insulation continuously through floor assembly.

1. For insulation with vapor retardants, seal insulation with vapor-retarding mastic where floor supports penetrate vapor retardant.

V. All sanitary sewer vents terminating through the roof shall be insulated for a minimum of 1.83 meters (6 feet) below the roof line and shall include a vapor barrier jacket on the insulation.  Insulation and vapor barrier jackets shall comply with the requirements of ASHRAE Standard 90.1, including related tables shown at the end of this section.  Insulation characteristics shall comply with applicable requirements of ASHRAE Standard 90.1.  Insulating materials and accessories shall comply with the fire and smoke hazard ratings indicated in ATSM E 84, NFPA 255 and UL723.  Accessories such as adhesives, mastics, cements, tapes, etc., shall have the same or better fire and smoke hazard ratings as that identified for the insulation materials.

W. All piping exposed in plenums or above ceilings shall be insulated in accordance with applicable requirements of ASHRAE Standard 90.1 or as described in this section.

X. All piping systems conveying liquids of fluids having design temperatures less than 18(C (65(F) or greater than 40(C (105(F) shall be insulated.  Piping systems with surface temperatures below the average dewpoint temperature of the indoor ambient air and where condensate drip will cause damage or create a hazard shall be insulated with a vapor barrier to prevent condensation formation regardless to whether piping is concealed or exposed.  Chilled water piping shall be insulated with non-permeable insulation having a perm rating of 0.00 such as cellular glass.

3.4 CELLULAR-GLASS INSULATION APPLICATION

A. Apply insulation to straight pipes and tubes as follows:

1. Secure each layer of insulation to pipe with wire, tape, or bands without deforming insulation materials.

2. Where vapor retardants are indicated, seal longitudinal seams and end joints with vapor-retarding mastic.

3. For insulation with factory-applied jackets, secure laps with outward clinched staples at 150 mm (6 inches) o.c.

4. For insulation with factory-applied jackets with vapor retardants, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by the insulation material manufacturer and seal with vapor-retarding mastic.

B. Apply insulation to flanges as follows:

1. Apply preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of cellular-glass block insulation of the same thickness as pipe insulation.

4. Apply canvas jacket material with manufacturer's recommended adhesive, overlapping seams at least 25 mm (1 inch), and seal joints with vapor-retarding mastic.

C. Apply insulation to fittings and elbows as follows:

1. Apply premolded insulation sections of the same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When premolded sections of insulation are not available, apply mitered sections of cellular-glass insulation.  Secure insulation materials with wire, tape, or bands.

3. Cover fittings with standard PVC fitting covers.

Select subparagraph above or below.

4. Cover fittings with heavy PVC fitting covers.  Overlap PVC covers on pipe insulation jackets at least 25 mm (1 inch) at each end.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

D. Apply insulation to valves and specialties as follows:

1. Apply premolded segments of cellular-glass insulation or glass-fiber blanket insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.  For check valves, arrange insulation for access to strainer basket without disturbing insulation.

2. Apply insulation to flanges as specified for flange insulation application.

3. Use preformed standard PVC fitting covers for valve sizes where available.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

Select subparagraph above or below.

4. Use preformed heavy PVC fitting covers for valve sizes where available.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

5. For larger sizes where PVC fitting covers are not available, seal insulation with canvas jacket and sealing compound recommended by the insulation material manufacturer.

3.5 FLEXIBLE ELASTOMERIC THERMAL INSULATION APPLICATION

A. Apply insulation to straight pipes and tubes as follows:

1. Follow manufacturer's written instructions for applying insulation.

2. Seal longitudinal seams and end joints with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

B. Apply insulation to flanges as follows:

1. Apply pipe insulation to outer diameter of pipe flange.

2. Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of sheet insulation of the same thickness as pipe insulation.

4. Secure insulation to flanges and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

C. Apply insulation to fittings and elbows as follows:

1. Apply mitered sections of pipe insulation.

2. Secure insulation materials and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

D. Apply insulation to valves and specialties as follows:

1. Apply preformed valve covers manufactured of the same material as pipe insulation and attached according to the manufacturer's written instructions.

2. Apply cut segments of pipe and sheet insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.  For check valves, fabricate removable sections of insulation arranged to allow access to strainer basket.

3. Apply insulation to flanges as specified for flange insulation application.

4. Secure insulation to valves and specialties and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

3.6 POLYOLEFIN INSULATION APPLICATION

A. Apply insulation to straight pipes and tubes as follows:

1. Follow manufacturer's written instructions for applying insulation.

2. For split tubes, seal longitudinal seams and end joints with manufacturer's recommended adhesive.

3. For self-adhesive insulation, staple longitudinal seams after sealing.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

B. Apply insulation to flanges as follows:

1. Apply pipe insulation to outer diameter of pipe flange.

2. Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of polyolefin sheet insulation of the same thickness as pipe insulation.

4. Secure insulation to flanges and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

C. Apply insulation to fittings and elbows as follows:

1. Apply mitered sections of polyolefin pipe insulation.

2. Secure insulation materials and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

D. Apply insulation to valves and specialties as follows:

1. Apply preformed valve covers manufactured of the same material as pipe insulation and attached according to the manufacturer's written instructions.

2. Apply cut segments of polyolefin pipe and sheet insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.  For check valves, fabricate removable sections of insulation arranged to allow access to strainer basket.

3. Apply insulation to flanges as specified for flange insulation application.

4. Secure insulation to valves and specialties and seal seams with manufacturer's recommended adhesive.  Cement to avoid openings in insulation that will allow passage of air to the pipe surface.

3.7 CLOSED-CELL PHENOLIC-FOAM INSULATION APPLICATION

A. Apply insulation to straight pipes and tubes as follows:

1. Secure each layer of insulation to pipe with wire, tape, or bands without deforming insulation materials.

2. Where vapor retardants are indicated, seal longitudinal seams and end joints with vapor-retarding mastic.

3. For insulation with factory-applied jackets, secure laps with outward clinched staples at 150 mm (6 inches) o.c.

4. For insulation with factory-applied jackets with vapor retardants, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by the insulation material manufacturer and seal with vapor-retarding mastic.

B. Apply insulation to flanges as follows:

1. Apply preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of block insulation of the same material and thickness as pipe insulation.

4. Apply canvas jacket material with manufacturer's recommended adhesive, overlapping seams at least 25 mm (1 inch), and seal joints with vapor-retarding mastic.

C. Apply insulation to fittings and elbows as follows:

1. Apply premolded insulation sections of the same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When premolded sections of insulation are not available, apply mitered sections of phenolic-foam insulation.  Secure insulation materials with wire, tape, or bands.

3. Cover fittings with standard PVC fitting covers.

Select subparagraph above or below.

4. Cover fittings with heavy PVC fitting covers.  Overlap PVC covers on pipe insulation jackets at least 25 mm (1 inch) at each end.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

D. Apply insulation to valves and specialties as follows:

1. Apply premolded insulation sections of the same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When premolded sections of insulation are not available, apply mitered segments of phenolic-foam insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.  For check valves, arrange insulation for access to strainer basket without disturbing insulation.

3. Apply insulation to flanges as specified for flange insulation application.

4. Use preformed standard PVC fitting covers for valve sizes where available.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

Select subparagraph above or below.

5. Use preformed heavy PVC fitting covers for valve sizes where available.  Secure fitting covers with manufacturer's attachments and accessories.  Seal seams with tape and vapor-retarding mastic.

6. For larger sizes where PVC fitting covers are not available, seal insulation with canvas jacket and sealing compound recommended by the insulation material manufacturer.

3.8 CALCIUM SILICATE INSULATION APPLICATION

A. Apply insulation to straight pipes and tubes as follows:

1. Secure each layer of insulation to pipe with stainless-steel bands at 300-mm (12-inch) intervals and tighten without deforming insulation materials.

2. Apply two-layer insulation with joints tightly butted and staggered at least 75 mm (3 inches).  Secure inner layer with 1.6-mm (0.062-inch), soft-annealed, stainless steel wire spaced at 300-mm (12-inch) intervals.  Secure outer layer with stainless-steel bands at 300-mm (12-inch) intervals.

3. Apply a skim coat of mineral-fiber, hydraulic-setting cement to surface of installed insulation.  When dry, apply flood coat of lagging adhesive and press on one layer of glass cloth or tape.  Overlap edges at least 25 mm (1 inch).  Apply finish coat of lagging adhesive over glass cloth or tape.  Thin the finish coat to achieve smooth finish.

B. Apply insulation to flanges as follows:

1. Apply preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of block insulation of the same material and thickness as pipe insulation.

4. Finish flange insulation the same as pipe insulation.

C. Apply insulation to fittings and elbows as follows:

1. Apply premolded insulation sections of the same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When premolded sections of insulation are not available, apply mitered sections of calcium silicate insulation.  Secure insulation materials with stainless-steel wire.

3. Finish insulation of fittings the same as pipe insulation.

D. Apply insulation to valves and specialties as follows:

1. Apply mitered segments of calcium silicate insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.  For check valves, arrange insulation for access to strainer basket without disturbing insulation.

2. Apply insulation to flanges as specified for flange insulation application.

3. Finish valve and specialty insulation the same as pipe insulation.

3.9 FIELD-APPLIED JACKET APPLICATION

A. Apply glass-cloth jacket, where indicated, directly over bare insulation or insulation with factory-applied jackets.

1. Apply jacket smooth and tight to surface with 50-mm (2-inch) overlap at seams and joints.

2. Embed glass cloth between two 1.6-mm- (0.062-inch-) thick coats of jacket manufacturer's recommended adhesive.

3. Completely encapsulate insulation with jacket, leaving no exposed raw insulation.

B. Foil and Paper Jackets:  Apply foil and paper jackets where indicated.

1. Draw jacket material smooth and tight.

2. Apply lap or joint strips with the same material as jacket.

3. Secure jacket to insulation with manufacturer's recommended adhesive.

4. Apply jackets with 40-mm (1-1/2-inch) laps at longitudinal seams and 75-mm- (3-inch-) wide joint strips at end joints.

5. Seal openings, punctures, and breaks in vapor-retardant jackets and exposed insulation with vapor-retarding mastic.

C. Apply PVC jacket where indicated, with 25-mm (1-inch) overlap at longitudinal seams and end joints.  Seal with manufacturer's recommended adhesive.

D. Apply metal jacket where indicated, with 50-mm (2-inch) overlap at longitudinal seams and end joints.  Overlap longitudinal seams arranged to shed water.  Seal end joints with weatherproof sealant recommended by insulation manufacturer.  Secure jacket with stainless-steel bands 300 mm (12 inches) o.c. and at end joints.

3.10 FINISHES

Coordinate paragraph below with Division 9 Section "Painting."

A. Glass-Cloth Jacketed Insulation:  Paint insulation finished with glass-cloth jacket as specified in Division 9 Section "Painting."

B. Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of the insulation manufacturer's recommended protective coating.

C. Color:  Final color shall be as selected by The Government.  Vary the color of the first and second coats to allow visual inspection of the completed Work.

3.11 PIPING SYSTEM APPLICATIONS

A. All insulation materials and thicknesses shall comply with the requirements of SAHRAE Standard 90.1, including related tables contained therein and at the end of this Section.

Edit list below to suit Project

B. Items Not Insulated:  Unless otherwise indicated, do not apply insulation to the following systems, materials, and equipment:

1. Flexible connectors.

2. Vibration-control devices.

3. Fire-suppression piping.

4. Drainage piping located in crawl spaces, unless otherwise indicated.

5. Below-grade piping, unless otherwise indicated.

6. Chrome-plated pipes and fittings, unless potential for personnel injury.

7. Air chambers, unions, strainers, check valves, plug valves, and flow regulators in systems not subject to producing condensation.

3.12 FIELD QUALITY CONTROL

Inspections in this Article are destructive inspections.  It is not necessary for applications where insulation on fittings and valves is not concealed under covers.  Contractors will include in construction costs the labor and materials to perform the inspection and the labor and materials to replace removed fitting and valve insulation and covers.  Architect should be prepared to reject all work if defective work is discovered in sample inspection.

Retain one of three paragraphs below.  Delete all if field quality-control inspections are not required.

A. [Inspection:  The Owner intends to engage a qualified inspection agency to perform the following field quality-control inspection, after installing insulation materials, jackets, and finishes, to determine compliance with these specifications:]

B. [Inspection:  The Contractor shall engage a qualified inspection agency to perform the following field quality-control inspections, after installing insulation materials, jackets, and finishes, to determine compliance with these specifications:]

C. [Inspection:  The Contractor shall perform the following field quality-control inspections, after installing insulation materials, jackets, and finishes, to determine compliance with the specifications:]

Retain subparagraphs below with any paragraph selected above.

1. Inspect fittings and valves randomly selected by the Government.

2. Remove fitting covers from 20 elbows or 1 percent of elbows, whichever is less, for various pipe sizes.

3. Remove fitting covers from 20 valves or 1 percent of valves, whichever is less, for various pipe sizes.

Edit paragraph below to limit noncompliance statement as required.  As stated, Architect could require all fittings to be removed and replaced.

D. Insulation applications will be considered defective if sample inspection reveals noncompliance with these specifications.  Remove defective Work and replace with new materials according to these Specifications.

E. Reinstall insulation and covers on fittings and valves uncovered for inspection according to these Specifications.

3.13 INSULATION APPLICATION SCHEDULE, GENERAL

A. Refer to insulation application schedules for required insulation materials, vapor retardants, and field-applied jackets.

B. Application schedules identify piping system and indicate pipe size ranges and material, thickness, and jacket requirements.

Modify schedules below to suit Project.  Do not duplicate requirements inserted in Part 2.  Remove brackets and uppercase editor's notes after editing schedules.

Select insulation thicknesses based on guidelines from ASHRAE 90.1 and local mechanical codes.  Thickness requirements also vary according to temperature differences, and relative humidity conditions affect thickness selections for each application.  Calculate thickness based on thermal properties of insulation materials specified.  Consider condensation prevention requirements.  Additional insulation and vapor retarders may be required to prevent condensation in some conditions.

Also consider the exposure of installed insulation to damage.  Concealed applications have less risk than exposed.

Consider finishes for exposed applications.  Finish requirements affect factory- and field-applied jacket selection.

Edit insulation schedules below to suit Project.

3.14 INTERIOR INSULATION APPLICATION SCHEDULE

A. Service:  Domestic hot and recirculated hot water.

1. Operating Temperature:  15 to 82 deg C (60 to 180 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

B. Service:  Domestic chilled drinking water.

1. Operating Temperature:  2 to 15 deg C (35 to 60 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thickness:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

C. Service:  Rainwater conductors.

1. Operating Temperature:  0 to 38 deg C (32 to 100 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

D. Service:  Roof drain bodies.

1. Operating Temperature:  0 to 38 deg C (32 to 100 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  <Insert Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

E. Service:  Sanitary waste piping where heat tracing is installed.

1. Operating Temperature:  2 to 38 deg C (35 to 100 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

F. Service:  Condensate drain piping from cooling equipment.

1. Operating Temperature:  2 to 24 deg C (35 to 75 deg F).

2. Insulation Material:  [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness:  <Insert Thickness>

4. Field-Applied Jacket:  None.

5. Vapor Retardant Required:  Yes.

6. Finish:  [Painted] [None].

G. Service:  Exposed sanitary drains and domestic water supplies and stops for fixtures for the disabled.

1. Operating Temperature:  2 to 49 deg C (35 to 120 deg F).

2. Insulation Material:  [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness:  <Insert Thickness>

4. Field-Applied Jacket:  PVC P-trap and supply covers.

5. Vapor Retardant Required:  No.

6. Finish:  [Painted] [None].

H. Service:  Chilled-water supply and return.

1. Operating Temperature:  2 to 24 deg C (35 to 75 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

I. Service:  Refrigerant suction and hot-gas piping.

1. Operating Temperature:  2 to 10 deg C (35 to 50 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

J. Service:  Condenser-water supply and return.

1. Operating Temperature:  10 to 40 deg C (50 to 105 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

K. Service:  Heating water supply and return.

1. Operating Temperature:  38 to 93 deg C (100 to 200 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

L. Service:  Steam and steam condensate.

1. Operating Temperature:  232 deg C (450 deg F) and lower.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

M. High-temperature heating water supply and return.

1. Operating Temperature:  2093 deg C (0 deg F) and higher.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

N. Service:  Process cold water.

1. Operating Temperature:  <Insert Temperature Range>

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

O. Service:  Diesel or natural-gas-fueled engine coolant.

1. Operating Temperature:  2 to 115 deg C (35 to 240 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

P. Service:  Diesel- or natural-gas-fueled engine exhaust.

1. Operating Temperature:  454 deg C (850 deg F) and lower.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

3.15 EXTERIOR INSULATION APPLICATION SCHEDULE

A. This application schedule is for aboveground insulation outside the building.  Loose-fill insulation, for belowground piping, is specified in Division 2 piping distribution Sections.

B. Service:  Domestic hot, cold and re-circulated hot water.

1. Operating Temperature:  15 to 82 deg C (60 to 180 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

C. Service:  Storm water.

1. Operating Temperature:  0 to 38 deg C (32 to 100 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Cast Iron] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel][None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

D. Service:  Refrigerant suction.

1. Operating Temperature:  2 to 10 deg C (35 to 50 deg F).

2. Insulation Material:  [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

E. Service:  Chilled-water supply and return.

1. Operating Temperature:  2 to 24 deg C (35 to 75 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

F. Service:  Condenser-water supply and return.

1. Operating Temperature:  10 to 35 deg C (50 to 95 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

G. Service:  Heating water supply and return.

1. Operating Temperature:  38 to 104 deg C (100 to 220 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Flexible elastomeric] [Polyolefin] [Closed-cell phenolic foam].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

H. High-temperature heating water supply and return.

1. Operating Temperature:  22104 deg C (0 deg F) and higher.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket] [Calcium silicate].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

I. Service:  Steam and steam condensate.

1. Operating Temperature:  232 deg C (450 deg F) and lower.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. [Steel] [Copper] Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

J. Service:  Diesel-and natural-gas-fueled engine coolant.

1. Operating Temperature:  2 to 115 deg C (35 to 240 deg F).

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

K. Service:  Diesel- and natural-gas-fueled engine exhaust.

1. Operating Temperature:  454 deg C (850 deg F) and lower.

2. Insulation Material:  [Cellular glass, with jacket] [Cellular glass, without jacket].

3. Insulation Thickness:  Apply the following insulation thicknesses:

Insert additional subparagraphs below if more size ranges are required.  Select or insert pipe material to suit Project.

a. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

b. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

c. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

d. Steel Pipe, <Insert Pipe Size Range>:  <Insert Insulation Thickness>

4. Field-Applied Jacket:  [Aluminum] [Stainless steel] [None].

5. Vapor Retardant Required:  [Yes] [No].

6. Finish:  [Painted] [None].

END OF SECTION 15083

PIPE INSULATION
15083 - 1

