Copyright 2000 AIA
GSA VERSION MASTERSPEC(
06/00 (GSA 03/03)


Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division .

SECTION 15519 - ELECTRIC BOILERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, factory-fabricated and -assembled electric boilers, trim, and accessories for generating [hot water] [steam].

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Equipment Insulation" for insulation materials and application for pumps, tanks, hydronic specialties, and other equipment.

2. Division 15 Section "Pipe Insulation" for insulation for piping systems.

3. Division 15 Section “Basic Materials and Methods” for additional material specifications.

4. Division 15 Section “Building Automation Systems” for additional control related equipment.

5. Division 15 Section “Temperature Controls” for additional control related requirements.

6. Division 15 Section “Testing, Adjusting, and Balancing” for additional related requirements.

7. Division 15 Section “Operations and Maintenance” for additional related requirements.

1.3 DEFINITIONS

A. k:
Thousand (1000) units

B. M:
Million (1,000,000) units

1.4 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

Signed and sealed Shop Drawings are necessary only for very large boilers.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other Work.[ Shop Drawings shall be signed and sealed by a qualified professional engineer.]

Retain subparagraphs below if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

1. For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

2. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

Retain subparagraph below if equipment includes wiring.

3. Wiring Diagrams:  Detail power, signal, and control wiring.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls" and with seismic-related requirements in Parts 2 and 3 of this Section.

C. Manufacturer Seismic Qualification Certification:  Submit certification that electric boiler, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when anchored to a concrete base.  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Edit the following to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Optional text is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

Retain first paragraph below for steam boilers operating at more than 15 psig (104 kPa) or hot-water boilers operating at more than 160 psig (1100 kPa) or 250 deg F (120 deg C).

E. ASME Stamp Certification and Report:  Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

F. Startup service reports.

G. Operation and Maintenance Data:  For electric boilers to include in emergency, operation, and maintenance manuals.

H. Warranties:  Special warranties specified in this Section.

1.5 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of electric boilers and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain first paragraph below for boilers that operate at more than 15 psig (104 kPa).

C. ASME Compliance:  Fabricate and label electric boilers to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

D. NFPA Compliance:  Design and fabricate electric boilers to comply with NFPA 70, "National Electrical Code," Article 424, Paragraphs G and H.

E. UL Compliance:  Test electric boilers to comply with UL 834, "Heating, Water Supply, and Power Boilers--Electric."

1.6 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace pressure vessels of electric boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

B. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Acme Engineering Products, Inc.

2. Bryan Steam Corporation.

3. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

4. Fulton Boiler Works, Inc.

5. Harsco Corp.; Patterson-Kelley Co./a Harsco Co.

6. Lattner Boiler Manufacturing.

7. Lochinvar Corp.

8. PRECISION Boilers, LLC.

9. PVI Industries Inc.

10. RECO USA.

11. Reimers Electra Steam, Inc.

12. <Insert manufacturer's name.>

2.2 PACKAGED ELECTRIC BOILERS

A. Description:  Factory-fabricated, -assembled, and -tested electric boiler with trim and controls necessary to generate [hot water] [steam].

B. [Water] [Steam]-Pressure Rating:  [15 psig (104 kPa)] [60 psig (420 kPa)] [125 psig (860 kPa)] <Insert psig (kPa)>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate base and attachment to pressure vessel with reinforcement strong enough to resist boiler movement during a seismic event when boiler base is anchored to building structure.

Delete paragraph and subparagraphs below if characteristics and capacities are scheduled on Drawings.

D. Boiler Characteristics and Capacities:

1. Heating Medium:  [Hot water] [Steam].

2. Maximum Pressure Rating:  [15 psig (104 kPa)] [60 psig (420 kPa)] [125 psig (860 kPa)] <Insert psig (kPa)>.

Retain subparagraph above for steam boilers and below for hot-water boilers.

3. Maximum Design Pressure Rating:  [160 psig (1100 kPa)] <Insert psig (kPa)>.

Retain two subparagraphs below for steam boilers.

4. Operating Pressure:  <Insert psig (kPa).>

5. Steam Flow Rate:  <Insert lb/h (kg/s).>

Retain first four subparagraphs below for hot-water boilers.

6. Entering-Water Temperature:  <Insert deg F (deg C).>

7. Leaving-Water Temperature:  <Insert deg F (deg C).>

8. Water Flow Rate:  <Insert gpm (L/s).>

9. Maximum Pressure Drop:  <Insert psig (kPa).>

10. Water Capacity:  <Insert gal. (L).>

Retain one of two subparagraphs below for rating methods.

11. Output Capacity:  <Insert MBh (kW).>

12. Equivalent Direct Radiation:  <Insert EDR (W).>

2.3 ELECTRIC BOILER COMPONENTS

A. Pressure Vessel:  [Carbon-steel] [Cast-iron] pressure vessel mounted on structural-steel base.

B. Nozzles:  Flanges for [water inlet and outlet] [steam outlet] and heating element inserts; threaded connections for trim and controls.

C. Insulation:  [One layer] [Two layers] of minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick glass-fiber insulation.

D. Jacket:  Sheet metal casing with [baked-enamel] [powder-coated] protective finish and removable panels with snap-in or interlocking closures for access to pressure vessel.

E. Lifting Lugs:  Welded to pressure vessel, extending above jacket.

F. Heating Elements:  [Copper] [Incoloy]-sheathed, replaceable electric-resistance element, rated 20 kW maximum, with maximum [50 W/sq. in. (7.7 W/sq. cm)] [75 W/sq. in. (11.5 W/sq. cm)] over heat-transfer length.

G. Mounting base to secure boiler to concrete base.

2.4 HOT-WATER BOILER TRIM

Delete this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

A. Include devices sized to comply with  ANSI B31.9, Building Services Piping."

Retain first paragraph below if using modulating sequence of elements.

B. Aquastat Controllers:  Operating auto-reset high limit.

C. Safety Relief Valve:  ASME rated.  [30 psig (210 kPa)] [45 psig (310 kPa)] [75 psig (517 kPa)] <Insert psig (kPa)>.

Delete subparagraph below if capacities are scheduled on Drawings.

1. Pressure Setting:  <Insert psig (kPa).>

D. Boiler Air Vent:  [Automatic] [Manual].

E. Dip-tube in water outlet.

F. Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end gate valve.

Retain paragraph and subparagraphs below if expansion tank is a component of electric boiler.  Coordinate with Division 15 Section "Hydronic Piping."

G. Expansion Tank:  Welded carbon steel, rated for operating pressure and temperature or minimum 125-psig (860-kPa) working pressure and 240 deg F (115 deg C) operating temperature.  Separate air charge from system water to maintain design expansion capacity by a flexible butyl-rubber bladder securely sealed into tank.  Include hose-end gate drain valve, pressure gage with minimum 3-inch (75-mm) dial, and air-charging fitting.  Factory fabricate and test tank with taps installed and labeled according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Delete first two subparagraphs below if capacities are scheduled on Drawings.

1. Tank Volume:  <Insert gal. (L).>

2. Acceptance Volume:  <Insert gal. (L).>

3. Charging Pressure:  <Insert psig (kPa).>

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic-water heaters.

H. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of pressure vessel and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges and according to ASME B16.24 for copper and copper-alloy flanges.

Delete four subparagraphs below if capacities are scheduled on Drawings.

3. Minimum Water Flow:  <Insert gpm (L/s).>

4. Maximum Pressure Drop:  <Insert psig (kPa).>

5. Entering-Water Temperature:  <Insert deg F (deg C).>

6. Leaving-Water Temperature:  <Insert deg F (deg C).>

2.5 STEAM BOILER TRIM

Delete this Article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain paragraph below if using modulating sequence of elements.

B. Pressure Controllers:  Operating auto-reset high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of electric boiler.  Coordinate with Division 15 Section "Steam and Condensate Piping."

C. Safety Relief Valve:

1. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Delete first subparagraph below if capacities are scheduled on Drawings.

a. Pressure Setting:  <Insert psig (kPa).>

2. Bronze Safety Valves:  Class 250, forged copper-alloy disc; fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage:  Minimum 3-1/2-inch (89-mm) diameter, 0- to 30-psig (0- to 210-kPa) range.

E. Water Column:  Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves:  Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves:  Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.[ Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]

H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle.  Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Factory-installed stop-check valve and stop valve at boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating stop-check valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic-water heaters.

J. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of pressure vessel and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges and according to ASME B16.24 for copper and copper-alloy flanges.

Delete four subparagraphs below if capacities are scheduled on Drawings.

3. Minimum Water Flow:  <Insert gpm (L/s).>

4. Maximum Pressure Drop:  <Insert psig (kPa).>

5. Entering-Water Temperature:  <Insert deg F (deg C).>

6. Leaving-Water Temperature:  <Insert deg F (deg C).>

2.6 ELECTRICAL COMPONENTS

A. Electrical Enclosures:  NEMA 250, Type 1 ventilated enclosure with hinged door and key-locking handle.

B. Electrical Circuits:  48 A, maximum.

C. Electrical Connectors:  Mechanical lugs bolted to copper bus bars or distribution blocks with pressure connectors.

D. Fuses:  NEMA FU 1, Class J or K5; 60 A, maximum.

E. Contactors:  3-pole magnetic contactors, listed for 500,000 cycles at full load.

F. Factory-wired internal control devices and heating elements.

2.7 SAFETY CONTROLS

A. Description:  To maintain safe operating conditions, safety controls limit the operation of boiler.

In first subparagraph below, retain "pressure" option for steam boiler and "temperature" option for hot-water boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops boiler if operating conditions rise above set point or maximum boiler design [pressure] [temperature].

2. Nonfused, interlocking disconnect switch.

3. Door interlock switch.

In first subparagraph below, retain first option for steam boilers and second option for hot-water boilers.

4. Low-Water Cutoff Switch:  [Float and electronic probe] [Electronic probe] shall prevent boiler operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

5. Alarm Bell:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

2.8 BOILER OPERATING CONTROLS

In paragraph below, retain the "existing" option if boilers are installed in existing conditions and must be integrated into existing control systems.

A. Boiler operating controls shall be integrated into and interface with [existing] control system specified in Division 15 Section(s) ["Building Automation Systems"] [and] ["Temperature Controls."]
Coordinate with Division 15 Section(s) ["Building Automation Systems"] [and] ["Temperature Controls."]
B. Boiler operating controls shall be microprocessor-based and shall include the following devices and features:

1. Power and control electrical connections shall be supplied through the control panel.

2. Control Transformer:  115 V.

3. Step controller.

4. Recycling relay returns controller to off position after power failure.

5. Multistage thermostat.

6. Control circuit switch.

7. Pilot lights for each step.

8. Supply-voltage indicator.

Retain subparagraph below for steam boilers.

9. Operating Level Control:  Factory wired and mounted to cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain first subparagraph for steam boilers; second or third, for hot-water boilers.

10. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control element sequence controller to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

11. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control element sequence controller to maintain space temperature in response to thermostat with heat anticipator located in heated space.

12. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control element sequence controller to reset supply-water temperature inversely with outside-air temperature.  At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

Retain subparagraph below with any of three sequences retained above.

a. Include automatic, alternating-operation sequence for multiple boilers.

Retain below if boiler controls interface with building management system.

C. Building Management System Interface:  Factory-installed microprocessor-based hardware and software to enable building automation system to monitor and control the boiler and display boiler status and alarms.  Control devices used to measure, monitor, and control the boiler operations and functions, and interface connections shall be [BACnet compatible] [LONtalk compatible] [electronic to match existing]  Compatibility shall be without the use of gateways or proprietary devices.

1. The interface between the boiler controls and building automation system shall enable the building automation system to read, as separate and discreet points, significant values and alarms on the boiler.  Use of a single set of contacts to send an alarm is not acceptable.  Interface shall allow a minimum of the the following inputs, outputs, and functions.

a. Boiler operating and alarm status.

b. [Steam] [Water] pressure.

Retain subparagraph below for water boilers.

c. Entering and leaving water temperatures.

d. Boiler tripped by high/low pressure, temperature, fuel pressure, or water level.

e. Loss of electrical power.

f. Boiler [steam] [water] flow.

2.9 SOURCE QUALITY CONTROL

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code:  Section 1, for high-pressure boilers and Section IV, for low-pressure boilers.

B. Hydrostatic Test:  Factory test assembled boiler including hydrostatic test.

Retain below if Owner wants to witness source quality-control testing.

C. Allow Owner access to source quality-control testing of electric boilers.  Notify Contracting Officer 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Examine mechanical spaces, including required space for element removal, for suitable conditions where boilers will be installed.  Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Revise first paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

B. Concrete Bases:  Anchor boilers to concrete base.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Cast-in-place concrete materials and placement requirements are specified in Division 3.

C. Install electrical devices furnished with boiler but not specified to be factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

C. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

D. Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 15 Section "Steam and Condensate Piping" or "Hydronic Piping."

E. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

F. Install piping adjacent to boiler to allow service and maintenance.

G. Ground equipment according to Division 16 Section "Grounding and Bonding."

H. Connect wiring according to Division 16 Section "Conductors and Cables."

I. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to test, inspect, and adjust boiler components and equipment installation and to perform startup service.

B. Perform installation and startup checks according to manufacturer's written instructions.

C. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

D. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

E. Adjust initial temperature set points.

F. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

G. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to site outside normal occupancy hours for this purpose, without additional cost.

H. Prepare written report that documents testing procedures and results.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain electric boilers.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15519

ELECTRIC BOILERS
15519 - 13

