Copyright 1999 AIA
GSA VERSION MASTERSPEC
3/99 (GSA 03/04)

Copyright 1999 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15525 - DEAERATORS
-------------------------------------------------------------------------------------------------------------------------------

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

-------------------------------------------------------------------------------------------------------------------------------

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, factory assembled deaerators.

1.3 DEFINITIONS

A. Transfer Pump:  Pump to move feedwater from the surge tank to the deaerator.

B. Feedwater Pump:  Pump to move feedwater from the deaerator to the boiler.

1.4 PERFORMANCE REQUIREMENTS

A. Operating Pressure Range:  From 14 to 104 kPa (2 to 15 psig).

B. Resultant Oxygen Content:  Not more than 0.005 cc/L for a range of conditions between 0 and 100 percent of full load.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph above for tray-type units and below for spray-type units.

-------------------------------------------------------------------------------------------------------------------------------

C. Resultant Oxygen Content:  Not more than 0.03 cc/L for a range of conditions between 50 and 100 percent of full load.

1.5 SUBMITTALS

A. Product Data:  Include rated capacity, furnished specialties, and accessories for each model.

B. Shop Drawings:  Signed and sealed by a qualified professional engineer; include plans, elevations, sections, details, and attachments to other Work.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if products are required to withstand specific design loads and Architect has either delegated design responsibility to Contractor or wants to review structural data as another means for verifying product's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section, "Quality Requirements."

-------------------------------------------------------------------------------------------------------------------------------

1. For installed products indicated to comply with design loads, include structural analysis data.

2. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing deaerator bases.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if equipment includes wiring.

-------------------------------------------------------------------------------------------------------------------------------

3. Wiring Diagrams:  Power, signal, and control wiring.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration Controls and Seismic Restraints" and with seismic-related requirements in Part 2 of this Section.

-------------------------------------------------------------------------------------------------------------------------------

C. Manufacturer Seismic Qualification Certification:  Submit certification that deaerators will withstand seismic forces as indicated in Division 15 Section, "Mechanical Vibration Controls and Seismic Restraints."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

-------------------------------------------------------------------------------------------------------------------------------Edit the subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

-------------------------------------------------------------------------------------------------------------------------------

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified." [and the unit will be fully operational after the seismic event."]
2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Field Test Reports:  Written reports specified in Part 3.

E. Maintenance Data:  For deaerators to include in maintenance manuals specified in Division 1.

1.6 QUALITY ASSURANCE

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Revise to identify specific proprietary system or indicate on Drawings.  Correlate with Division 1 requirements.

-------------------------------------------------------------------------------------------------------------------------------

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of unit and are based on the specific system indicated.  Other manufacturers' products complying with requirements may be considered.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Protect flanges, pipe openings, nozzles, bearings, and couplings from damage during shipping and storage.

B. Comply with manufacturer's written rigging instructions.

C. Deliver deaerators as factory assembled units with protective crating and covering.

1.8 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

1.9 EXTRA MATERIALS

-------------------------------------------------------------------------------------------------------------------------------Extra materials may not be allowed for publicly funded projects.

-------------------------------------------------------------------------------------------------------------------------------

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

-------------------------------------------------------------------------------------------------------------------------------Revise below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Gaskets:  Furnish [one] <Insert number> replacement gasket[s] for each gasketed opening.

2. Gauge Glass:  Furnish [one] <Insert number> replacement glass[es] for each gauge glass.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Ambassador Heat Transfer Company.

2. Bethlehem Corp. (The).

3. Bryan Steam Corp.

4. Burnham; Kewanee Manufacturing Co., Inc., Div.

5. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

6. Cochrane, Inc.; a Crane Co. Company.

7. Deaerator Design.

8. Dixon Boiler Works.

9. Donlee Technologies, Inc.; York-Shipley Div.

10. Eastern Industrial Products, Inc.; Smith-Koch, Inc., Div.

11. Ecodyne Ltd.; Graver Water Conditioning Subsidiary.

12. Enpro, Inc.

13. Industrial Boiler Co., Inc.

14. Industrial Steam; Custom Steam and Pressure Vessel Systems.

15. International Boiler Works Co. (The).

16. Kansas City Deaerator Company.

17. Lockwood Products, Inc.; Sub. of John L. Underwood Co., Inc.

18. Nationwide Boiler, Inc.

19. PVI Industries, Inc.

20. Sellers Engineering Company.

21. Skidmore.

22. Sterling Deaerator Co.

23. U.S. Deaerator Co.

24. Wabash Power Equipment Co.

2.2 CONFIGURATION

-------------------------------------------------------------------------------------------------------------------------------Retain one of the paragraphs below with applicable configuration, or edit to suit Project.  See "Product Selection Considerations" Article in the Evaluations for discussion about spray type versus tray type units.

-------------------------------------------------------------------------------------------------------------------------------

A. [Horizontal] [Vertical], [spray] [tray], single compartment deaerator[, and a separate packaged surge tank with transfer and feedwater pumps and controls to supply feedwater to the boiler].

B. [Horizontal] [Vertical], [spray] [tray], two compartment deaerator.  One compartment for deaeration and one for surge volume, each with its own transfer and feedwater pumps and controls.

C. [Horizontal] [Vertical], [spray] [tray] deaerator and separate surge tank, both mounted on the same factory fabricated stand with necessary transfer and feedwater pumps and controls.

2.3 CAPACITIES AND CHARACTERISTICS

A. Capacity:  Capable of raising temperature of condensate and makeup water to within 1.6 deg C (3 deg F) of saturated steam temperature.

B. Minimum Working Pressure:  345 kPa (50 psig).

C. Capacity.

-------------------------------------------------------------------------------------------------------------------------------

Delete subparagraphs below which are including in Drawings.

-------------------------------------------------------------------------------------------------------------------------------

1. Capacity:  <Insert Number> kg/h.

2. Storage minutes to overflow:  <Insert Number> minutes.

3. Tank size:  <Insert Number> mm diameter by <Insert Number> mm long.

2.4 FABRICATION

A. Material Thickness:  Add 1.8 mm (0.07 inch) corrosion allowance to ASME required material thicknesses.

B. Materials:  Fabricate components, that come in contact with water that has not been deaerated, using stainless steel.
C. Adjustable Spray Valve:  Stainless steel internal parts, with automatic and manual vent valves.  Arrange spray valves for counterflow of steam and condensate and so corrosive gases being vented do not contact deaerator's head or shell.

D. Storage Tank:  345 kPa (50 psig) minimum working pressure, with a manhole 305 by 414 mm (12 by 16 inches) minimum.

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.  Do not specify both electrolyte anode and a lining.

-------------------------------------------------------------------------------------------------------------------------------

1. Interior Finish:  [Galvanized][Epoxy coated][with electrolyte corrosion-inhibiting anode].

2. Vessels 900 mm (36 inches) and smaller in diameter shall be factory insulated with a minimum of 38 mm (1 1/2 inch) thick, mineral-fiber insulation having a minimum of 0.7 mm (0.0269 inch) thick steel jacket.  For larger vessels, increase insulation thickness to a minimum of 50 mm (2 inches).

E. Factory Furnished Pipe, DN 80 (NPS 3) and Smaller:  ASTM A 53, Type S (seamless), Grade A, Schedule  [40] [80], with threaded joints and malleable iron fittings of class to match pressure rating of pipe.

F. Factory Furnished Pipe Larger Than DN 80 (NPS 3):  ASTM A 53, Type E (electric resistance welded), Grade A, Schedule  [40] [80], with welded joints and malleable iron fittings of class to match pressure rating of pipe.

G. Packaged deaerator shall include the following accessories:

-------------------------------------------------------------------------------------------------------------------------------Retain accessories below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Inlet strainer.

2. Lifting eyes.

3. Companion flanges.

4. Pump discharge check valve.

5. Pump discharge pressure gage graduated in both pounds force per square inch and kilopascals.

6. Pump discharge relief valve with orifice plate union for minimum flow for constant running pumps.

7. Pump suction isolation valve.

8. Pump discharge isolation valve.

9. Makeup Water:  [Inlet regulating valve with stainless steel float] [Electric, pilot operated, solenoid valve for field mounting with water level controller factory mounted on tank].  Provide three valve bypass and inlet strainer for field mounting.

10. Steam Pressure Reducing Valve(s):  Sized to reduce boiler outlet pressure to the deaerator design pressure.

11. Overflow Drain:  Sized to relieve full capacity at operating pressure.

12. Safety Valve(s):  ASME labeled and sized to relieve full capacity of pressure reducing valve.

13. Alarms:  High water level alarm switch, low water level alarm switch, and one alarm bell with silence switch.

14. Vent condenser.

15. Vents:  Manual and automatic vent valves with vacuum breaker.

16. Meters and Gages:  Full height, water level, gauge glass and stop valve set.  [Liquid filled] [Dial type] thermometer and pressure gauge graduated in both pounds force per square inch and kilopascals.

H. Support Frame:  Welded structural steel frame for supporting tank and pumps.  Weld to storage tank before ASME pressure testing and labeling.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if Project is located in a seismic area.

-------------------------------------------------------------------------------------------------------------------------------

1. Fabricate support frame with bracing adequate for seismic forces according to authorities having jurisdiction and to allow installation by anchoring deaerators to floor only.

I. Feedwater Pump:  Cast iron, [flange] [base ]mounted volute; with [bronze] [stainless steel], [multi stage centrifugal] [turbine] impeller, renewable bronze case ring, and stainless steel shaft for [intermittent] [continuous] service.
1. Seals:  Mechanical, suitable for 121 deg C (250 deg F).

2. Pump Motor:  [Vertical] [Horizontal], [open dripproof] [totally enclosed fan cooled], [close] [flexible] coupled to pump.

J. Feedwater Pump Control Panel:  Unit mounted, factory wired, and including the following:

1. NEMA 250, Type 2 enclosure.

2. Compliant with UL standards.

3. Combination magnetic starters for each pump, with three overload relays, [fused disconnect switch] [circuit breaker], and interlocking cover.

4. [Manual] [Automatic electric] lead/lag switch and test push button for each pump.

5. Numbered terminal block.

6. Removable control mounting plate.

7. Pilot lights to indicate pump is running.

8. Alarm with bell and silence switch.

9. Elapsed time run meter, graduated in hours.

10. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.

11. Fusible, control circuit transformer if motor voltage exceeds 130 V ac.

12. Control Sequence:  Lead pump shall run continuously while boiler water level control modulates feedwater control valve.  Lag pump shall start on loss of discharge water pressure for 60 seconds or more.  Alarm shall sound when lag pump starts.

-------------------------------------------------------------------------------------------------------------------------------A surge tank with modulating makeup to the deaerator should be used if the steam system extends beyond the boiler room.

-------------------------------------------------------------------------------------------------------------------------------

2.5 SURGE TANK

A. Description:  Factory assembled and tested unit consisting of a condensate receiver, transfer pumps, and controls.

B. Compliance with ASME standards.

C. Accessories shall include the following:

1. [Liquid filled] [Dial type] thermometer graduated in both Fahrenheit and Celsius scales.

2. Gage glass with stops at top and bottom.

3. Inlet strainer.

4. Lifting eyes.

5. Companion flanges.

6. Pump discharge check valve.

7. Pump discharge pressure gauge, graduated in both pounds force per square inch and kilopascals.

8. Pump discharge relief valve with orifice plate union for minimum flow for constant-running pumps.

9. Pump suction isolation valve.

10. Pump discharge isolation valve.

11. Factory Furnished Pipe, DN 50 (NPS 2) and Smaller:  ASTM A 53, Type S (seamless), Grade A, Schedule  [40] [80], with threaded joints and malleable iron fittings of class to match pressure rating of pipe.

12. Factory Furnished Pipe, DN 65 (NPS 2 1/2) and Larger:  ASTM A 53, Type E (electric resistance welded), Grade A, Schedule  [40] [80], with welded joints and malleable iron fittings of class to match pressure rating of pipe.

D. Tank Material:  [Close grain cast iron] [Welded steel].

-------------------------------------------------------------------------------------------------------------------------------Surge tank liners are not subject to the higher temperature inside deaerators and do not deteriorate prematurely.

-------------------------------------------------------------------------------------------------------------------------------

1. Liner:  Epoxy, a minimum of 2 coats totaling 250 to 300 micrometers (10 to 12 mil) film thickness.

2. Arrangement:  [Recessed below floor] [Floor mounted].

3. Support Frame:  Welded, structural steel frame for supporting tank.  Weld to tank before ASME pressure testing and labeling.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if Project is located in a seismic area.

-------------------------------------------------------------------------------------------------------------------------------

4. Fabricate support frame with bracing adequate for seismic forces according to authorities having jurisdiction and to allow installation by anchoring deaerators to floor only.

E. Capacity.

-------------------------------------------------------------------------------------------------------------------------------Delete subparagraphs below which are included in Drawings.

-------------------------------------------------------------------------------------------------------------------------------

1. Capacity:  <Insert Number> kg/h.

2. Storage minutes to overflow:  <Insert Number> minutes.

-------------------------------------------------------------------------------------------------------------------------------Retain one of the two paragraphs and associated subparagraphs below and edit for desired pump construction.

-------------------------------------------------------------------------------------------------------------------------------

F. Transfer Pump:  Vertical, flange mounted, close coupled, [single stage] [multistage], radially split case centrifugal pump; rated for 1207 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Seals:  Mechanical.

3. Motor:  

a. [Open dripproof] [Totally enclosed fan cooled].  

b. Efficiency: NEMA Premium

c. Comply with requirements in Division 15 Section "Motors."

G. Transfer Pump:  Horizontal, base mounted, [single stage] [multistage], radially split case centrifugal pump; rated for 1207 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Coupling:  [Close] [Flexible].

3. Seals:  Mechanical.

4. Motor:  [Open dripproof] [Totally enclosed fan cooled].  Comply with requirements in Division 15 Section "Motors."

H. Transfer Pump Control Panel:  Unit mounted, factory wired, and including the following:

1. NEMA 250, Type 2 enclosure.

2. Compliant with UL standards.

3. Combination magnetic starters for each pump, with three overload relays, [fused disconnect switch] [circuit breaker], and interlocking cover.

4. Numbered terminal block.

5. Removable control mounting plate.

6. Electric alternator for duplex units.

7. Pilot lights to indicate pump is running.

8. Alarm with bell and silence switch.

9. Elapsed time run meter, graduated in hours.

10. Fusible, control circuit transformer if motor voltage exceeds 130 V ac.

11. Native BACnet , ASHRAE 135, microprocessor controls to be factory installed, supplied by Division 15 Section "Building Automation System" and “Temperature Controls”.
-------------------------------------------------------------------------------------------------------------------------------Retain only one of the three options below.  Select first for simplex (single) transfer system, second for duplex pump units with operating and standby pumps, and third for modulating, water level control valve.  Third is preferred.

-------------------------------------------------------------------------------------------------------------------------------

I. Transfer Pump Control Sequence:  [Deaerator water level controller starts simplex unit with momentary test push button] [Deaerator water level controller starts lead pump; alternator switches lead and lag pumps after each cycle] [Lead pump runs continuously; deaerator water level controller modulates water level control valve; electric interlock with deaerator control starts lead pump when deaerator starts].

2.6 FACTORY INSULATION

-------------------------------------------------------------------------------------------------------------------------------Factory applied insulation and jacket should be limited to assemblies less than 3.7 meters (12 feet) in height as shipping methods risk damage.

-------------------------------------------------------------------------------------------------------------------------------

A. Insulation.

1. Type:  fiberglass blanket.

2. Thickness:  50 mm (2 inches).

3. Density:  24 kg/cu. m (1-1/2 lb/cu. ft.)<Insert Number>.

B. Resistance:  R-3.

C. Jacket:  0.75 mm (22 gauge) steel.

2.7 FACTORY FINISHES

-------------------------------------------------------------------------------------------------------------------------------Specify field painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field applied coats.

-------------------------------------------------------------------------------------------------------------------------------

A. Manufacturer's standard prime coat finish ready for field painting.

-------------------------------------------------------------------------------------------------------------------------------Edit below to include custom colors.  Coordinate custom color requirements with sample submittal requirements.

-------------------------------------------------------------------------------------------------------------------------------

B. Manufacturer's standard paint applied to factory assembled and tested unit before shipping.

2.8 SOURCE QUALITY CONTROL

A. Fabricate and label deaerator tanks according to ASME Boiler and Pressure Vessel Code, Section VIII, "Pressure Vessels," Division 1.

-------------------------------------------------------------------------------------------------------------------------------Select ASME B31.1 for systems operating at more than 15 psig (104 kPa) and ASME B31.9 for systems operating at 15 psig (104 kPa) and less.

-------------------------------------------------------------------------------------------------------------------------------

B. Factory install and test piping that connects transfer and feedwater pumps to tanks according to ASME  [B31.1, "Power Piping] [B31.9, "Building Services Piping]."

C. Test performance and certify test results on packaged deaerator units, according to ASME PTC 12.3, Deaerators, before shipping to Project.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine equipment foundation and anchor bolt locations for compliance with requirements for installation and other conditions affecting performance.

B. Examine rough in for condensate return piping systems to verify actual locations of piping connections before equipment installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install deaerators level and plumb.

B. Install deaerators to permit access for service and maintenance.

C. Support piping independent of pumps.

D. Install base mounted pumps on concrete base with grouted base frame.

E. Install all parts and materials not factory installed.

F. Extend overflow drains to floor drains.

G. Extend vent piping to outside and terminate with manufacturer approved cap furnished with deaerator.

H. Install piping adjacent to machine to allow service and maintenance.

3.3 CONNECTIONS

-------------------------------------------------------------------------------------------------------------------------------Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

-------------------------------------------------------------------------------------------------------------------------------

A. Steam and condensate piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect steam and condensate piping to tank tappings with shutoff valves and unions or flanges at each connection.

C. Connect condensate drains, pump-discharge piping, vents, overflow drains, makeup water, steam supply, and cooling water piping.

D. Ground equipment.

E. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

F. Connect to Building Automation System.

3.4 FIELD QUALITY CONTROL

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if manufacturer should perform commissioning.  Coordinate with Part 1 requirement for report submittal.

-------------------------------------------------------------------------------------------------------------------------------
A. Manufacturer's Field Service:  Engage a factory-authorized service representative, specified in Section 01700 “Execution Requirements”, to perform the following:

1. Inspect field-assembled components and equipment installation, including piping and electrical connections, for compliance with requirements.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3. Verify bearing lubrication.

4. Verify proper motor rotation.

5. Test Reports:  Prepare a written report to record the following:

a. Test procedures used.

b. Test results that comply with requirements.

c. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

B. Replace malfunctioning controls and equipment.

3.5 ADJUSTING AND CLEANING

A. Adjust initial temperature and pressure set points.

B. Set field-adjustable switches and circuit-breaker trip ranges.

C. Clean strainers.

3.6 STARTUP SERVICE

-------------------------------------------------------------------------------------------------------------------------------Delete paragraph below if factory authorized service representative is not required.

-------------------------------------------------------------------------------------------------------------------------------

A. Engage a factory-authorized service representative to perform startup service.  Complete installation and startup checks according to manufacturer's written instructions and do the following:

1. Set deaerator makeup water-level controls.

2. Verify bearing lubrication.

3. Verify proper motor rotation.

4. Start feedwater and transfer pumps according to manufacturer's written instructions.

3.7 DEMONSTRATION

A. Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”, to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] <Insert Number > hours to adjust, operate, and maintain deaerators.

1. Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment.

2. Review data in maintenance manuals.  Refer to Division 1 Section "Closeout Procedures."

-------------------------------------------------------------------------------------------------------------------------------Delete subparagraph above or below depending on which Section is retained in Division 1.

-------------------------------------------------------------------------------------------------------------------------------

3. Review data in maintenance manuals.  Refer to Division 1 Section, "Operation and Maintenance Data."

4. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 15525

DEAERATORS
15525 - 7

