Copyright 2000 AIA
GSA VERSION MASTERSPEC
9/00 (GSA 03/04)

Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15550 - BREECHINGS, CHIMNEYS, AND STACKS
-------------------------------------------------------------------------------------------------------------------------------

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

-------------------------------------------------------------------------------------------------------------------------------

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

-------------------------------------------------------------------------------------------------------------------------------Adjust list below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Listed [single] [double] wall [vents] [chimneys].

2. Field fabricated metal breechings[ and chimneys].

3. Listed [grease] [dishwasher] [grease and dishwasher] ducts.

B. Related Sections include the following:

-------------------------------------------------------------------------------------------------------------------------------List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

-------------------------------------------------------------------------------------------------------------------------------

1. Division 15 Section "Draft Control Devices" for induced draft and mechanical fans and motorized and barometric dampers.

1.3 SUBMITTALS

A. Product Data:  For the following:

1. Chimney liners.

2. Type B and BW vents.

3. Type L vents.

4. Special gas vents.

5. Building heating appliance chimneys.

6. Grease ducts.

7. Guy wires and connectors.

B. Shop Drawings:  For vents, breechings, chimneys, and stacks.  Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, methods of field assembly, components, hangers and seismic restraints, and location and size of each field connection.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section, "Quality Requirements."

-------------------------------------------------------------------------------------------------------------------------------

2. For installed products indicated to comply with design loads, include calculations required for selecting seismic restraints and structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

-------------------------------------------------------------------------------------------------------------------------------

C. Welding certificates.

D. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain listed system components through one source from a single manufacturer.

-------------------------------------------------------------------------------------------------------------------------------Delete paragraph below if no welding.  Retain "Welding certificates" paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability. 

-------------------------------------------------------------------------------------------------------------------------------

B. Welding:  Qualify processes and operators according to AWS D1.1, "Structural Welding Code - Steel," for hangers and supports and AWS D9.1, "Sheet Metal Welding Code," for shop and field welding of joints and seams in vents, breechings, and stacks.

C. Certified Sizing Calculations:  Manufacturer shall certify venting system sizing calculations.

1.5 COORDINATION

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for chimneys and stacks supported on concrete bases.

-------------------------------------------------------------------------------------------------------------------------------

A. Coordinate size and location of concrete bases.  Cast anchor bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.6 WARRANTY

-------------------------------------------------------------------------------------------------------------------------------Verify available warranties for units and components and insert number below.

-------------------------------------------------------------------------------------------------------------------------------

A. Warranty Period:  [10] [15] [25] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the manufacturers specified.

2.2 LISTED CHIMNEY LINERS

A.  Available Manufacturers:

1. American Metal Products; MASCO Corporation.

2. Deflect-O Corp.

3. Heat-Fab Inc.

4. Industrial Chimney Company.

5. Metal-Fab, Inc.

6. Pringle Power-Vac, Inc.

7. ProTech Systems Inc.

8. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

9. Shook Manufactured Products, Inc.

10. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

11. Tru-Flex Metal Hose Corp.

12. <Insert manufacturer's name.>

-------------------------------------------------------------------------------------------------------------------------------Straight, stainless steel chimney liners can be used for dishwasher exhaust ducts and Type II, commercial kitchen hood exhaust ducts.

-------------------------------------------------------------------------------------------------------------------------------

B. Description:  [Straight] [Corrugated], single wall chimney liner tested according to UL 1777 and rated for 538 deg C (1000 deg F) continuously, or 1150 deg C (2100 deg F) for 10 minutes; with negative or positive flue pressure complying with NFPA 211 and suitable for general usage.

C. Straight Liner Materials:  ASTM A 666, Type [304] [316] stainless steel.

D. Corrugated Liner Materials:  [ASTM A 240/A 240M, Type 321] [ASTM A 240/A 240M, Type 430] [ASTM A 959, Type 29 4C].

E. Accessories:

1. Fittings:  Tees, elbows, increasers, draft hood connectors, metal caps with bird barriers, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar or compatible materials and designs.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below for positive pressure applications.

-------------------------------------------------------------------------------------------------------------------------------

2. Sealant:  Manufacturer's standard high temperature sealant.

3. Insulating Fill:  Manufacturer's standard high temperature insulation fill material in annular space surrounding chimney liner including high temperature, ceramic fiber insulation required to seal chimney at top and bottom.

2.3 LISTED TYPE B AND BW VENTS

A.  Available Manufacturers:

1. American Metal Products; MASCO Corporation.

2. Cleaver-Brooks.

3. FAMCO.

4. Hart & Cooley, Inc.

5. Heat-Fab Inc.

6. Industrial Chimney Company.

7. LSP Products Group, Inc.

8. Metal-Fab, Inc.

9. ProTech Systems Inc.

10. Schebler Co. (The).

11. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

12. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

13. Tru-Flex Metal Hose Corp.

14. Van-Packer Co.

15. <Insert manufacturer's name.>

B. Description:  Double wall metal vents tested according to UL 441 and rated for 248 deg C (480 deg F) continuously for Type B, or 288 deg C (550 deg F) continuously for Type BW; with neutral or negative flue pressure complying with NFPA 211 and suitable for certified gas fired appliances.

C. Construction:  Inner shell and outer jacket separated by at least a 6 mm (1/4 inch) airspace.

D. Inner Shell:  [ASTM B 209M (ASTM B 209), Type 1100 aluminum] [ASTM B 209M (ASTM B 209), Type 3003 aluminum] [ASTM B 209M (ASTM B 209), Type 3105 aluminum] [ASTM A 666, Type 430 stainless steel].

E. Outer Jacket:  [Galvanized] [Aluminized] steel.

F. Accessories:  Tees, elbows, increasers, draft hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent pipe straight sections; all listed for same assembly.

-------------------------------------------------------------------------------------------------------------------------------Retain one of the three terminations below or add type to suit Project.  Use caution because many systems are tested with specific terminations.

-------------------------------------------------------------------------------------------------------------------------------

1. Termination:  Stack cap designed to exclude 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert special type termination.>

2.4 LISTED TYPE L VENT

A.  Available Manufacturers:

1. American Metal Products; MASCO Corporation.

2. FAMCO.

3. Heat-Fab Inc.

4. Industrial Chimney Company.

5. LSP Products Group, Inc.

6. Metal-Fab, Inc.

7. ProTech Systems Inc.

8. Schebler Co. (The).

9. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

10. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

11. Tru-Flex Metal Hose Corp.

12. Van-Packer Co.

13. <Insert manufacturer's name.>

B. Description:  Double wall metal vents tested according to UL 641 and rated for 300 deg C (570 deg F) continuously, or 926 deg C (1700 deg F) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211 and suitable for low heat appliances.

C. Construction:  Inner shell and outer jacket separated by at least a [6 mm (1/4 inch)] [25 mm (1 inch)] [50 mm (2 inch)] [100 mm (4 inch)] airspace filled with high temperature, [ceramic fiber] [mineral wool] insulation.

D. Inner Shell:  ASTM A 666, Type [304] [316] stainless steel.

E. Outer Jacket:  [Galvanized] [Aluminized] [Stainless] steel.

F. Accessories:  Tees, elbows, increasers, draft hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent pipe straight sections; all listed for same assembly.

-------------------------------------------------------------------------------------------------------------------------------Retain one of the terminations below or add type to suit Project.  Use caution because many systems are tested with specific terminations.

-------------------------------------------------------------------------------------------------------------------------------

1. Termination:  Stack cap designed to exclude 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert special type termination.>

2.5 LISTED SPECIAL GAS VENT

A.  Available Manufacturers:

1. Heat-Fab Inc.

2. Metal-Fab, Inc.

3. ProTech Systems Inc.

4. Selkirk Inc.:  Selkirk, Metalbestos and Air Mate.

5. Z-FLEX.

6. <Insert manufacturer's name.>

B. Description:  Double wall metal vents tested according to UL 1738 and rated for 245 deg C (480 deg F) continuously, with positive or negative flue pressure complying with NFPA 211 and suitable for condensing gas appliances.

C. Construction:  Inner shell and outer jacket separated by at least a 13 mm (1/2 inch) airspace.

D. Inner Shell:  ASTM A 959, Type 29 4C stainless steel.

E. Outer Jacket:  [Aluminized] [Stainless] steel.

F. Accessories:  Tees, elbows, increasers, draft hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent pipe straight sections; all listed for same assembly.

-------------------------------------------------------------------------------------------------------------------------------Retain one of the three terminations below or add type to suit Project.  Use caution because many systems are tested with specific terminations.

-------------------------------------------------------------------------------------------------------------------------------

1. Termination:  Stack cap designed to exclude 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert special type termination.>

2.6 LISTED BUILDING HEATING APPLIANCE CHIMNEYS

A.  Available Manufacturers:

1. American Metal Products; MASCO Corporation.

2. Cleaver-Brooks.

3. FAMCO.

4. Hart & Cooley, Inc.

5. Heat-Fab Inc.

6. Industrial Chimney Company.

7. LSP Products Group, Inc.

8. Metal-Fab, Inc.

9. ProTech Systems Inc.

10. Schebler Co. (The).

11. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

12. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

13. Tru-Flex Metal Hose Corp.

14. Van-Packer Co.

15. <Insert manufacturer's name.>

-------------------------------------------------------------------------------------------------------------------------------Retain the three paragraphs below for building heating appliance chimneys.

-------------------------------------------------------------------------------------------------------------------------------

B. Description:  Double wall metal vents tested according to UL 103 and rated for 538 deg C (1000 deg F) continuously, or 926 deg C (1700 deg F) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211 and suitable for dual fuel boilers, oven vents, water heaters, or exhaust for engines.

C. Construction:  Inner shell and outer jacket separated by at least a  [50 mm (1 inch)] [50 mm (2 inch)] [75 mm (3 inch)] [100 mm (4 inch)] annular space [filled with high temperature, ceramic fiber insulation].

D. Inner Shell:  ASTM A 666, Type 316 stainless steel.

-------------------------------------------------------------------------------------------------------------------------------Retain the three paragraphs below for 1400 deg F (760 deg C) chimneys.

-------------------------------------------------------------------------------------------------------------------------------

E. Description:  Double wall metal vents tested according to UL 103 and 959 and rated for 760 deg C (1400 deg F) continuously, or 982 deg C (1800 deg F) for 10 minutes; with positive or negative flue pressure complying with NFPA 211 and suitable for dual fuel boilers, oven vents, water heaters, or exhaust for engines.

F. Construction:  Inner shell and outer jacket separated by at least a [25 mm (1 inch)] [50 mm (2 inch)] [75 mm (3 inch)] [100 mm (4 inch)] annular space filled with high temperature, ceramic fiber insulation.

G. Inner Shell:  ASTM A 666, Type [304] [316] stainless steel.

-------------------------------------------------------------------------------------------------------------------------------Retain the three paragraphs below for Type HT chimneys.

-------------------------------------------------------------------------------------------------------------------------------

H. Description:  Double wall metal vents tested according to UL 103 and rated for 538 deg C (1000 deg F) continuously, or 1150 deg C (2100 deg F) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211 and suitable for fireplaces and other solid fuel burning appliances.

I. Construction:  Inner shell and outer jacket separated by at least a [25 mm (1 inch)] [38 mm (1 1/2 inch)] [50 mm (2 inch)] [100 mm (4 inch)] annular space filled with high temperature, ceramic fiber insulation.

J. Inner Shell:  [ASTM A 666, Type 304] [ASTM A 666, Type 316] [ASTM A 240/A 240M, Type 430] stainless steel.

K. Outer Jacket:  [Galvanized] [Stainless] steel.

L. Accessories:  Tees, elbows, increasers, draft hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent pipe straight sections; all listed for same assembly.

-------------------------------------------------------------------------------------------------------------------------------Retain one of the terminations below or add type to suit Project.  Use caution because many systems are tested with specific terminations.

-------------------------------------------------------------------------------------------------------------------------------

1. Termination:  Stack cap designed to exclude 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert special type termination.>

2.7 LISTED GREASE DUCTS

A.  Available Manufacturers:

1. American Metal Products; MASCO Corporation.

2. FAMCO.

3. Heat-Fab Inc.

4. Industrial Chimney Company.

5. LSP Products Group, Inc.

6. Metal-Fab, Inc.

7. ProTech Systems Inc.

8. Schebler Co. (The).

9. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

10. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

11. Tru-Flex Metal Hose Corp.

12. Van-Packer Co.

13. <Insert manufacturer's name.>

B. Description:  Double wall metal vents tested according to UL 1978 and rated for 260 deg C (500 deg F) continuously, or 1093 deg C (2000 deg F) for 30 minutes; with positive or negative duct pressure and suitable for Type I, commercial kitchen grease duct.

C. Construction:  Inner shell and outer jacket separated by at least a [25 mm (1 inch)] [50 mm (2 inch)] [75 mm (3 inch)] [100 mm (4 inch)] annular space filled with high temperature, ceramic fiber insulation.

D. Inner Shell:  ASTM A 666, Type [304] [316] stainless steel.

E. Outer Jacket:  [Aluminized] [Stainless] steel.

F. Accessories:  Tees, elbows, increasers, hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent pipe straight sections; all listed for same assembly.  Include unique components required to comply with NFPA 96.

2.8 FIELD FABRICATED METAL BREECHINGS AND CHIMNEYS

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for freestanding stacks.  Insert dimensions unless they are indicated on Drawings.

-------------------------------------------------------------------------------------------------------------------------------

A. Fabricate freestanding chimneys according to SMACNA's "Guide for Steel Stack Design and Construction."  Design for minimum <meters (feet)> high and <Insert mm (inches)> in diameter.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for low heat appliances.

-------------------------------------------------------------------------------------------------------------------------------

B. Fabricate breechings and chimneys from ASTM A 569/A 569M hot rolled steel with continuously welded joints, complying with NFPA 211 for minimum metal thickness.

1. Equal to or Less Than 0.099 sq. m. (1.069 sq. ft.) or 356 mm (14 inches) in Diameter:  1.35 mm (0.053 inch).

2. Up to 1.396 sq. ft. (1.396 sq. ft.) or 406 mm (16 inches) in Diameter:  1.7 mm (0.067 inch).

3. Up to 0.164 sq. m. (1.764 sq. ft.) or 457 mm (18 inches) in Diameter:  2.36 mm (0.093 inch).

4. Larger Than above:  3.12 mm (0.123 inch).

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for oil fired appliances, solid fuel burning appliances, or appliances listed for venting with Type L vents.

-------------------------------------------------------------------------------------------------------------------------------

C. Fabricate chimneys and vent connectors from galvanized steel, complying with NFPA 211 for minimum metal thickness.

1. Equal to or Less Than 152 mm (6 inches) in Diameter:  0.48 mm (0.019 inch).

2. Up to 254 mm (10 inches) in Diameter:  0.61 mm (0.024 inch).

3. Up to 406 mm (16 inches) in Diameter:  0.74 mm (0.029 inch).

4. Larger Than above:  1.42 mm (0.056 inch).

-------------------------------------------------------------------------------------------------------------------------------Retain two paragraphs below for appliances not installed in attics that are listed to be vented by Type B or L vents.

-------------------------------------------------------------------------------------------------------------------------------

D. Fabricate chimneys and vent connectors from ASTM B 209M (ASTM B 209), Type 1100 or 3003, aluminum or stainless steel, complying with NFPA 211 for the following minimum metal thicknesses:

1. Aluminum:  0.69 mm (0.027 inch).

2. Stainless Steel:  0.31 mm (0.012 inch).

E. Fabricate cleanout doors from compatible material, same thickness as breeching, bolted and gasketed.

2.9 GUYING AND BRACING MATERIALS

-------------------------------------------------------------------------------------------------------------------------------This Article contains materials recommended by one manufacturer that also advises a professional engineer design components and connections to adjacent structures.

-------------------------------------------------------------------------------------------------------------------------------

A. Cable:  [Three] [Four] <Insert number> galvanized, stranded wires of the following thickness:

-------------------------------------------------------------------------------------------------------------------------------Select appropriate size from subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

1. Minimum Size:  6 mm (1/4 inch) in diameter.

2. For ID Sizes 100 to 381 mm (4 to 15 inches):  8 mm (5/16 inch).

3. For ID Sizes 457 to 610 mm (18 to 24 inches):  9.5 mm (3/8 inch).

4. For ID Sizes 685 to 762 mm (27 to 30 inches):  11 mm (7/16 inch).

5. For ID Sizes 838 to 915 mm (33 to 36 inches):  12.7 mm (1/2 inch).

6. For ID Sizes 990 to 1220 mm (39 to 48 inches):  14.3 mm (9/16 inch).

7. For ID Sizes 1295 to 1524 mm (51 to 60 inches):  16 mm (5/8 inch).

B. Pipe:  [Two] [Three] <Insert number> galvanized steel, DN 32 (NPS 1 1/4).

C. Angle Iron:  [Two] [Three] <Insert number> galvanized steel, 50 by 50 by 6 mm (2 by 2 by 0.25 inch).

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of work.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION OF LISTED VENTS AND CHIMNEYS

A. Locate to comply with minimum clearances from combustibles and minimum termination heights according to product listing or NFPA 211, whichever is most stringent.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if specifying positive pressure vents.

-------------------------------------------------------------------------------------------------------------------------------

B. Seal between sections of positive pressure vents according to manufacturer's written installation instructions, using sealants recommended by manufacturer.

C. Support vents at intervals recommended by manufacturer to support weight of vents and all accessories, without exceeding appliance loading.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for appliances more than 83 percent efficient.

-------------------------------------------------------------------------------------------------------------------------------

D. Slope breechings down in direction of appliance, with condensate drain connection at lowest point piped to nearest drain.

3.3 INSTALLATION OF UNLISTED, FIELD FABRICATED BREECHINGS AND CHIMNEYS

A. Suspend breechings and chimneys independent of their appliance connections.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for Projects in seismic areas.

-------------------------------------------------------------------------------------------------------------------------------

B. Install, support, and restrain according to seismic requirements.

C. Align breechings at connections, with smooth internal surface and maximum 3 mm (1/8 inch) misalignment tolerance.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for appliances more than 83 percent efficient.

-------------------------------------------------------------------------------------------------------------------------------

D. Slope breechings down in direction of appliance, with condensate drain connection at lowest point piped to nearest drain.

E. Support breechings and chimneys from building structure with bolts, concrete inserts, steel expansion anchors, welded studs, C clamps, or beam clamps according to manufacturer's written instructions.

3.4 CLEANING

A. After completing system installation, including outlet fittings and devices, inspect exposed finish.  Remove burrs, dirt, and construction debris and repair damaged finishes.

B. Clean breechings internally, during and after installation, to remove dust and debris.  Clean external surfaces to remove welding slag and mill film.  Grind welds smooth and apply touchup finish to match factory or shop finish.

C. Provide temporary closures at ends of breechings, chimneys, and stacks that are not completed or connected to equipment.

END OF SECTION 15550

BREECHINGS, CHIMNEYS, AND STACKS
15550 - 1

