Copyright 2000 AIA
GSA VERSION MASTERSPEC(
09/00 (GSA 03/03)


Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15622 - DIRECT-FIRED ABSORPTION WATER CHILLERS
PART 1 -   - GENERAL

1.1 RELATED DOCUMENTS

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

A. Drawings, and the general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, direct-fired, double-effect absorption water chillers, with [gas] [fuel oil] [combination gas-oil] burners, with the following features:  

B. Microprocessor-based controls shall comply with ANSI/ASHRAE Standard 135.

C. Related Sections include the following:

1. Division 15 Section "Equipment Insulation" for insulation materials and application for pumps, tanks, hydronic specialties, and other equipment.

2. Division 15 Section "Pipe Insulation" for insulation for piping systems.

3. Division 15 Section “Basic Materials and Methods” for additional material specifications.

4. Division 15 Section “Building Automation Systems” for additional control related equipment.

5. Division 15 Section “Temperature Controls” for additional control related requirements.

6. Division 15 Section “Testing, Adjusting, and Balancing” for additional related requirements.

7. Division 15 Section “Operations and Maintenance” for additional related requirements.

1.3 DEFINITIONS

A. K:  Thousand (1000) units

B. M:  Million (1,000,000) units

1.4 SUBMITTALS

A. Product Data:  Submittals shall include rated capacities, operating characteristics, furnished specialties, COP and accessories.  Submit data on heat exchange materials, pressure vessels and their materials, finishes insulation and protective coatings.

Retain first subparagraph and associated subparagraphs below if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  Submit a complete set of manufacturer’s certified prints of the water chiller assemblies, control panels, sections and elevations, and unit isolation.  Submittal shall including the following as a minimum:

1. Assembled unit dimensions.

2. Operating weight and load distribution.

3. Required clearances for maintenance and operation.

4. Size and location of piping and wiring connections.

5. Vibration Isolation Calculations and Details:  

C. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

D. Vibration Isolation Base Detail:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

Items a. and b. above shall be signed and sealed by a qualified, registered professional engineer.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

1. Power, signal, and control wiring diagrams.

E. Coordination Drawings:  Prepare and submit a floor and sections plan drawn to scale and coordinated with the following:

Edit subparagraphs below to suit Project.

1. Structural supports.

2. Piping rough-in requirements.

3. Wiring rough-in requirements, including spaces reserved for electrical equipment.

4. Access requirements, including working clearances for mechanical controls and electrical equipment, and tube pull and service clearances.

Retain paragraph below if ARI certification is retained in "Quality Assurance" Article.

F. Certificates:  Submit certifications required in "Quality Assurance" paragraph.

Some manufacturers will not provide certification specified in first paragraph and subparagraphs below.  Verify availability with manufacturers and retain below if required by seismic criteria applicable to Project.  See the "Seismic Considerations" Article in the Evaluations in Division 15 Section "Packaged Water Chillers."  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

G. Manufacturer Seismic Qualification Certification:  Submit certification that water chillers, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."  Submittal shall include the following:

1. Basis for Certification:  Indicate whether the withstand certification is based on an actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of parts from the device when subjected to the seismic forces specified [and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit.  Identify the center of gravity and locate and describe the mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

H. Source quality-control test reports.

I. Startup service reports.

J. Operation and Maintenance Data:  Submit operation and maintenance data for each water chiller.  Data shall include emergency operation, and preventative and emergency maintenance manuals.

K. Warranties:  Submit signed certificates for special warranties specified in this Section.

L. Provide factory-certified performance ratings indicated conformance with the operating efficiencies and related characteristics indicated in Section 6 Heating, Ventilating, and Air Conditioning, including Tables 6.2.1C, 6.2.1G, Section 8 Power, Section 10, including Table 10.2, and Section 11, Energy Cost Budget Method ASHRAE/IESNA Standard 90.1-1999 and Code of Federal Regulations 10-CFR-434 and 435.

1.5 QUALITY ASSURANCE

A. ARI Certification:  Submit a certificate signed by the manufacturer certifying compliance with the requirements in ARI 560, "Absorption Water Chilling and Water Heating Packages."

B. ASHRAE/IESNA 90.1 Compliance:  Indirect fired water absorption water chillers shall have a minimum efficiency in accordance with ASHRAE Standard 90.1, Table 6.2.1C or the table at the end of this Section of the specifications, which ever is most stringent.  Comply with ASHRAE/IESNA 90.1 for COP’s and IPLV’s.

C. ASME Compliance:  Fabricate and label the water chiller pressure vessels in accordance with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Retain first paragraph below for oil-fired absorption water chillers; retain second paragraph for gas-fired absorption water chillers; retain both for absorption water chillers with combination burners.

D. NFPA Compliance:  Comply with the NFPA Standards listed below:

1. NFPA 31

2. NFPA 54

3. NFPA 70

1.6 DELIVERY, STORAGE, AND HANDLING

A. Water chillers shall be shipped from the factory with either a vacuum, fully charged with lithium bromide or a dry nitrogen-holding charge.

1.7 COORDINATION

A. Coordinate the size and the location of required concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements shall be as specified in Division 3.

B. Determine the means and methods necessary to install the equipment specified herein.  For repairs, alterations, additions and other forms of installation of equipment specified in this section into existing conditions, develop a plan including the delivery of the equipment to the site and into the space allocated for the equipment as indicated on the contract documents.  Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment to be approved by the contracting officer for this project.  Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment is included in the scope of work for this project.  Repairs and new work required to replace feature of the building or site altered in the process of delivering and installing the equipment are included in the scope of work.

1.8 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  See discussion about warranties in the "General Comments" Article in the Evaluations in Division 15 Section "Packaged Water Chillers."  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of the water chillers that fail in due to faulty materials or workmanship.

B. Warranty Period for <insert equipment name>:  [Two] <insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with these specifications, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Carrier; a United Technologies Company.

2. McQuay International.

3. Trane Company (The).

4. YORK International Corporation.

5. <Insert manufacturer's name.>

2.2 PACKAGED WATER CHILLERS

A. Description:  Furnish and install factory-assembled and -tested water chillers complete with generator, evaporator, absorber, condenser, controls, solution pump, purge system, interconnecting unit piping and wiring, indicated accessories, and mounting frame.

B. Refrigerant:  [Distilled] [or] [deionized] water.

C. Absorbent:  Lithium bromide.

Retain paragraph below for projects in seismic areas.

D. Fabricate the water chiller mounting frame and attachment to the pressure vessel with reinforcement strong enough to resist water chiller movement during a seismic event when the water chiller mounting frame is anchored to the building structure.

Delete paragraph and subparagraphs below if characteristics and capacities are scheduled on Drawings.

E. Water Chiller Characteristics and Capacities:  

1. Net Refrigeration Capacity:  <Insert kW (tons).>

2. [IPLV 1.00 for double effect].

3. COP:  [0.95].

4. Chilled-Water Flow:  <Insert L/s (gpm).>

5. Evaporator Entering-Water Temperature:  <Insert deg C (deg F).>

6. Evaporator Leaving-Water Temperature:  <Insert deg C (deg F).>

7. Evaporator Water-Pressure Drop:  <Insert kPa (feet of head).>

8. Evaporator Fouling Factor:  <Insert factor.>

9. Condenser Entering-Water Temperature:  <Insert deg C (deg F).>

10. Condenser Leaving-Water Temperature:  <Insert deg C (deg F).>

11. Condenser-Water Pressure Drop:  <Insert kPa (feet of head).>

Delete first four subparagraphs below if water chiller is not used for water heating.

12. Condenser Fouling Factor:  <Insert factor.>

13. Heating-Water Flow:  <Insert L/s (gpm).>

14. Entering Heating-Water Temperature:  <Insert deg C (deg F).>

15. Leaving Heating-Water Temperature:  <Insert deg C (deg F).>

16. Heating-Water Heat-Exchanger Water Pressure Drop:  <Insert kPa (feet of head).>

17. Fuel Consumption:  <Insert value in kW (MBh).>

Retain subparagraph above for natural gas burners or first subparagraph below for oil burners.

18. Fuel Consumption:  <Insert value in mL/s (gph).>

19. Solution-Pump Motor Data:

a. <Insert number> hp.

b. [120] [240] [480] <Insert other>-V ac.

c. [Single] [Three] phase.

d. <Insert number> A, full load.

e. <Insert number> A, locked rotor.

2.3 SHELL

A. Construction:  Shell shall be fabricated from carbon steel, and be ASME labeled.

1. Maximum Working Pressure:  104 kPa (15 psig).

2. Maximum Working Temperature:  171 deg C (340 deg F).

3. Tube Sheets:  Carbon-steel plates; drilled and reamed for tubes.

2.4 HEAT EXCHANGERS

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger depending on fluid types and heat-exchanger temperatures.

A. Tube Construction:  Each tube shall be individually replaceable and expanded securely into the tube sheets in an approved manner.

Both "Standard" and "Marine" water boxes are available in both pressure ratings, but 300 psig (2070 kPa) may be a special order.

B. Evaporator:

1. Tube Materials:  Tubes shall be [copper] [copper-nickel alloy] [copper or copper-nickel alloy].

2. Water Box:  Water boxes shall be [standard] [marine] type, with a design working pressure of [1035 kPa (150 psig)] [2070 kPa (300 psig)], and shall have [flanged] [grooved mechanical-joint coupling] water-nozzle connections with a thermistor-type temperature sensor factory installed in each nozzle.

C. Condenser:

1. Tube Materials:  Tubes shall be [copper] [copper-nickel alloy] [copper or copper-nickel alloy].

Both "Standard" and "Marine" water boxes are available in both pressure ratings, but 300 psig (2070 kPa) may be a special order.

2. Water Box:  Water boxes shall be [standard] [marine] type, with a design working pressure of [1035 kPa (150 psig)] [2070 kPa (300 psig)], and shall have [flanged] [grooved mechanical-joint coupling] water-nozzle connections with a thermistor-type temperature sensor factory installed in each nozzle.

D. Absorber:

1. Tube Materials:  Tubes shall be [copper] [copper-nickel alloy] [copper or copper-nickel alloy].

Both "Standard" and "Marine" water boxes are available in both pressure ratings, but 300 psig (2070 kPa) may be a special order.

2. Water Box:  Water boxes shall be [standard] [marine] type, with a design working pressure of [1035 kPa (150 psig)] [2070 kPa (300 psig)], and shall have [flanged] [grooved mechanical-joint coupling] water-nozzle connections with a thermistor-type temperature sensor factory installed in each nozzle.

E. First-Stage Generator:

1. Tube Materials:  [Carbon] [Stainless] steel.

2. Working Pressure:  90 to 104 kPa (13 to 15 psig).

3. Burner Assembly:

a. Forced draft, single- or dual-fuel type; welded [stainless-] steel construction.

b. Minimum Turndown Ratio:  [3:1] [8:1].

c. UL approved.

d. Flame safeguard.

e. Fuel:  [Natural gas] [Propane] [No. 2 fuel oil] <Insert combination of fuels>.

4. Gas Train:  AGA and FMG approved, consisting of manual-shutoff valve, main gas regulator, low and high gas-pressure switches, and two leak-test valves.

Retain subparagraph above or below if only single-fuel burner assembly is used.

5. Oil Train:  Consisting of components supplied by the burner manufacturer to provide specified fuel and air control operation.

F. Second-Stage Generator:

1. Tube Materials:  [Copper] [Copper-nickel alloy] [Copper or copper-nickel alloy].

2. Working Pressure:  90 to 104 kPa (13 to 15 psig).

G. Evaporator and Absorber Nozzle Materials:  Materials shall be stainless steel or another approved material that does not corrode.

H. Chillers shall have factory-mounted controls and devices that allow for measuring, monitoring, and controlling energy consumption, output, and operating efficiencies prescribed in Section 6: Heating, Ventilation, and Air Conditioning and Section 11: Energy Cost Budget Method of ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10-CFR-43, including Tables 6.2.1.C, 6.2.1.G, 11.4.3.B, and 11.4.3.C.  Factory-mounted controls shall include a controller with an LED panel capable of calculating and indicating the values required to verify the efficiencies and operating characteristics identified in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10-CFR-434 and 435.

2.5 INSULATION

Insulating materials and thicknesses may vary among manufacturers; verify availability.

A. Cold Surfaces:  Insulation shall be a closed-cell, flexible elastomeric, thermal insulation complying with ASTM C 534, Type II, for sheet materials.

1. Thickness:  [19 mm (3/4 inch)] [38 mm (1-1/2 inches)] <Insert thickness>.

2. Adhesive:  As recommended by insulation manufacturer.

3. Factory apply insulation over entire cold surface of water chiller components.

a. Apply adhesive to 100 percent of insulation contact surface.

b. Seal seams and joints.

c. After adhesive has fully cured, apply two coats of protective coating to insulation.

B. Hot Surfaces:  Insulation shall be a mineral-Fiber Board Thermal Insulation:  Glass fibers bonded with thermosetting resin.  Insulation shall comply with ASTM C 612, Type IB, without facing.

1. Thickness:  [38 mm (1-1/2 inches)] <Insert thickness>.

2. Factory apply insulation materials, accessories, and finishes; with smooth, straight, and even surfaces.  Insulation shall be free of voids throughout the length of equipment.

3. Adhesive-Attached Anchor Pins and Speed Washers:  Use galvanized-steel plate, pin, and washer manufactured for attachment to water chiller's heating surfaces with adhesive.  Pin length shall be sufficient for the insulation thickness indicated.

a. Adhesive:  Adhesive shall be as recommended by anchor pin manufacturer as appropriate for surface temperatures of water chillers; and with 45-kg (100-lb) holding capacity for direct pull perpendicular to adhered surface.

4. Bands:  Bands shall be 19 mm (3/4 inch) wide, [stainless] [galvanized] steel.

5. Jacket:  Jacket shall be Factory apply glass-cloth jacket, directly over insulation.

a. Apply jacket smooth and tight to surface with 50-mm (2-inch) overlap at seams and joints.

b. Embed glass cloth between two 1.6-mm- (0.062-inch-) thick coats of jacket manufacturer's recommended adhesive.

c. Completely encapsulate insulation with jacket, leaving no exposed insulation.

d. Apply two coats of latex paint to glass-cloth jacket.

2.6 ACCESSORIES

A. Solution Pump:  Solution shall be a hermetically sealed, self-lubricating, liquid cooled unit.  Open type pumps are not acceptable.

B. Purge System:  Provide a unit mounted, factory wired system, equipped with a pump and controls to constantly remove non-condensable vapors.

C. Control Valve:  Control valve shall have a cast-iron or carbon-steel body, with PTFE seat and flanged connections, suitable for energy source specified, complete with actuator and linkage.

1. Actuator and Linkage:  Capable of modulating flow from 20 to 100 percent.

2.7 CONTROLS

Coordinate this Article with Division 15 Section "HVAC Instrumentation and Controls."

A. Control Panel:  Controls shall be the stand-alone, microprocessor based type controls.  Controls shall be BACnet compatible and data points and alarms shall be accessible from the Building Automation System.

B. Status Display:  Display shall be the multiple-character liquid-crystal display or light-emitting diode type with keypad.  Display the following conditions:

Edit list below to suit Project.  Verify availability; status displays may vary depending on unit size.

1. Date and time.

2. Operating or alarm status.

3. Operating hours.

4. Outside-air temperature if required for chilled-water reset.

5. Temperature and pressure of operating set points.

6. Entering and leaving temperatures of chilled water and condenser water.

7. Entering and leaving hot-water temperatures.

8. Refrigerant temperature.

9. Solution concentration and temperature.

10. First-stage generator pressure and temperature.

11. Indication of solution- and purge-pump operation.

12. Generator shell pressure.

13. Number of starts.

Retain first subparagraph below for units that generate heating or domestic hot water.

14. Number of purge cycles.

15. <Insert other status display items.>

C. Control Functions:

Edit list below to suit Project.  Verify availability; functions may vary depending on unit size.

1. Automatically control burner-firing rate to maintain chilled-water or heating-water temperature set points.

2. Entering and leaving chilled-water temperatures and control set points.  Chilled-water temperature shall be reset based on [return-water] [outside-air] [space] temperature.

3. Operate solution and refrigerant pumps for several minutes after heat-input valve is closed to ensure crystallization does not occur.

4. Fuel flow

5. Chilled and condenser water flow

6. Capacity and COP

7. <Insert other control functions.>

D. Safety Shutdowns:

Edit list below to suit Project.  Verify availability; conditions may vary depending on unit size.

1. Crystallization.

2. Low refrigerant temperature.

3. Loss of chilled- or condenser-water flow.

4. Low leaving chilled-water temperature [, 2 deg F (1 deg C) below set point].

5. Power failure.

6. Solution-pump overloads.

7. Burner alarm indication.

8. First-stage generator high temperature or pressure.

9. High solution concentration.

10. Incomplete dilution cycle.

11. <Insert other conditions.>

E. Warning Conditions:  Control panel shall close warning contacts and generate a discreet message when one of the following operating conditions is detected:

Edit list below to suit Project.  Verify availability; conditions may vary depending on unit size.

1. Low refrigerant temperature.

2. High generator temperature or pressure.

3. High or low entering condenser-water temperature.

4. Purge-pump current overload.

5. Solution temperature sensor failure.

6. Low chilled-water flow.

7. <Insert other warning conditions.>

2.8 BUILDING AUTOMATION SYSTEM INTERFACE

A. The chiller manufacturer shall provide factory-installed DDC microprocessor based hardware and software to enable the Building Automation System (BAS) to monitor and control the chiller and to display the chiller status and alarms specified in this paragraph and else where in this specification.  The chiller controls shall interface seamlessly with other DDC microprocessor-based building subsystems as shown on the drawings and as specified in this and other sections of the specifications.  Interface shall be BACnet compatible.

B. The interface between the chiller controls and BAS shall enable the BAS to read as separate and discreet points significant values and alarms on the chiller.  Use of a single set of contacts to send an alarm will not be acceptable.  The contractor shall furnish and install necessary hardware, wiring, gateways, computing equipment and software, as defined in this specification and as required for the chiller to operate in accordance with the sequence of operation.

C. As a minimum the interface shall allow the following inputs, outputs and functions.

1. Chiller and operating and alarm status

2. Solution pump motor status, amps
3. Chiller capacity

4. Solution temperatures, i.e. evaporator and absorber
5. Entering and leaving temperatures for chilled and condenser water

6. Chiller tripped by high/low pressure or high/low temperature or high/low electrical current or high/low oil pressure

7. Loss of electrical power

8. Chilled and condenser water flows
D. Controls:  Chiller applications where the chiller controls interface with a Building Automation System (BAS) having [BACnet] [LONtalk/LONworks] [controls to match existing] compatibility, the chiller shall be provided with a factory-mounted controller having [BACnet] [LONtalk/LONworks] [controls to match existing] compatibility.  Controls and control devices associated with the chiller shall function with [BACnet] [LONtalk/LONworks] [controls to match existing] compatibility without the need for or used of gateways, product specific or proprietary devices.

2.9 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. Refer to Division 15 Section "Motors" for general requirements.

B. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2.10 ELECTRIC MOTORS

A. All electric motors shall comply with the requirements of ASHRAE/IESNA Standard 90.1 Section 10, including Table 10.2, and Section 11:  Energy Cost Budget Method of ASHRAE/IESNA Standard 90.1-1999 and Code of Federal Regulations 10-CFR-434 and 435.

2.11 SOURCE QUALITY CONTROL

Factory tests are an added cost option and may not be available from some manufacturers.  Verify requirement with Owner.

A. The chiller manufacturer shall factory test and rate water chillers, before shipping, according to ARI 560, "Absorption Water Chilling and Water Heating Packages."

Test and inspection in first paragraph below are not required on water chillers operating at less than 15 psig (104 kPa).

B. The chiller manufacturer shall factory test and inspect each heat exchanger according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, if the operating pressure will exceed 104 kPa (15 psig).  Stamp with ASME label.

C. The chiller manufacturer shall factory test and inspect water boxes at 150 percent of operating pressure.

D. The chiller manufacturer shall rate sound power level according to ARI 575 procedure.

Retain below if Owner wants to witness source quality-control testing.

E. The chiller manufacturer shall allow the Owner access to the places where the water chillers are being source quality control tested.  The government shall be notified 14 days in advance of and testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before water chiller installation, the Contractor shall examine the rough in for concrete equipment bases, anchor-bolt sizes and locations, piping, and electrical to verify actual locations, sizes, and other conditions affecting water chiller performance, maintenance, and operations.

1. Final water chiller locations indicated on the Drawings are approximate.  The Contractor shall determine the exact locations before roughing-in for piping and electrical connections.

B. The Contractor shall proceed with the installation only after unsatisfactory conditions have been corrected.

3.2 WATER CHILLER INSTALLATION

A. Install water chillers on a concrete base.  Concrete base shall be as specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements shall be as specified in Division 3.

Revise paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

B. Concrete Bases:  Anchor chiller mounting frame to concrete base.

1. Install dowel rods to connect the concrete base to the concrete floor.  Unless otherwise indicated, install dowel rods on 450-mm (18-inch) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices in accordance with approved setting drawings, templates, diagrams, instructions, and directions furnished with items specified to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Cast-in-place concrete materials and placement requirements shall be as specified in Division 3.

6. Vibration Isolation:  Rubber pads with a minimum deflection of [6.35 mm (0.25 inch)] <Insert deflection>.  Vibration isolation devices and installation requirements shall be as are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

7. Maintain manufacturer's recommended clearances for service and maintenance.

8. Evacuate and charge water chiller with lithium bromide solution if not factory charged.

9. Install devices furnished by manufacturer that were shipped unattached to the chiller.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in Division 15 Section "Hydronic Piping."  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Chilled- and condenser-water piping installation requirements are specified in Division 15 Section "Hydronic Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect gas piping full size to water chiller gas-train inlet with union.

Retain paragraph above for gas-fired water chillers and first paragraph below for oil-fired water chillers, or both for combination gas- and oil-fired water chillers.

C. Connect oil piping full size to burner inlet with shutoff valve and union.

D. Install piping adjacent to water chillers to allow service and maintenance.

E. Generator Connections:  Connect fuel-fired burner assembly and blower and associated damper for combustion air.

F. Evaporator Connections:  Connect inlet to evaporator with controller-bulb well, shutoff valve, thermometer, strainer, pressure gage, and union or flange.  Connect outlet to evaporator with shutoff valve, flow switch, balancing valve, thermometer, pressure gage, and union or flange.

G. Condenser Connections:  Connect inlet to condenser with shutoff valve, thermometer, plugged tee, and pressure gage.  Connect outlet to condenser with shutoff valve, thermometer, drain line and shutoff valve, strainer, and plugged tee.

H. Connect flue to burner outlet.

I. Safety Relief Valve Connections:  Extend vent piping to the outside without valves or restrictions.  Pipe drip-pan elbow drain connection to suitable drain.

J. Ground water chillers according to Division 16 Section "Grounding and Bonding."

K. Connect wiring according to Division 16 Section "Conductors and Cables."

L. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 
STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. The Contractor shall engage a factory-authorized service representative to perform startup service.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Verify that refrigerant charge is sufficient and water chiller has been leak tested.

2. Verify that pumps are installed and functional.

3. Verify that thermometers and gages are installed.

4. Operate water chiller for run-in period according to manufacturer's written instructions.

5. Verify and record performance of chilled- and condenser-water flow and low-temperature interlocks.

6. Verify and record performance of water chiller protection devices.

7. Test and adjust controls and safeties.  Replace damaged or malfunctioning controls and equipment.

D. Prepare and submit to the government a written startup report that records results of tests and inspections.

E. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to site outside normal occupancy hours for this purpose.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain water chillers.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15622 

DIRECT-FIRED ABSORPTION WATER CHILLERS
15622 – 14

