Copyright 2000 AIA
GSA VERSION MASTERSPEC
12/00 (GSA 03/04)

Copyright 2000 (R 3/02) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15642 - CLOSED CIRCUIT, MECHANICAL DRAFT COOLING TOWERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes factory assembled and tested, closed circuit, [induced] [forced] draft cooling towers.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section, "Building Automation System" and “Temperature Controls” for control devices including thermostats.

2. Division 15 Section, "Heating Cables"

3. Division 16 Section, "Lightning Protection System."

4. Division 15 Section, "Meters and Gauges" for supply line water meters.

5. Division 15 Section “Valves”

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, pressure drop, fan performance data, rating curves with selected points indicated, furnished specialties, and accessories.

1. Provide factory certified performance ratings indicated conformance with the operating efficiencies and related characteristics indicated in Code of Federal Regulations 10 CFR 434 and ASHRAE/IESNA Standard 90.1, Section 6 Heating, Ventilating, and Air Conditioning, including Tables 6.2.1C, 6.2.1G, 6.2.1H, 6.2.1I, Section 8 Power, Section 10, including Table 10.2, and Section 11, Energy Cost Budget Method.

2. Equipment sound data.

Retain paragraph below if cooling towers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section, "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  

a. Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Calculate requirements for foundation elements and connections to resist a 44 m/s (100 mph) wind design load.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include handrails, ladders, and equipment mounting frame.

Ensure that layout complies with manufacturers’ recommended clearances from walls and enclosures.

3. Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field piping and wiring connection.

4. Wiring Diagrams:  Power, signal, and control wiring.

C. Product Certificates: CTI performance certification.

Retain paragraph if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Structural supports.

2. Piping and wiring roughing-in requirements (determine spaces reserved for electrical equipment).

3. Access requirements for service and maintenance.

Retain paragraph if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section, "Mechanical Vibration and Seismic Controls."

E. Manufacturer Seismic Qualification Certification:  Submit certification that cooling towers, accessories, and components will withstand seismic forces defined in Division 15 Section, "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Definition varies with type of building and occupancy and is critical to valid certification.  The option is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.  

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality control test reports.

G. Operation and Maintenance Data:  For cooling towers to include in emergency, operation, and maintenance manuals.

H. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

If an independent testing agency is required, see Division 1 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7 or other more specific criteria.  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain paragraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is [certified by CTI] [a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7], and that is acceptable to authorities having jurisdiction.

B. ASHRAE Compliance: ASHRAE /IESNA 90.1.

C. Product Options:  Information on Drawings and in Specifications establishes requirements for system's aesthetic effects and performance characteristics.  Aesthetic effects are indicated by dimensions, arrangements, alignment, and profiles of components and assemblies as they relate to sightlines, to one another, and to adjoining construction.  Performance characteristics are indicated by criteria subject to verification by one or more methods including preconstruction testing, field testing, and in-service performance.

Retain paragraph above or paragraph below.  Retain below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

D. Product Options:  Drawings indicate size, profiles, and dimensional requirements of cooling towers and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

Retain subparagraph below with either "Product Options" paragraph above or revise to suit Project.

1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain paragraph below if Owner prefers the security of a coil designed and fabricated according to ASME Boiler and Pressure Vessel Code or where state or local codes require it.

F. ASME Compliance:  Fabricate and label heat exchange coils to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

G. Comply with NFPA 70.

H. Certification: Factory Mutual Research

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division [3] [15].
B. Coordinate installation of equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

Edit paragraph below accordingly for new or existing construction.

C. Determine the means and methods necessary to install equipment specified herein.  For repairs, alterations, additions and any other form of installation of equipment specified in this section into existing conditions, develop a plan including the delivery of the equipment to the site and into the space allocated for the equipment.  Obtain approval from the project’s contracting officer, prior to execution, for demolition of existing features of the building or site required to accomplish the delivery and installation of the equipment.  Demolition to any existing features of the building or site required to accomplish the delivery and installation of equipment shall be included in the scope of work and contract amount.  Repairs and new work required to replace and restore any feature of the building or site altered or damaged in the process of delivering and installing the equipment shall be included in the scope of work and contract amount.

1.6 WARRANTY

When warranties are required, verify with Owner that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section, "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of closed-circuit, mechanical-draft cooling towers that fail in materials or workmanship within specified warranty period:

1. Fan, motor, drive shaft, bearings, and motor supports.

2. Tube bundle.

3. External-circuit circulating pump.

4. Internal circuit circulating pump.

5. Integral controls.

6. Basin

7. Fill material.

8. <Insert other components requiring extended warranty.>

Verify available warranties for units and components and insert number below.

9. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A.  Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Baltimore Aircoil Company.

2. Evapco Inc.

3. Marley Cooling Tower; a United Dominion Company.

4. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory assembled and tested, closed circuit, [induced] [forced] draft cooling tower.

Retain paragraph below for projects in areas with seismic greater than 1.

B. Fabricate cooling tower mounting frame and attachments with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower mounting frame is attached to the building structure.

Delete the following paragraph if scheduled on drawings..

C. Cooling Tower Characteristics and Capacities:

1. Condenser-Water Flow:  <Insert L/s (gpm).>

2. Maximum Condenser-Water Pressure Drop:  <Insert kPa (psig).>

3. Entering Condenser-Water Temperature:  <Insert deg C (deg F).>

4. Leaving Condenser-Water Temperature:  <Insert deg C (deg F).>

5. External-Circuit [Water] [Glycol] Flow:  <Insert L/s (gpm).>

6. Entering-Air Wet-Bulb Temperature:  <Insert deg C (deg F).>

7. Maximum Drift Loss:  <Insert number> percent of external-circuit flow.

8. External-Circuit Circulating Pump Motor Electrical Characteristics:  [240] [480] <Insert other>-V ac, 3 phase, 60 Hz.

9. Number of Fans:  [One] [Two] <Insert number>.

10. Fan Motor Electrical Characteristics:  [240] [480] <Insert other>-V ac, 3 phase, 60 Hz.

11. Noise Rating:  <Insert dBA> at <Insert distance in m (feet)>.

12. Basin depth:  <Insert mm (inches).>

13. Basin Heater:  Maintain 4 deg C (40 deg F) condenser-water temperature at minus 18 deg C (0 deg F) outside-air temperature.  [Electric heaters to have a minimum of two stages.]
2.3 MATERIALS

A. Casing Material:  ASTM A666 Type 304 sheet stainless steel.
1. Fasteners:  Corrosion resistance equal to or better than materials being fastened.

2. Joints:  Sealed watertight.

3. Welded Connections:  Continuous and watertight.

4. Rigging Supports:  For handling cooling towers at construction site.

B. Collection Basin Material:  ASTM A666 Type 304 sheet stainless steel.

1. Removable strainer with openings smaller than nozzle orifices.

2. Overflow connection.

3. Makeup water connection.

C. Drain Connection:  [Oversized for use with remote sump] [Side] [Bottom].

Retain one of the four paragraphs below.  Verify availability of features with manufacturers.

D. Tube Bundle Material and Construction:  Type 304 stainless steel serpentine tubes designed for low pressure drop and free drainage of fluid; factory tested at 2400 kPa (350 psig) air pressure while underwater.

1. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

E. Tube Bundle Material and Construction:  Cleanable Type 304 stainless steel tubes, factory tested at 860 kPa (125 psig) air pressure while underwater.

1. Pitch in direction of fluid flow for free drainage.

2. Include cover plates that are removable without disturbing piping, on headers to permit access for mechanical cleaning; headers and removable cover plates constructed of stainless steel plate.

3. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

F. Tube Bundle Material and Construction:  Copper serpentine tubes in a stainless steel sheet frame.  Copper and stainless steel components shall be separated by phenolic isolators; pitch tubes in direction of fluid flow for free drainage.  Factory tested at 2400 kPa (350 psig) air pressure while underwater.

1. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

G. Tube Bundle Material and Construction:  Type 304 stainless steel serpentine tubes in a stainless steel sheet frame.  Pitch tubes in direction of fluid flow for free drainage.  Factory tested at 2400 kPa (350 psig) air pressure while underwater.

1. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

Retain one of the three paragraphs below if required.

H. Drift Eliminator Material:  PVC with maximum flame-spread index of 5 according to ASTM E 84.

I. Drift Eliminator Material:  ASTM A666 Type 304 stainless steel.

J. Water Distribution System:  Header pipe and removable branch pipes for even distribution of water over fill.

1. Pipe Material:  Schedule 40, [Type 304 stainless steel] [PVC].

2. Nozzles:  Removable plastic, brass, or ceramic nozzles with a maximum pressure drop of 83 kPa (12 psig) <Insert kPa (psig)>.

3. Hot-Water-Basin Control Valves:  Manufacturer's standard butterfly or globe valves arranged to balance flow to each distribution basin and shut flow off during servicing.

4. Hot water basin balance indicator.

K. Inlet Screen Material:  Type 304 stainless steel mesh mounted in removable frames.

Retain paragraph below if discharge hoods are required.

L. Draft Hood Material:  Type 304 stainless steel with stainless steel access door.

2.4 COMPONENTS

Retain one of three paragraphs below if makeup water valve is supplied with cooling tower.          Mechanical makeup water valve in first paragraph is most common.

A. Water Level Control:  [Manufacturer's standard mechanical makeup water valve and plastic or bronze float with an adjustable linkage] [Electric float switch and solenoid operated, makeup water valve] [Electronic float switch and solenoid operated, makeup water valve] [Infrared level sensor with electronic control and solenoid operated water valve] with level indicator.

B. Fan(s):  [Type 304 stainless steel, propeller] [Cast aluminum, propeller] [Type 304 stainless  steel, centrifugal].

1. Drive:  [Direct] [or] [belt].

2. Bearings:  Self-aligning ball bearings or bronze sleeve bearings with lubrication lines and fittings.  Grease fittings extended to accessible location at front of unit.

3. Vibration Cutout Switch:  [Solid state, with adjustable time delay and NEMA 250, Type 4 enclosure] [Mechanical, with manual reset].

C. External Circuit Circulating Pump:  Close coupled, end suction, single stage, [casing wear ring] [impeller wear ring] [all bronze], mechanical seal, centrifugal pump; with a totally enclosed motor; and suitable for outdoor service.

Retain fan discharge dampers in first paragraph below for centrifugal fans if required.

D. Capacity Control Dampers:  Type 304 stainless steel, fan discharge dampers, with linkages, electric damper operator, controller, end switches, transformer, and weatherproof enclosure.  Reset dampers to vary airflow through evaporative condenser to control leaving condenser water temperature.

E. Basin Heater:  [Hot water coil] [Electric resistance coil with minimum of two stages].

2.5 CONTROLS

A. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.

B. Cooling Towers shall be interlocked with the Building Automation System (BAS) and be provided with the controls and devices that allow for measuring, monitoring, and controlling energy consumption, and operating efficiencies as prescribed in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.  Cooling tower controls shall include a controller with an LED panel capable of calculating and indicating the values required to verify the efficiencies and operating characteristics identified in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.  Controller shall be remotely mounted indoors.

C. Any cooling tower application where the cooling tower controls interface with a Building Automation System (BAS) shall have [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility, the cooling tower system shall be provided with a remote mounted controller having [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility.  All controls and control devices associated with the cooling tower shall function with [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility without the need for or use of gateways, product specific or proprietary devices.

D. In addition to controls specified in other sections, provide the following item[s] compatible with main control system:

1. Energy usage meter reporting kilowatt hours 

2.6 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section, "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. Comply with requirements in Division 15 Section, "Motors."

B. Maximum total fan motor power.

Divide maximum flow by the ratio below to determine maximum fan nameplate rated motor power in accordance with Table 6.2.1G, ASHRAE Standard 90.1-2001.

1. Propeller fans:

3.3 L/s per fan kW (38 gpm per fan hp)
2. Axial fans:


3.3 L/s per fan kW (38 gpm per fan hp)
3. Centrifugal fans:
1.7 L/s per fan kW (20 gpm per fan hp)
See Evaluation Editing Instructions for discussion on enclosure types for various applications.  Retain first paragraph below if enclosure is not open dripproof type.

C. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, air over].

D. Motor Speed:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Inverter type for variable-speed controller].

E. All electric motors shall comply with the requirements of ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10-CFR-434.

2.7 HANDRAILS, LADDERS, AND PLATFORMS

Requirements for handrails, ladders, and platforms for cooling towers depend on tower height and accessibility of maintenance items.  Edit this Article accordingly.  Clarify if these are provided by the manufacturer or designed by the structural engineer.

A. Handrails:  Type 304 stainless steel or aluminum complying with 29 CFR 1910.23.  Pipe-rail materials and fabrication are specified in Division 5 Section, "Pipe and Tube Railings."  

B. Ladders and Safety Cages:  Type 304 stainless steel or aluminum complying with 29 CFR 1910.27.  Provide ladder of sufficient height to reach from base to top of tower in its final installation.

C. Platforms:  Stainless steel with a bar grating floor.

2.8 SOURCE QUALITY CONTROL

Select one of the following paragraphs.  ASME’s testing is more stringent and more costly.
A. Verification of Performance:  Test and certify cooling tower performance according to CTI's STD 201, "Certification Standard for Commercial Water Cooling Towers Thermal Performance."

B. Verification of Performance:  Test and certify cooling tower performance according to ASME's PTC 23-86 (Reaffirmed in 1997), "Atmospheric Water Cooling Equipment."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for concrete bases, anchor-bolt sizes and locations, piping, and electrical to verify actual locations and sizes before cooling tower installation and other conditions affecting cooling tower performance, maintenance, and operation.

B. Examine proposed route of moving cooling towers into place and verify that it is free of interferences.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain two paragraphs below for cooling towers mounted on grade.

A. Install cooling towers on concrete bases.  Concrete base is specified in Division 15 Section, "Basic Mechanical Materials and Methods,"[ and concrete materials and installation requirements are specified in Division 3]. 

Retain paragraph below based on installed equipment.  Coordinate concrete base with Section 15050 requirements.  Indicate dowel rod quantity, size, and spacing on Drawings if cooling towers are mounted on vibration isolators.  Delete below if retaining vibration isolation equipment bases.

B. Concrete Bases:  Anchor cooling tower to concrete base.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 450 mm (18 inch) centers around full perimeter of the base.

2. For equipment supported on structural slab, install epoxy coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Install anchor bolts according to anchor bolt manufacturer's written instructions.

6. Cast-in-place concrete materials and placement requirements are specified in Division 3.

Retain paragraph below for cooling towers mounted on structural steel.  Steel design and specifications are in other sections.

C. Steel supports: Attach tower to structural steel.

D. Ensure a minimum 1.22 m (4 foot) clear space beneath the bottom of the lowest structural member, piping, or sump, to allow re-roofing beneath the tower.

E. Install freeze protection on exposed piping.

Retain one of three paragraphs below.  Coordinate with Drawings and Division 15 Section,          "Mechanical Vibration and Seismic Controls."  Retain first paragraph for equipment supported on slabs-on-grade.

F. Vibration Isolation:  Rubber pads with a minimum deflection of [6.35 mm (0.25 inch)] <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

Based on supporting structure and seismic requirements, insert amount of required deflection in paragraph below.

G. Vibration Isolation:  Restrained spring isolators with a minimum deflection of <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

If retaining paragraph below, delete "Concrete Bases" paragraph and subparagraphs above.

H. Vibration Isolation:  Mount water cooling towers on a vibration isolation equipment base as specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

I. Maintain manufacturer's recommended clearances for service and maintenance.

J. Loose Equipment:  Install electrical components, devices, and accessories that are not factory mounted.

NFPA 214, Standard on Water Cooling Towers, calls for sprinkler protection for field erected and factory assembled water cooling towers of combustible construction or those in which the fill is of combustible material.

K. Install sprinkler piping as specified in [Division 13][Division 15].
L. Install lightning protection system as specified in [Division 13][Division 16].
3.3 CONNECTIONS

Coordinate piping installation and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install meter with pulse head on make-up water supply line.

C. Install piping adjacent to cooling towers to allow service and maintenance.

D. Install flexible pipe connectors at final connections of towers mounted on vibration isolators.

E. Connect overflow drain and bleed lines to sanitary sewage system.

F. Domestic Water Piping:  Comply with applicable requirements in Division 15 Section "Domestic Water Piping."  Connect to water level control with shutoff valve and union or flange at each connection.

G. Condenser Water Piping:  Comply with applicable requirements in Division 15 Section "Hydronic Piping."  Connect to supply and return cooling tower connections with shutoff valve, flow control valve, and union or flange on supply connection to the cooling tower and shutoff valve and union or flange to return connection from the cooling tower to the chiller.

H. Hot Water Piping:  Comply with applicable requirements in Division 15 Section "Hydronic Piping."  Connect to supply and return basin heater tappings with shutoff valve, strainer, control valve, and union or flange on supply connection and union or flange and balancing valve with indicator on return connection.

Retain the paragraph below when there are two towers or more.

I. Equalizer piping.  Install equalizer piping between towers with isolation valves and automatic shutoff valves for each cell.
Retain paragraph below only if cooling tower is installed indoors.

J. Ducts:  Comply with applicable requirements in Division 15 Section, "Metal Ducts."  Connect ducts to cooling tower inlet and outlet, full size of outlet, with flexible duct connection.

K. Ground cooling towers according to Division 16 Section, "Grounding and Bonding."

L. Connect wiring according to Division 16 Section "Conductors and Cables."

M. Tighten electrical connectors and terminals according to manufacturer's published torque tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

N. Connect to building automation system.

3.4 FIELD QUALITY CONTROL

Retain one of two paragraphs below.

A. Testing Agency:  Engage a qualified testing and inspecting agency to perform field tests and inspections according to [ASME PTC 23, "ASME Performance Test Codes--Code on Atmospheric Water Cooling Equipment] [CTI's Supplement to ATC 105, "Acceptance Test Code for Closed Circuit Cooling Towers]," and prepare test reports to be submitted within 10 working days.
B. Perform field tests and inspections according to [ASME PTC 23, "ASME Performance Test Codes--Code on Atmospheric Water Cooling Equipment] [CTI's Supplement to ATC 105, "Acceptance Test Code for Closed Circuit Cooling Towers]," and prepare test reports to be submitted within 10 working days.
3.5 STARTUP SERVICE

Delete paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative, specified in Section 01700 “Execution Requirements”, to perform startup service.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Obtain performance tables from manufacturer.

D. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Clean and flush entire unit including basins prior to initial startup.

2. Verify that accessories are properly installed.

3. Check makeup water control.
4. Verify clearances for airflow and for cooling tower servicing.

5. Check for vibration isolation and structural support.

6. Verify bearings on fans, motors, and shafts are properly lubricated.

7. Verify fan wheel rotation for correct direction and for vibration or binding.  Correct vibration and binding problems.

8. Adjust belts to proper alignment and tension.

9. Verify water level in tower basin.  Fill to proper startup level.

10. Start external circuit circulating and condenser water pumps.

11. Verify operation of tower basin, makeup line, automatic freeze protect dump, and controlling device.  Replace defective and malfunctioning units.

12. Verify operation of basin heater and control thermostat.  Replace defective and malfunctioning units.

13. Verify that tower discharge is not recirculating into air intakes.  Recommend corrective action.

E. Check HVAC water treatment system for proper operation, and measure chemical treatment levels.  Verify operation of tower basin automatic blowdown, and controlling device.

F. Start cooling tower and condenser water pumps.  Follow manufacturer's written starting procedures.

G. Prepare a written startup report that records the results of tests and inspections to be submitted within 10 working days.
3.6 ADJUSTING

A. Set and balance condenser water flow to each cooling tower inlet.

B. Adjust water level control for proper operating level.

C. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site in assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to site outside normal occupancy hours for this purpose.

3.7 DEMONSTRATION

Engage a factory authorized service representative, as specified in Section 01700 “Execution Requirements”, to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] [hours] to adjust, operate, and maintain cooling towers.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15642

CLOSED CIRCUIT, MECHANICAL DRAFT COOLING TOWERS
15642 - 1

