Copyright 2000 AIA
GSA VERSION MASTERSPEC
12/00 (GSA 03/04)

Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15663 - EVAPORATIVE CONDENSERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes factory assembled and tested, [induced] [forced] draft evaporative condensers.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Building Automation System" and “Temperature Controls” for control devices including thermostats.

2. Division 15 Section "Meters and Gauges" for supply line water meters.

3. Division 15 Section "Heating Cables"

4. Division 16 Section "Lightning Protection System".

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, pressure drop, fan performance data, installation instructions, furnished specialties, and accessories.

1. Provide factory certified performance ratings indicating conformance with the operating efficiencies and related characteristics indicated in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.

2. Equipment sound data.

Retain paragraph below if evaporative condensers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  
a. Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Calculate requirements for foundation elements and connections to resist a 44 m/s (100 mph) wind design load.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include handrails, ladders, and equipment mounting frame.

Ensure that layout complies with manufacturers’ recommended clearances from walls and enclosures.

3. Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field piping and wiring connection.

4. Equipment sound data.

5. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Structural supports.

2. Piping and wiring roughing-in requirements (determine spaces reserved for electrical equipment).

3. Access requirements for service and maintenance.

Retain first paragraph below if required by seismic criteria applicable to Project.     Coordinate with Division 15 Section, "Mechanical Vibration and Seismic Controls."

D. Manufacturer Seismic Qualification Certification:  Submit certification that evaporative condensers, accessories, and components will withstand seismic forces defined in Division 15 Section, "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified [and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Operation and Maintenance Data:  For evaporative condensers to include in emergency, operation, and maintenance manuals.

F. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

A. Product Options:  Information on Drawings and in Specifications establishes requirements for system's aesthetic effects and performance characteristics.  Aesthetic effects are indicated by dimensions, arrangements, alignment, and profiles of components and assemblies as they relate to sightlines, to one another, and to adjoining construction.  Performance characteristics are indicated by criteria subject to verification by one or more methods including preconstruction testing, field testing, and in-service performance.

B. ASHRAE Certification:  comply with ASHRAE /IESNA 90.1.

Retain paragraph above or paragraph below.  Retain below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

C. Product Options:  Drawings indicate size, profiles, and dimensional requirements of evaporative condensers and are based on the specific system indicated.  Refer to Division 1 Section, "Product Requirements."

Retain subparagraph below with either "Product Options" paragraph above or revise to suit Project. 

1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain paragraph below if Owner prefers the security of a coil designed and fabricated according to ASME Boiler and Pressure Vessel Code or where state or local codes require it.

E. ASME Compliance:  Fabricate and label heat exchange coils to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

F. Certification: Factory Mutual Research

G. Comply with NFPA 70.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate installation of equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

Edit paragraph below accordingly for new or existing construction.

C. Determine the means and methods necessary to install the equipment specified herein.  For repairs, alterations, additions and other forms of installation of equipment specified in this section into existing conditions, develop a plan including the delivery of the equipment to the site and into the space allocated for the equipment.  Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment to be approved by the contracting officer for this project.  Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment is included in the scope of work for this project.  Repairs and new work required to replace feature of the building or site altered in the process of delivering and installing the equipment are included in the scope of work.

1.6 WARRANTY

When warranties are required, verify with Owner that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section, "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of evaporative condensers that fail in materials or workmanship within specified warranty period:

1. Fan, motor, drive shaft, bearings, and motor supports.

2. Tube bundle.

3. Internal circuit circulating pump.

4. Basin

5. External circuit circulating pump.

6. Integral controls.

7. <Insert other components requiring extended warranty.>

Verify available warranties for units and components and insert number below.

8. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Baltimore Aircoil Company.

2. Evapco, Inc.

3. Recold.

4. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory assembled and  tested, [induced] [forced] draft evaporative condensers.

Retain paragraph below for projects in seismic areas.

B. Fabricate evaporative condenser mounting frame and attachments with reinforcement strong enough to resist evaporative condenser movement during a seismic event when evaporative condenser mounting frame is attached to the building structure.

Provide the following information when it is not shown on the drawings.

C. Evaporative Condenser Characteristics and Capacities:

1. Cooling Capacity:  <Insert kW (Btuh).>

2. Internal Circuit:

a. Refrigerant Type:  <Insert type.>

b. Entering Air Wet Bulb Temperature:  <Insert deg C (deg F).>

c. Condensing Temperature:  <Insert deg C (deg F).>

d. Minimum Heat Rejection:  <Insert kW (Btuh).>

3. External Circuit [Water] [Glycol] Flow:  <Insert L/s (gpm).>

4. Maximum Drift Loss:  <Insert number> percent of external circuit flow.

5. External Circuit Circulating Pump Motor Electrical Characteristics:  [240] [480] <Insert number> V ac, 3 phase, 60 Hz.

6. Number of Fans:  [One] [Two] <Insert number>.

7. Fan Motor Electrical Characteristics:  [240] [480] <Insert number> V ac, 3 phase, 60 Hz.

8. Noise Rating:  <Insert dBA> at <Insert distance in m (feet)>.

9. Basin Heater:  Maintain 4 deg C (40 deg F) external circuit [water] [glycol] temperature at minus 18 deg C (0 deg F) outside air temperature.

2.3 MATERIALS

A. Casing Material:  Stainless steel.

1. Fasteners:  Corrosion resistance equal to or better than materials being fastened.

2. Joints:  Sealed watertight.

3. Welded Connections:  Continuous and watertight.

4. Rigging Supports:  For handling evaporative condensers at construction site.

B. Collection Basin Material:  Stainless steel sheet.

1. Removable strainer with openings smaller than nozzle orifices.

2. Overflow connection.

3. Makeup water connection.

4. Drain Connection:  [Oversized for use with remote sump] [Side] [Bottom].

C. Tube Bundle Material and Construction:  Copper serpentine tubes designed for low pressure drop and free drainage of refrigerant; factory tested at 2400 kPa (350 psig) air pressure while underwater.

Retain one of subparagraphs below.  Note that coil selection might eliminate one or more vendors.

1. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

2. Multiple-circuit coil.

3. Subcooling Coil:  [Minus 12 deg C (Plus 10 deg F)] <Insert deg C (deg F)>.

4. Extended-surface coil.

Retain one of two options below.

D. Drift Eliminator Material:  [PVC with maximum flame spread index of 5 according to ASTM E 84 ][Type 304 stainless steel [sheet]].

E. External Water Distribution System:  Header pipe and removable branch pipes for even distribution of water over the coil.

1. Pipe Material:  Schedule [40, stainless steel] [40, PVC] [80, PVC].

2. Nozzles:  Removable plastic or brass with a maximum pressure drop of 83 kPa (12 psig) <Insert kPa (psig)>.

3. Hot Water Basin Control Valves:  Manufacturer's standard globe valves arranged to balance flow to each distribution basin and shut flow off during servicing.

F. Inlet Screen Material:  Type 304 stainless steel mesh mounted in removable frames.

G. Draft Hood Material:  Type 304 stainless steel [with access door].

2.4 COMPONENTS

Retain one of three paragraphs below if makeup water valve is supplied with evaporative condenser.  Mechanical makeup water valve in first paragraph is most common.

A. Water Level Control:  [Manufacturer's standard mechanical makeup water valve and plastic or bronze float with an adjustable linkage] [Electric float switch and solenoid operated, makeup water valve] [Electronic float switch and solenoid operated, makeup water valve] [Infrared level sensor with electronic control and solenoid operated water valve] with level indicator.

B. Fan(s):  [Type 304 stainless steel, propeller] [Cast aluminum, propeller] [Type 304 stainless steel, centrifugal].

1. Drive:  [Direct] [or] [belt].

2. Bearings:  Self-aligning ball bearings or bronze sleeve bearings with lubrication lines and fittings extended to base of unit.

3. Vibration Cutout Switch:  [Solid state, with adjustable time delay and NEMA 250, Type 4 enclosure] [Mechanical, with manual reset].

C. External Circuit Circulating Pump:  Close coupled, end suction, single stage, [casing wear ring] [impeller wear ring] [all bronze], mechanical seal, centrifugal pump; with a totally enclosed motor; and suitable for outdoor service.

Retain fan-discharge dampers in paragraph below for centrifugal fans if required.

D. Capacity Control Dampers:  Type 304 stainless steel, fan discharge dampers, with linkages, electric damper operator, controller, end switches, transformer, and stainless steel weatherproof enclosure.  Reset dampers to vary airflow through evaporative condenser to control leaving condenser water temperature.

E. Basin Heater:  [Hot water coil] [Electric resistance coil].

F. Basin Depth:   Minimum <Insert Number> mm.

2.5 CONTROLS

A. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.

B. Evaporative condensers shall be interlocked with the Building Automation System (BAS) and be provided with the controls and devices that allow for measuring, monitoring, and controlling energy consumption, and operating efficiencies as prescribed in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.  Evaporative condenser controls shall include a controller with an LED panel capable of calculating and indicating the values required to verify the efficiencies and operating characteristics identified in ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.  Controller shall be remotely mounted indoors.

C. Any evaporative condenser application where the evaporative condenser controls interface with a Building Automation System (BAS) shall have [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility.  Evaporative condenser system shall be provided with a remote mounted controller having [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility.  All controls and control devices associated with the evaporative condenser shall function with [BACnet] [LONtalk/LonWorks] [controls to match existing] compatibility without the need for or use of gateways, product specific or proprietary devices.

D. In addition to controls specified in other sections, provide the following item[s] compatible with main control system:

1. Energy usage meter reporting kilowatt hours 

2.6 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency, are specified in Division 15 Section, "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. Comply with requirements in Division 15 Section, "Motors."

See Evaluations for discussion on enclosure types for various applications.  Retain first paragraph below if enclosure is not open dripproof type.

B. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, air over].

C. Motor Speed:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Inverter type for variable speed controller].

D. All electric motors shall comply with the requirements of ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations 10 CFR 434.

2.7 HANDRAILS, LADDERS, AND PLATFORMS

Requirements for handrails, ladders, and platforms for evaporative condensers depend on condenser height and accessibility of maintenance items.  Edit this Article accordingly.

A. Handrails:  Stainless steel or aluminum complying with 29 CFR 1910.23.  Pipe rail materials and fabrication are specified in Division 5 Section "Pipe and Tube Railings."  

B. Ladders and Safety Cages:  Stainless steel or aluminum complying with 29 CFR 1910.27.  Provide ladder of sufficient height to reach from base to top of unit in its final installation.

C. Platforms:  External, stainless steel with a bar grating floor to provide access to water distribution piping and spray nozzles.

D. Platforms:  Internal, stainless steel with a bar grating floor to provide access to moving parts.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine rough-in for concrete bases, anchor bolt sizes and locations, piping, and electrical to verify actual locations and sizes before evaporative condenser installation and other conditions affecting evaporative condenser performance, maintenance, and operation.

1. Final evaporative condenser locations indicated are approximate.  Determine exact locations before rough-in water piping and electrical connections.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain two paragraphs below for evaporative condensers mounted on grade.

A. Install evaporative condensers on concrete bases.  Concrete base is specified in Division 15 Section, "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Retain paragraph below based on installed equipment.  Coordinate concrete base with Section 15050 requirements.  Indicate dowel rod quantity, size, and spacing on Drawings if evaporative condensers are mounted on vibration isolators.  Delete if retaining vibration isolation equipment bases. 

B. Concrete Bases:  Anchor evaporative condenser to concrete base.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 450 mm (18 inch) centers around full perimeter of the base.

2. For equipment supported on structural slab, install epoxy coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Install anchor bolts according to anchor bolt manufacturer's written instructions.

6. Cast-in-place concrete materials and placement requirements are specified in Division 3.

Retain paragraph below for units mounted on structural steel.  Steel design and specifications are in other sections.

C. Steel supports: Attach unit to structural steel.

D. Ensure a minimum 1.22 m (4 foot) clear space beneath the bottom of the lowest structural member, piping, or sump, to allow re-roofing beneath the unit.

Retain one of four paragraphs below.  Coordinate with Drawings and Division 15 Section, "Mechanical Vibration and Seismic Controls."  Retain first paragraph for equipment supported on slabs-on-grade.

E. Vibration Isolation:  Rubber pads with a minimum deflection of [6.35 mm (0.25 inch)] [<Insert number>mm (<Insert number> inch)].  Vibration isolation devices and installation requirements are specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

F. Vibration Isolation:  Install evaporative condensers with spring isolators per manufacturer's written recommendation.

Based on supporting structure and seismic requirements, insert amount of required deflection in paragraph below.

G. Vibration Isolation:  Restrained spring isolators with a minimum deflection of [25.4 mm (1 inch)] <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

If retaining paragraph below, delete "Concrete Bases" paragraph and subparagraphs above.

H. Vibration Isolation:  Mount evaporative condensers on a vibration isolation equipment base as specified in Division 15 Section, "Mechanical Vibration and Seismic Controls."

I. Maintain manufacturer's recommended clearances for service and maintenance.

J. Loose Equipment:  Install electrical components, devices, and accessories that are not factory mounted.

K. Install lightning protection system as specified in [Division 13][Division 16].
3.3 CONNECTIONS

Coordinate piping installation and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install meter with pulse head on make-up water supply line.

C. Install piping adjacent to evaporative condensers to allow service and maintenance.

D. Install flexible pipe connectors on [condenser] [make-up] [hot water] pipes at final connection of evaporative condensers mounted on vibration isolators.

E. Connect overflow drain and bleed lines to sanitary sewage system.

F. Domestic Water Piping:  Comply with applicable requirements in Division 15 Section, "Domestic Water Piping."  Connect to water level control with shutoff valve and union or flange at each connection.

G. Refrigerant Piping:  Comply with applicable requirements in Division 15 Section, "Refrigerant Piping."  Connect to evaporative condenser coil with isolation valves and union at each connection.

H. Hot Water Piping:  Comply with applicable requirements in Division 15 Section, "Hydronic Piping."  Connect to supply and return basin heater tappings with shutoff valve, strainer, control valve, and union or flange on supply connection and union or flange and balancing valve on return connection.

Retain paragraph below only if evaporative condenser is installed indoors.

I. Ducts:  Comply with applicable requirements in Division 15 Section "Metal Ducts."  Connect ducts to evaporative condenser inlet and outlet, full size of outlet, with flexible duct connection.

J. Ground evaporative condenser according to Division 16 Section "Grounding and Bonding."

K. Connect wiring according to Division 16 Section "Conductors and Cables."

L. Tighten electrical connectors and terminals according to manufacturer's published torque tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

M. Connect to building automation system.

3.4 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”, to perform startup service.

B. Inspect field assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Obtain performance tables from manufacturer.

D. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Clean entire unit including basins.

2. Verify that accessories are properly installed.

3. Check makeup water float.

4. Verify clearances for airflow and for evaporative condenser servicing.

5. Check for vibration isolation and structural support.

6. Lubricate bearings on fans and shafts.

7. Verify fan wheel rotation for correct direction and for vibration or binding.  Correct vibration and binding problems.

8. Adjust belts to proper alignment and tension.

9. Verify water level in basin.  Fill to proper startup level.

10. Start external circuit circulating pumps.

11. Verify operation of unit basin, makeup line, automatic freeze protect dump, and controlling device.  Replace defective and malfunctioning units.

12. Verify operation of basin heater and control thermostat.  Replace defective and malfunctioning units.

13. Verify that unit discharge is not recirculating into air intakes.  Recommend corrective action.

E. Check HVAC water treatment system for proper operation, and measure chemical treatment levels.  Verify operation of evaporative condenser basin automatic blowdown, and controlling device.

F. Start evaporative condenser.  Follow manufacturer's written starting procedures.

G. Prepare a written startup report that records the results of tests and inspections.  Submit within 10 working days.
3.5 ADJUSTING

A. Adjust water level control for proper operating level.

B. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site in assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to site outside normal occupancy hours for this purpose.

3.6 DEMONSTRATION

Engage a factory authorized service representative, as specified under Section 01700 “Execution Requirements”, to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] <Insert Number Here > hours to adjust, operate, and maintain evaporative condensers[ for minimum of [2 ][4 ][6 ]hours].  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15663

EVAPORATIVE CONDENSERS
15663 - 1

