
GSA SUPPLEMENT TO MASTERSPEC(
GSA 03/03


This Section was developed by the U.S. General Services Administration (GSA) as a supplement to MASTERSPEC.  It is based on MASTERSPEC organization, writing style, and model text; and is for ARCOM to distribute to MASTERSPEC Licensed Users for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has included text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA version of Division 1.

SECTION 15990 - TESTING, ADJUSTING, AND BALANCING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Communicate design assumptions, calculations, conditions (both environmental and systems’ output), and philosophies and assumptions about system and equipment controls to TAB firm.  See Evaluations for discussion.  Edit testing requirements to suit Project.

A. This Section includes testing, adjusting, and balancing HVAC systems to produce design objectives, including but not limited to the following:
1. Balancing airflow and water flow within distribution systems, including sub-mains, branches, and terminals, to indicated quantities according to specified tolerances.
2. Adjusting total HVAC systems to provide indicated quantities.
3. Measuring electrical performance of HVAC equipment.
4. Setting quantitative performance of HVAC equipment.
5. Verifying that automatic control devices are functioning properly.
6. Measuring sound and vibration.
7. Reporting results of activities and procedures specified in this Section.
8. Verifying the compliance of equipment to ASHRAE Standard 90.1/99 and ASHRAE Standard 62.99.
9. Verification of performance of equipment during beginning of startup, at mid occupancy and full occupancy before the expiration of the one year warranty period after the beneficial occupancy.
B. Related Sections include the following:
1. Division 15 Section [  ] [Flushing of Hydronic Systems].
2. Division 15 Section [  ] [Sequence of Operations].
3. Division 15 Section [  ] [Temperature Controls].
4. Division 15 Section [  ] [Building Automation Systems].
5. Division 15 Section [  ] [Operations and Maintenance].
6. Division 15 Section [  ] [Air Distribution Equipment and Ductwork].
1.3 DEFINITIONS

Retain acronyms, abbreviations, and definitions that remain after this Section has been edited.

Definitions below are paraphrased from ASHRAE’s Handbooks and ASHRAE 111.

A. DALT:  Duct air leakage test.
B. TAB:  Testing and balancing
C. SMT:  Sound measurement technology:  Defined in AABC MN-1 or NEBB MASV
D. BAS:  Building Automation System
E. IAQ:  Indoor Air Quality
1.4 SUBMITTALS 

Adjust time and number of copies in three paragraphs below to suit Project.  Coordinate with Division 1 Sections.  See Editing Instruction in the Evaluations for timing of submittal requirements.

Coordinate first paragraph with qualification requirements retained in “Quality Assurance” Article.

A. Quality Assurance Submittal:  Within [30] days [   days] of the Contractor’s Notice to Proceed, submit [6] copies of evidence that the testing, adjusting, and balancing team members meet the qualifications specified in the "Quality Assurance" Article below.
B. Contract Documents Examination Report:  Within [45 days] [   days] from the Contractor’s Notice to Proceed, submit [6] copies of the Contract Documents review report as specified in Part 3 of this Section.
1.5 PERFORMANCE REQUIREMENTS

1.6 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Product Data:  For the following:

1. {Insert product.}

2. {Insert product.}

C. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.

D. Strategies and Procedures Plan:  Within [60] [days] from the Contractor’s Notice to Proceed, submit [3 copies] [   copies] of the complete testing, adjusting, and balancing strategies and step-by-step procedures as specified in Part 3, "Preparation" Article below.  Include a complete set of report forms intended for use on this project.
Specify reports required because of editing procedures in Part 3.

E. Certified Testing, Adjusting, and Balancing Reports:  Following completion of TAB submit [X] bound sets of reports prepared as specified in this section, on approved forms certified by the testing, adjusting, and balancing Agent.
Delete paragraph below if standard report forms from AABC, NEBB, or SMACNA are required.  Retain for verification purposes if desired.  Report contents are specified in Part 3.

F. Sample Report Forms:  Submit [6] [  ] copies of sample report forms.
G. Submit a list including calibration data on instruments that will be used to test and balance the systems.
H. System Effect Factors:  Submit System Effect Factors information to be certified for this project.
Warranty submittals should be forwarded to Owner for review and approval by owner’s legal counsel.
I. Warranty:  Submit [6] [  ] copies of special warranty specified in the "Warranty" Article below.
J. Instrumentation calibration of control equipment, valves and dampers.
K. Submit a complete list of instruments that are proposed for use on this project.  The list shall be complete and comprehensive and shall include as a minimum the following:

1. Name of Manufacturer

2. Model Number

3. Serial Number

4. Description of the Instrument

5. Year of Manufacture

6. Manufacturer’s Instructions

7. Calibration Data, including date of last calibration, name of calibrating agency and name of technician.

8. Description of calibration procedure.

9. Photograph of the actual instrument, including carrying case, accessories, tools, and other ancillary items.

1.7 QUALITY ASSURANCE

Retain first paragraph below if certified firms are available or Project scope justifies this requirement.

A. Agent Qualifications:  The Contractor shall engage a testing, adjusting, and balancing Agent certified by [AABC] [NEBB] [AABC or NEBB].
B. The Agent, in addition to meeting the requirements of certification by the specified balancing entities, shall posses credentials indicating a knowledge and familiarity with the ASHRAE publications listed herein.  The Agent personally or the TAB team members collectively shall attend each of the ASHRAE sponsored seminars listed.
C. Certification of Testing, Adjusting, and Balancing Reports:  The TAB Agent shall certify testing, adjusting, and balancing field data reports.  This certification shall include the following:
1. Review field data reports to validate accuracy of data and to prepare certified testing, adjusting, and balancing reports.
2. Certify that testing, adjusting, and balancing team complied with approved testing, adjusting, and balancing plan and procedures specified and referenced in this Specification.
NEBB and SMACNA forms are identical.

D. Testing, Adjusting, and Balancing Reports:  Reports shall use standard forms from [AABC's "National Standards for Testing, Adjusting, and Balancing."] [NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems."] [testing, adjusting, and balancing Agent, approved by the Design Entity.]

Edit first paragraph below if Project scope justifies requirements which can be imposed even if firm certification is not required.

E. Instrumentation Type, Quantity, and Accuracy:  If digital type instruments are available, they shall be used in lieu of analog types.  Otherwise, instruments shall be as described in [AABC national standards.] [NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems," Section II, "Required Instrumentation for NEBB Certification."]

F. Instrumentation Calibration:  Instruments shall have been calibrated at least within the last six months or more recently if required by the instrument manufacturer.
G. Comply with the following:
1. ASSOCIATED AIR BALANCE COUNSCEL (AABC)

2. AIR MOVEMENT AND CONTROL ASSOCIATION, INC. (AMCA)

3. AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

4. AMERICAN SOCIETY OF HEATING, REFRIGERATING, AND AIR CONDITIONING ENGINEERS, INC. (ASHRAE)

5. COOLING TOWER INSTITUTE (CTI)

6. NATIONAL ENVIRONMENTAL BALANCING BUREAU (NEBB)

7. SHEET METAL & AIR CONDITIONING CONTRACTORS’ NATIONAL ASSOCIATION, INC. (SMACNA)

1.8 PROJECT CONDITIONS

Retain one of three paragraphs below.

A. [Full Owner Occupancy:  The Owner intends to occupy the site and existing building during the entire testing, adjusting, and balancing period.  The Contractor shall cooperate with the Owner during testing, adjusting, and balancing operations to minimize conflicts with the Owner's operations.]
B. [Partial Owner Occupancy:  The Owner may occupy completed areas of the building before Substantial Completion.  Cooperate with the Owner during testing, adjusting, and balancing operations to minimize conflicts with the Owner's operations.]
C. [No Owner Occupancy until final acceptance:  The Owner intends to occupy the building only after construction is 100% complete and the building has been accepted.]
1.9 EXISTING SYSTEMS

A. When air and water systems are added to the existing systems in a repair, alteration or addition, contractor shall balance the existing system to the extent required so that the added system[s] operate properly.
1.10 COORDINATION
A. The TAB Agent shall coordinate the efforts of factory authorized service representatives for systems and equipment, HVAC controls installers, and other mechanics to operate the HVAC systems and equipment to support and assist testing, adjusting, and balancing activities.
B. Testing, adjusting, and balancing shall be performed only after leakage and pressure tests on air and water distribution systems have been satisfactorily completed and approved by the Design Entity.
C. Modifications to the systems shall only be made after approval of the Architect/Engineer has been obtained in writing.  This includes changing equipment speeds and installation of additional testing devices and instruments.
1.11 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

Retain paragraph below if AABC standards are used.

A. National Project Performance Guarantee:  The TAB Agent shall provide a guarantee on AABC'S "National Standards" forms stating that AABC will assist in completing the requirements of the Contract Documents if the testing, adjusting, and balancing Agent fails to comply with the Contract Documents.  Guarantee shall include the provisions specified in paragraph 1 and paragraph 2 below.
Retain paragraph below if NEBB or SMACNA standards are used.

B. Special Guarantee:  A guarantee on NEBB forms shall be furnished stating that NEBB will assist in completing the requirements of the Contract Documents if the testing, adjusting, and balancing Agent fails to comply with the Contract Documents.  Guarantee shall include the provisions specified in paragraph 1 and paragraph 2 below:
Retain both subparagraphs below with either paragraph above.

1. The certified TAB Agent has tested and balanced systems according to the Contract Documents during the startup, mid-occupancy, and full occupancy before the warranty period expires.
2. The systems are balanced to optimum performance capabilities within the design and installation limits of the systems and equipment and shall conform to ASHRAE Standard 90.1.99.
PART 2 -  PRODUCTS

2.1 SHEAVES AND BELTS
A. The TAB Agent shall be responsible for providing and installing new fan sheaves and belts when required to obtain the designed air flow.
2.2 AIR FILTERS 

A. The TAB Agent shall be responsible for providing and installing new, clean air filters.  Filters shall be installed before final inspection and before giving notice for the testing, adjusting and balancing.
2.3 BALANCING INSTRUMENTS

A. General: Instruments shall be manufactured by companies regularly engaged in the manufacture of precision instruments of the specific type for a minimum of 10 years.  Use of shop-made instruments or use of instruments modified from their original configuration is prohibited.  Use of instruments not in manufacture for 10 years is specifically prohibited.  Submit data on instruments as specified in submittals paragraph above.
B. Air Flow Measuring Instruments:  Instruments used to measure airflow shall be of the Pitot tube type, hot wire anemometer type, turban type, or vortex shedding type.

1. Airflow from air distribution devices shall be measured using an airflow hood with grid type Pitot tube sensing element and inclined liquid manometer for output.  The manometer shall be scaled in inches of water column and a conversion chart prepared to convert the readings to air flow in cubic feet per minute at the site elevation and atmospheric conditions.

2. Airflow in ducts shall be measured using precision Pitot tubes and inclined liquid manometers for output.  The output from the manometer shall be scaled as specified above.  Traverses in the duct shall be as prescribed by ASHRAE or SMACNA.

C. Water Flow Measuring Instruments:  Instruments used to measure water or other liquid flow shall be of the Pitot type, orifice type, venturi type, nozzle type, variable area type, or vortex shedding type.

1. Each type of device shall be installed in the liquid conveyance system in strict accordance with the manufacturer’s instructions and recommendations or in accordance with the data contained in ASHRAE publications, whichever is most stringent.

2. Output instruments shall read in basic values such as inches of mercury, feet of water, pulses per second, etc., and then be converted to an appropriate value.  The reading shall be corrected for temperature, pressure, altitude, etc., to obtain true values.

D. Temperature Measuring Instruments:  Instruments used to measure temperature shall be one of the types described below.  Use of bimetallic thermometers is prohibited.  Mercury or alcohol-filled glass tube thermometers may be used when temperature changes are 0 or less than 1 degree F per hour.  Thermometers shall be high quality and have a correction chart furnished with it for temperatures on either side of its true calibration point.

1. Variable resistance devices, RTD’s, thermistors, etc., shall be used when temperatures may vary more than 1 degree F per hour.  Readings shall be taken using an electronic balanced bridge and meter arrangement.  Direct reading instruments are prohibited.  Hot wire anemometers may be used in varying temperature situations provided each of the components are a factory-matched assembly.

2. When required or at the contractor’s option, thermocouples may be used to measure temperature.  An electronic balanced bridge shall be used for output as described above.

2.4 PRESSURE MEASURING INSTRUMENTS 

A. Instruments used to measure pressure shall be the liquid manometer type, bourdon tube type, precision transducer type, strain gauge type, or dead weight, piston and cylinder type.
B. Manometers using water or alcohol shall be used to measure low pressures or differential pressures in the zero to 60 inches of water range.
C. Manometers utilizing mercury shall be used to measure pressures in the zero to 60 inches of mercury range.
D. Bourdon tube type pressure gauges, precision transducers, strain gauges, and deadweight type instruments shall be used for pressures 10 psi and above or –5 psi and below.  Compound gauges shall not be used to measure pressures below atmospheric.
E. Atmospheric pressure shall be measured by using a mercury barometer.
2.5 HUMIDITY MEASURING INSTRUMENTS 

A. Instruments used to measure humidity shall be of the precision electronic type or the use of a sling psychrometer may be used.
2.6 ROTARY SPEED MEASURING INSTRUMENTS 

A. Rotary speeds, generally in RPM, shall be measured using a precision, magnetic direct reading tachometer, strobic effect type electronic tachometer or a revolution counter with stopwatch.
B. When rotary speed is expected to vary as in variable speed equipment, strobic effect devices or electronic tachometers shall be used.
2.7 ELECTRICAL MEASURING INSTRUMENTS

A. Electrical measurements shall be taken with precision, solid state, electronic devices.  Voltage, amperage, wattage and power factor readings shall utilize digital output type reading and recording instruments.
B. [Facilities housing sensitive electronic equipment such as computers, electron microscopes, electronic medical instruments, etc., shall have an analysis conducted to determine the quality of the incoming power and the quality of the power downstream of filtering equipment.]
2.8 ENERGY MEASURING INSTRUMENTS

A. Energy Measurements shall not be made directly except for watt hour measuring devices.  Energy shall be calculated using measured values as specified above
2.9 COMBUSTION PRODUCTS MEASUREMENTS

A. Fuel burning equipment effluent analysis shall be made using equipment based on the Orsat analysis method.
PART 3 -  EXECUTION

3.1 EXAMINATION

See Editing Instruction in the Evaluations for discussion of the Contract Documents review.

A. The TAB Agent shall examine the Contract Documents to become familiar with the project requirements and to discover conditions in the systems' designs that may preclude proper testing, adjusting, and balancing of systems and equipment and for verifying compliance with ASHRAE Std. 90.1.
Verify that first subparagraph below is correct for this Project.  Statement is true if AIA standard documents are used correctly.

1. The TAB Agent shall, prior to bidding, verify that balancing devices, such as test ports, gage cocks, thermometer wells, flow control devices, flow metering devices, balancing valves and fittings, and manual volume dampers, necessary for proper TAB, are required by, specified in or shown on the Contract Documents.  Prior to starting the TAB, verify that quantities and locations of these balancing devices are accessible and appropriate for effective balancing and for efficient system and equipment operation, and to validate the ASHRAE 90.1 Standard.

B. Approved submittal data of HVAC systems and equipment shall be examined and discrepancies shall be identified.
C. Project Record Documents described in Division 1 Section "Project Record Documents" shall be examined and discrepancies shall be identified.
See “Design Data” Article in the Evaluations.

D. Equipment performance data, including fan and pump curves shall be examined.  The TAB Agent shall examine and compare the performance data to Project conditions and requirements, including system effects that may create undesired or unpredicted conditions that cause reduced capacities in the entire or part of a system.  Calculate system effect factors that might reduce performance ratings of HVAC equipment when installed under conditions different from those presented when equipment was performance tested at the factory.  To calculate system effects for air systems, use tables and charts found in AMCA 201, "Fans and Systems," Sections 7 through 10; or in SMACNA's "HVAC Systems--Duct Design," Sections 5 and 6.  Examine and note items preventing compliance with ASHRAE Standard 90.1, AHSRAE Standard 62-99, and ASHRAE Standard 135.  Compare this data with design data and installed conditions and submit for examination by the Design Entity.  The TAB results shall include ASHRAE Standard 90.1/99 compliance with regards to EER, equipment energy consumption, and system efficiency.
E. System and equipment installations shall be examined to verify that they are complete and that testing, cleaning, flushing, adjusting, and commissioning specified in other individual Specification Sections have been performed and shall also be submitted in the TAB report.
F. System and equipment test reports shall be examined.
G. HVAC system and equipment installations shall be examined to verify that indicated balancing devices, such as test ports, gage cocks, thermometer wells, flow control devices, balancing valves and fittings, and manual volume dampers, are properly installed, and their locations are accessible and appropriate for effective balancing and for efficient system and equipment operation.
H. Systems shall be examined for functional deficiencies that cannot be corrected by adjusting and balancing.
I. Air handling equipment shall be examined to ensure clean filters have been installed, bearings are properly lubricated, belts are aligned and properly tensioned, and equipment with functioning controls is ready for operation.
J. Each terminal unit, such as variable air volume boxes and mixing boxes shall be examined to verify that they are accessible and their controls are connected and functioning properly.
K. Examine plenum ceilings, utilized for supply return or relief air, to verify that they are airtight and properly separated from adjacent areas.  Verify that pipe penetrations and other holes are sealed and fire stopped.
L. Examine strainers for clean screens, proper perforations and correct materials.
M. Examine three-way valves for proper installation for their intended function of diverting or mixing fluid flows and for proper failsafe positioning.
N. Examine heat transfer coils for correct piping connections, airflow direction and for clean and straight fins.
O. Examine open piping system pumps to ensure the absence of entrained air in suction piping.
P. Examine equipment for proper installation and for properly installed operating safety interlocks, controls and mechanical guards.
Q. Contractor to provide control system performance results after the part occupancy and before the warranty period expires.  The report shall be interim and final.  Examine the automatic temperature control system components to verify the following during the part load and full load conditions:
1. Dampers, valves, and other controlled devices operate by the intended controller.  
2. Dampers and valves are in the position indicated by the controller.
3. Installation of valves and dampers are correct for free and full operation and for tightness of fully closed and fully open positions.  This includes dampers in multi-zone units, mixing boxes, and variable air volume terminals.
4. Automatic modulating and shutoff valves, including two-way valves and three-way mixing and diverting valves, are properly connected, piped and have the required accessories.
5. Thermostats and humidistats are located to avoid adverse effects of sunlight, drafts, and cold walls.
6. Sensors are located to sense only the intended conditions.
7. Sequence of operation for control modes is according to the Contract Documents.
8. Controller set points are set at design values.  Observe and record system reactions to changes in conditions.  Record default set points if different from design values.
9. Interlocked systems are operating as intended or as required.
10. Changeover from heating to cooling mode occurs according to design values.
R. Report deficiencies discovered before and during performance of testing, adjusting, and balancing procedures.  Do not proceed until directed by the Design Entity.
S. Examine closed hydronic systems to determine if automatic air vents are installed at each of the high points and are operating properly.
3.2 PREPARATION

A. The TAB Agent shall prepare a testing, adjusting, and balancing plan that includes strategies and step-by-step procedures.
B. System readiness checks shall be determined as complete and a system readiness report shall be prepared, submitted and approved before proceeding.  Verify the following:
1. Permanent electrical power wiring is complete.
2. Hydronic systems have been cleaned and completely flushed in accordance with Section [15…], are filled and free of air.
3. Automatic temperature control systems are operational and functional from fully open to completely closed.
4. Equipment and duct access doors are securely closed.
5. Balancing, smoke, and fire dampers are open.
6. Isolating and balancing valves are open and control valves are operational.
7. Ceilings are installed in each of the areas where air pattern adjustments are required and access to balancing devices has been provided.
8. Windows and doors can be closed so design conditions for system operations can be met.
9. Strainers have been cleaned prior to testing.
3.3 TESTING AND BALANCING PROCEDURES 

A. The TAB Agent shall perform testing and balancing procedures on each system according to the procedures contained in [AABC Test and Balance Procedures] [NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems."] [SMACNA's "HVAC Systems--Testing, Adjusting, and Balancing."] and as specified herein.
B. Cut insulation, ducts, pipes, and equipment cabinets for installation of test probes to the minimum extent necessary to allow adequate performance of procedures.  After testing and balancing, close probe holes and patch insulation with new materials identical to those removed.  Restore vapor barrier and finish according to the insulation Specifications for this Project.
C. Mark equipment settings with paint or other suitable, permanent identification material, including damper control positions, valve indicators, fan speed control levers, and similar controls and devices, to show final settings.
3.4 TOLERANCES 

A. Set HVAC system airflow and water flow rates within the following tolerances:  
1. Supply, Return, and Exhaust Fans:  Plus 5 to plus 10 percent.
2. Air Outlets and Inlets:  0 to minus 10 percent.
3. Heating-Water Flow Rate:  0 to minus 10 percent.
4. Cooling-Water Flow Rate:  0 to minus 5 percent.  
B. Equipment capacities shall be adjusted in accordance with the following:
1. Fan capacities shall be adjusted by changing fan speeds provided the adjustment does not result in increasing the energy consumption beyond 10%.  Obtain approval from the Design Entity prior to making permanent changes.  Verify that changing speeds will not result in unstable or noisy operation of the system.
2. Pump capacities shall be adjusted by position balancing valves on the discharge side of the pump.  If valve positioning results in 10% or more of an increase in pump head, verify from the pump curve data that the efficiency of the pump has not decreased by more than 5%.  Evaluate and recommend in the report whether another impeller size would result in satisfactory operation and increased efficiency.
3.5 AIR DISTRIBUTION SYSTEMS SETTINGS AND TESTING

A. Air distribution devices may be balanced using a flow measuring hood as permitted by [AABC Test and Balance Procedures.] [NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems."] [SMACNA's "HVAC Systems--Testing, Adjusting, and Balancing."]  Dampers further from the air distribution device shall be set first.  Dampers within the device shall be used for final airflow settings to minimize noise generation.
B. Each air supply device shall be checked to determine that conditioned air supplied to the space is in the correct direction and proportion for the device as shown on the plans.  For example, a 4-way pattern ceiling diffuser should deliver 25% of the total airflow in each of the four quadrants.  The airflow pattern shall be measured by use of a velometer, hot wire anemometer or vortex shedding, airflow measuring instrument.  A tolerance of plus or minus 10% in each direction will be acceptable.  Variations in excess of 10% shall be corrected by baffles inside the diffuser or device, provided excessive noise is not generated.  Linear diffusers, designated as having a bi-directional pattern shall be checked as described above.  Devices with single direction distribution shall be checked for proper air flow spread and drop as indicated by the plans.
C. A minimum of 10% of the total amount of spaces, but not less than 10, shall be tested shall be tested for proper air diffusion in accordance with ASHRAE Std. 113. Spaces that are unique or substantially different in size or configuration from other spaces shall also be tested as directed by the Owner.
3.6 FUNDAMENTAL AIR SYSTEMS' BALANCING PROCEDURES
A. Prepare test reports for both fans and outlets.  Obtain manufacturer's outlet factors and recommended testing procedures.  Crosscheck the summation of required outlet volumes with required fan volumes.
B. Prepare schematic diagrams of systems' "as-built" duct layouts.
C. For variable air volume systems, develop a plan to simulate diversity.
D. Determine the best locations in main and branch ducts for accurate duct airflow measurements.
E. Check the airflow patterns from the outside air louvers and dampers and the return and exhaust air dampers, through the supply fan discharge and mixing dampers.
F. Locate start-stop and disconnect switches, electrical interlocks, and motor starters.
G. Verify that motor starters are equipped with properly sized thermal protection.
H. Check dampers for proper position to achieve desired airflow path.
I. Check for airflow blockages.
J. Check condensate drains for proper connections and functioning.
K. Check for proper sealing of air handling unit components.
3.7 CONSTANT VOLUME AIR SYSTEMS' BALANCING PROCEDURES

The procedures in this Article apply to constant-volume supply-, return-, and exhaust-air systems.  Additional procedures are required for variable-air-volume, multizone, dual-duct, induction-unit supply-air systems and process exhaust-air systems.  These additional procedures are specified in other articles in this Section.

A. Adjust fans to deliver total design airflows within the maximum allowable rpm listed by the fan manufacturer.
B. Measure fan static pressures to determine actual static pressure as follows:
1. Measure outlet static pressure as far downstream from the fan as practicable and upstream from restrictions in ducts such as elbows and transitions.
2. Measure static pressure directly at the fan outlet or through the flexible connection.
First two subparagraphs below may require changes to installed systems or equipment; these changes may require a contract modification.

3. Measure inlet static pressure of single inlet fans in the inlet duct as near the fan as possible, upstream from flexible connection and downstream from duct restrictions.
See Evaluations for discussion of fan speed adjustments.

4. Measure inlet static pressure of double inlet fans through the wall of the plenum that houses the fan.
5. Measure static pressure across each air handling unit component.
C. Simulate dirty filter operation and record the point at which maintenance personnel must change filters.
D. Measure static pressures entering and leaving other devices such as sound traps, heat recovery equipment, and air washers under final balanced conditions.
The 2 subparagraphs below may require changes to installed systems or equipment and may require a contract modification.

E. Compare design data with installed conditions to determine variations in design static pressures versus actual static pressures.  Compare actual system effect factors with calculated system effect factors to identify where variations occur.  Recommend corrective action to align design and actual conditions.
See Editing Instruction No. 3 in the Evaluations for discussion on fan-speed adjustments.

F. Adjust fan speed higher or lower than design with the approval of the Architect.  Make required adjustments to pulley sizes, motor sizes, and electrical connections to accommodate fan speed changes.
G. Do not make fan speed adjustments that result in motor overload.  Consult equipment manufacturers about fan speed safety factors.  Modulate dampers and measure fan motor amperage to ensure no overload will occur.  Measure amperage in full cooling, full heating, and economizer modes to determine the maximum required brake horsepower.
H. Adjust volume dampers for main duct, sub-main ducts, and major branch ducts to design airflows within specified tolerances.
I. Measure static pressure at a point downstream from the balancing damper and adjust volume dampers until the proper static pressure is achieved.
J. Where sufficient space in sub-mains and branch ducts is unavailable for Pitot tube traverse measurements, measure airflow at terminal outlets and inlets and calculate the total airflow for that zone.
K. Remeasure each sub-main and branch duct after each have been adjusted.  Continue to adjust sub‑mains and branch ducts to design airflows within specified tolerances.
L. Measure terminal outlets and inlets without making adjustments.
M. Measure terminal outlets using a direct reading hood or the outlet manufacturer's written instructions and calculating factors.
N. Adjust terminal outlets and inlets for each space to design airflows within specified tolerances of design values.  Make adjustments using volume dampers rather than extractors and the dampers at the air terminals.
O. Adjust each outlet in the same room or space to within specified tolerances of design quantities without generating noise levels above the limitations prescribed by the Contract Documents.
P. Adjust patterns of adjustable outlets for proper distribution without drafts.
3.8 DUAL DUCT SYSTEM ADDITIONAL PROCEDURES 

Retain this Article if dual duct systems are used.

Delete this Article if no dual-duct systems are used.  Select type of dual-duct system from paragraphs below and delete system types not used.

A. Set mixing boxes at full cold airflow position for setting the fan volume, after verifying that the cooling coil is capable of full system airflow.
B. Measure static pressure in both hot and cold ducts at the end of the longest duct run to determine that sufficient static pressure exists to operate mixing box controls and to overcome resistance in the ducts and outlets downstream from mixing box.
C. If insufficient static pressure exists, increase the airflow at the fan.
D. Test and adjust the constant volume mixing boxes as follows:
1. Verify both hot and cold operations by adjusting the thermostat and observing the air temperature and volume changes.
2. Verify sufficient inlet static pressure before making volume adjustments.
3. Adjust mixing box to design airflows within specified tolerances.  Measure the airflow by Pitot tube traverse readings, totaling the airflow of the outlets; or by measuring static pressure at mixing box taps if provided by the box manufacturer.
E. Remeasure static pressure in both hot and cold ducts at the end of the longest duct run to determine that sufficient static pressure exists to operate mixing box controls and to overcome resistance in the ducts and outlets downstream from mixing box.
F. Adjust variable air volume, dual duct systems in the same way as constant volume dual duct systems, and adjust each mixing box maximum and minimum airflow settings.
3.9 VARIABLE AIR VOLUME SYSTEM ADDITIONAL PROCEDURES 

Retain this Article if variable air volume systems are used.

A. Compensating for Diversity:  When the total airflow of the combined total of the terminal units is more than the fan design airflow volume, place a selected number of terminal units at a maximum set point airflow condition until the total airflow of the terminal units equals the design airflow of the fan.  Select the reduced airflow terminal units so they are distributed evenly among the branch ducts.
B. Pressure Independent, Variable Air Volume Systems:  After the fan systems have been adjusted, adjust the variable air volume systems as follows:
1. Set outside air dampers at minimum, and return and exhaust air dampers at a position that simulates full cooling load.
2. Select the terminal unit that is most critical to the supply fan airflow and static pressure.  Measure static pressure.  Adjust system static pressure so the entering static pressure for the critical terminal unit is not less than the sum of the terminal unit manufacturer's recommended minimum inlet static pressure plus the static pressure needed to overcome terminal unit discharge duct losses.
3. Measure total system airflow.  Adjust to within 10 percent of design airflow.
4. Set terminal units at maximum airflow and adjust controller or regulator to deliver the designed maximum airflow.  Use the terminal unit manufacturers written instructions to make this adjustment.  When total airflow is correct, balance the air outlets downstream from terminal units as described for constant volume air systems.
5. Set terminal units at minimum airflow and adjust controller or regulator to deliver the designed minimum airflow.  Check air outlets for a proportional reduction in airflow as described for constant volume air systems.
C. If air outlets are out of balance at minimum airflow, report the condition but leave the outlets balanced for maximum airflow.
1. Remeasure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow.  Adjust the fan and balance the return air ducts and inlets as described for constant volume air systems.
2. Measure static pressure at the most critical terminal unit and adjust the static pressure controller at the main supply air sensing station to ensure adequate static pressure is maintained at the most critical unit.
3. Record the final fan performance data.
D. Pressure Dependent, Variable Air Volume Systems without Diversity:  After the fan systems have been adjusted, adjust the variable air volume systems as follows:
1. Balance systems similar to constant volume air systems.
2. Set terminal units and supply fan at full airflow condition.
3. Adjust inlet dampers of each terminal unit to design airflow and verify operation of the static pressure controller.  When total airflow is correct, balance the air outlets downstream from terminal units as described for constant volume air systems.
4. Readjust fan airflow for final maximum readings.
5. Measure operating static pressure at the sensor that controls the supply fan, if one is installed, and verify operation of the static pressure controller.
Retain first subparagraph below if static pressure controller is used.

Delete subparagraph below if no static-pressure controller is used in system.

6. Set supply fan at minimum airflow if minimum airflow is indicated.  Measure static pressure to verify that it is being maintained by the controller.
7. Set terminal units at minimum airflow and adjust controller or regulator to deliver the designed minimum airflow.  Check air outlets for a proportional reduction in airflow as described for constant volume air systems.
E. If air outlets are out of balance at minimum airflow, report the condition but leave the outlets balanced for maximum airflow.
F. Measure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow.  Adjust the fan and balance the return air ducts and inlets as described for constant volume air systems.
G. Pressure Dependent, Variable Air Volume Systems with Diversity:  After the fan systems have been adjusted, adjust the variable air volume systems as follows:
1. Set system at maximum design airflow by setting the required number of terminal units at minimum airflow.  Select the reduced airflow terminal units so they are distributed evenly among the branch ducts.
2. Adjust supply fan to maximum design airflow with the variable airflow controller set at maximum airflow.
3. Set terminal units being tested at full airflow condition.
4. Adjust terminal units starting at the supply fan end of the system and continuing progressively to the end of the system.  Adjust inlet dampers of each terminal unit to design airflow.  When total airflow is correct, balance the air outlets downstream from terminal units as described for constant volume air systems.
5. Adjust terminal units for minimum airflow.
Retain first subparagraph below if static pressure controller is used.

Delete subparagraph below if static-pressure sensor is not installed.

6. Measure static pressure at the sensor.
7. Measure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow.  Adjust the fan and balance the return air ducts and inlets as described for constant volume air systems.
3.10 MULTI-ZONE SYSTEM ADDITIONAL PROCEDURES
Retain this Article if multi-zone systems are used.
Delete this Article if no multizone units are used.

A. Set unit at full flow through the cooling coil if coil has that capacity.
B. Adjust each zone damper to design airflow.
3.11 INDUCTION UNIT SYSTEM ADDITIONAL PROCEDURES 

Retain this Article if induction units are used.
Delete this Article if no induction units are used.

A. Balance primary air risers by measuring static pressure at the nozzles of the top and bottom units of each riser to determine which risers must be throttled.  Adjust risers to design airflow within specified tolerances.
B. Adjust each induction unit.
3.12 FUNDAMENTAL PROCEDURES FOR HYDRONIC SYSTEMS 

A. Prepare test reports with pertinent design data and number in sequence starting at pump to end of system.  Check the sum of branch circuit flows against approved pump flow rate.  Correct variations that exceed plus or minus 5 percent.
B. Prepare schematic diagrams of systems' "as-built" piping layouts.
C. Prepare hydronic systems for testing and balancing according to the following, in addition to the general preparation procedures specified above:
1. Open each of the manual valves for maximum flow.
2. Check expansion tank liquid level.
3. Check makeup water station pressure gage for adequate pressure for highest vent.
4. Check flow control valves for specified sequence of operation and set at design flow.
5. Set differential pressure control valves at the specified differential pressure.  Do not set at fully closed position when pump is positive displacement type, unless several terminal valves are kept open.
6. Set system controls so automatic valves are wide open to heat exchangers.
7. Check pump motor load.  If motor is overloaded, throttle main flow balancing device so motor nameplate rating is not exceeded.
8. Check air vents for a forceful liquid flow exiting from vents when manually operated.
3.13 HYDRONIC SYSTEM BALANCING PROCEDURES 

A. Determine water flow at pumps.  Use the following procedures, except for positive displacement pumps:
1. Verify impeller size by operating the pump with the discharge valve closed.  Verify with the pump manufacturer that this will not damage pump.  Read pressure differential across the pump.  Convert pressure to head and correct for differences in gage heights.  Note the point on the manufacturer's pump curve at zero flow and confirm that the pump has the intended impeller size.

2. Check system resistance.  With each of the valves in the open position, read pressure differential across the pump and mark the pump manufacturer's head capacity curve.  Adjust pump discharge valve until design water flow is achieved.
3. Verify pump motor brake horsepower.  Calculate the intended brake horsepower for the system based on the pump manufacturer's performance data.  Compare calculated brake horsepower with nameplate data on the pump motor.  Report conditions where actual amperage exceeds motor nameplate amperage.
4. Report flow rates that are not within plus or minus 5 percent of design.
B. Set calibrated balancing valves, if installed, at calculated presettings.

C. Measure flow at each of the stations and adjust, where necessary, to obtain first balance.
D. System components that have Cv rating or an accurately cataloged flow pressure drop relationship may be used as a flow indicating device.
E. Measure flow at main balancing station and set main balancing device to achieve flow that is 5 percent greater than design flow.
F. Adjust balancing stations to within specified tolerances of design flow rate as follows:
1. Determine the balancing station with the highest percentage over design flow.
2. Adjust each station in turn, beginning with the station with the highest percentage over design flow and proceeding to the station with the lowest percentage over design flow.
3. Record settings and mark balancing devices.
G. Measure pump flow rate and make final measurements of pump amperage, voltage, rpm, pump heads, and systems' pressures and temperatures, including outdoor air temperature.
H. Measure the differential pressure control valve settings existing at the conclusions of balancing.
3.14 VARIABLE FLOW HYDRONIC SYSTEM ADDITIONAL PROCEDURES
A. Balance systems with automatic 2- and 3-way control valves by setting systems at maximum flow through heat exchange terminals and proceed as specified above for hydronic systems.
3.15 PRIMARY-SECONDARY FLOW HYDRONIC SYSTEM ADDITIONAL PROCEDURES

A. Balance the primary system crossover flow first, then balance the secondary system.
3.16 HEAT EXCHANGERS

A. Measure water flow through each of the circuits.
B. Adjust water flow to within specified tolerances.
C. Measure inlet and outlet water temperatures.
D. Measure inlet steam pressure.  Check the setting and operation of automatic temperature control valves, self-contained control valves, and pressure-reducing valves.
E. Record safety valve settings.
F. Verify operation of steam traps.
3.17 MOTORS

A. Motors, 1/2 HP and Larger:  Test at final balanced conditions and record the following data:
1. Manufacturer, model, and serial numbers.
2. Motor horsepower rating.
3. Motor rpm.
4. Efficiency rating if high efficiency motor.
5. Nameplate and measured voltage, each phase.
6. Nameplate and measured amperage, each phase.
7. Starter thermal protection element rating.
B. Motors Driven by Variable Frequency Controllers:  Test for proper operation at speeds varying from minimum to maximum.  Test the manual bypass for the controller to prove proper operation.  Record observations, including controller manufacturer, model and serial numbers, and nameplate data.
3.18 CHILLERS

A. Balance water flow through each evaporator and condenser to within specified tolerances of design flow with each of the pumps operating simultaneously.  With only one chiller operating in a multiple chiller installation, do not exceed the flow for the maximum tube velocity recommended by the chiller manufacturer.  Measure and record the following data with each chiller operating at design conditions:
1. Evaporator water entering and leaving temperatures, pressure drop, and water flow.
2. Condenser water entering and leaving temperatures, pressure drop, and water flow.
3. Evaporator and condenser refrigerant temperatures and pressures, using instruments furnished by the chiller manufacturer.
4. Power factor if factory-installed instrumentation is furnished for measuring kW.
5. The kW input if factory-installed instrumentation is furnished for measuring kW.
6. Capacity:  Calculate in tons of cooling.
7. Air Cooled Chillers:  Verify condenser fan rotation and record fan data, including number of fans and entering and leaving air temperatures.
3.19 COOLING TOWERS

Tests below do not qualify as a CTISTD-105, “Acceptance Test Code.”  If a CTI test of cooling tower is specified in cooling tower Section, delete this Article.

Tests below do not qualify as a CTI STD-103 "Acceptance Test Code."  If a CTI test of cooling tower is specified in cooling tower Section, delete this Article.

A. Shut off makeup water for the duration of the test, and then make sure the makeup and blow-down systems are fully operational after tests and before leaving the equipment.  Perform the following tests and record the results:
1. Measure condenser water flow to each cell of the cooling tower.
2. Measure entering and leaving water temperatures.
3. Measure wet and dry bulb temperatures of entering air.
4. Measure wet and dry bulb temperatures of leaving air.
5. Measure condenser water flow rate recirculating through the cooling tower.
6. Measure cooling tower pump discharge pressure.
7. Adjust water level and feed rate of makeup water system.
3.20 CONDENSING UNITS

A. Verify proper rotation of fans and measure entering and leaving air temperatures.  Record compressor data.
3.21 BOILERS

A. Measure entering and leaving water temperatures and water flow.
3.22 HEAT TRANSFER COILS

A. Water Coils:  Measure the following data for each coil:
1. Entering and leaving water temperatures.
2. Water flow rate.
3. Water pressure drop.
4. Dry bulb temperatures of entering and leaving air.
5. Wet bulb temperatures of entering and leaving air for cooling coils designed for less than 3540 L/s (7500 cfm).
6. Airflow.
7. Air pressure drop.
B. Electric Heating Coils:  Measure the following data for each coil:
1. Nameplate data.
2. Airflow.
3. Entering and leaving air temperatures at full load.
4. Voltage and amperage input of each phase at full load and at each incremental stage.
5. Calculated kW at full load.
6. Fuse or circuit breaker rating for overload protection.
3.23 TEMPERATURE TESTING

A. During testing, adjusting, and balancing, report need for adjustment in temperature regulation within the automatic temperature control system.
B. Measure indoor wet and dry bulb temperatures every other hour for a period of two (2) successive 8-hour days, in each separately controlled zone, to prove correctness of final temperature settings.  Measure when the building or zone is occupied.
C. Measure outside air, wet and dry bulb temperatures.
3.24 FUME HOODS

A. Determine total airflow into the room where the fume hood is located and balance systems to ensure adequate air supply to each hood.
1. Set fume hood door opening at position of normal use.

2. Energize the exhaust fan and adjust airflow to provide the indicated average fume hood face velocity at hood opening.

3. Measure exhaust airflow volume by measuring airflow by Pitot tube duct traverse.

4. Measure air velocity using Pitot tube traverse method.

5. Record each face velocity measurement taken at 100- to 150-mm (4- to 6-inch) increments over the entire hood door opening.
6. Calculate the average face velocity by averaging each of the velocity measurements.
7. Calculate the airflow volume of exhaust-hood face velocity by multiplying the calculated average face velocity by the opening area.  Compare this quantity with exhaust volume at exhaust fan and report duct leakage.
8. Measure airflow volume supplied by makeup fan.  Verify that the makeup system supplies the proper amount of air to keep the space at the indicated pressure with the exhaust systems in each operating condition.
9. Retest for average face velocity.  Adjust hood baffles, fan drives, and other parts of the system to provide the indicated average face velocity and the indicated auxiliary air supply percentages.
10. Retest and adjust the systems until fume hood performance complies with Contract Documents.
3.25 TEMPERATURE CONTROL VERIFICATION

A. Verify that controllers are calibrated and commissioned.
B. Check transmitter and controller locations and note conditions that would adversely affect control functions.
C. Record controller settings and note variances between set points and actual measurements.
D. Verify operation of limiting controllers; i.e., high and low temperature controllers.
E. Verify free travel and proper operation of control devices such as damper and valve operators.
F. Verify sequence of operation of control devices.  Note air pressures and device positions and correlate with airflow and water flow measurements.  Note the speed of response to input changes.
G. Confirm interaction of electrically operated switch transducers.
H. Confirm interaction of interlock and lockout systems.
I. Verify main control supply air pressure and observe compressor and dryer operations.
J. Record voltages of power supply and controller output.  Determine if the system operates on a grounded or nongrounded power supply.
K. Note operation of electric actuators using spring return for proper failsafe operations.
3.26 ENERGY EFFICIENCY COMPLIANCE AND IAQ COMPLIANCE

A. Perform operating tests on each air and hydronic system in size or configuration to measure and determine if the systems, as installed, meet the energy efficiency requirements of ASHRAE Standard 90.1 and ASHRAE Standard 62-99 and submit the report along with corrections.
B. Perform air system purge and baseline Indoor Air Quality (IAQ) testing for identifying the existence and quantities of irritating or toxic gas and particulates in the building as delivered by the HVAC system.  These tests shall include measurements of the following contaminants:
1. Carbon Monoxide (CO).

2. Carbon Dioxide (CO2).
3. Formaldehyde and other volatile organic compounds (VOC’s).
4. Tobacco smoke.
5. Dust.
6. Nitrogen Dioxide (NO2).
7. Ozone (O3).
8. Moisture (H2O)
C. The test shall include inspection of each system and their associated components to insure that the system is properly installed, conforms to the construction documents and is in clean and new condition.
D. The TAB report identified in Paragraph 1.5.D shall include the methods and devices used for the analysis, the quantities recorded, and a description of the quality of the building air tested in conformance with paragraph B above and other related paragraphs in this specification section.
E. The report shall contain descriptions of HVAC system components which require servicing or modification which will result in maintaining an acceptable indoor air quality as interpreted by the AHSRAE Standard 62-1999: Ventilation for Acceptable Indoor Air Quality.
F. All sensing and metering devices within the BAS shall be used to read, collect and record the necessary data, once the BAS has been certified to conform to the plans and specifications.
G. The TAB Agent shall utilize flow meters, sensors, BTU meters, energy meters, pump systems, refrigerant systems, heat generation systems, fuel systems, electrical systems, and related systems or subsystems that will assist in validating compliance with ASHRAE Standard 90.1 energy efficiency requirements.
H. All data produced by these devices and systems shall be delivered to the main control console for storage, display, manipulation, and transmission to other systems or sites.
I. The TAB Agent shall furnish additional instrumentation that may be necessary to prove conformance with ASHRAE Standards 90.1 and 62.  This shall include but not be limited to computers, flow measuring devices for air and water, temperature and pressure sensors and transducers.
J. Data produced for the reports developed for compliance with the requirements of this specification section shall be provided to the owner in the following formats:
1. [Hardcopy on standard bond 8-1/2 x 11 sheets of paper.]
2. [3-1/2 inch, 1.44 MB floppy disc, IBM format.]
3. [Compact disk, IBM format.]
4. [GSA standard web-based (HTML) format.]
5. [Drawings can be 11x17 folded to 8-1/2 x 11 in two folds] [If the number of drawings exceeds 20, a separate book for drawings shall be furnished with unfolded drawings.]
3.27 REPORTS

A. Status Reports:  As work progresses, reports shall be prepared and submitted to describe completed procedures, procedures in progress, and scheduled procedures.  Include a list of deficiencies and problems found in systems being tested and balanced.  Prepare a separate report for each system and each building floor for systems serving multiple floors.
B. Final Report:  The final report shall be generated as a computer printout in a letter quality font, on standard white bond paper, bound in a three-ring, loose-leaf binder, and tabulated and divided into sections by tested and balanced systems.  Colored paper may be used as divider sheets.
C. Include a certification sheet in the front of the binder signed and sealed by the certified testing and balancing Agent.
D. Include a list of the instruments used for procedures, along with proof of calibration.
E. Final Report Contents:  In addition to certified field report data, include the following:
1. Pump curves
2. Fan curves
3. Manufacturers' test data
4. Field quality control test reports prepared by system and equipment installers
5. Other information relative to equipment performance, but do not include approved Shop Drawings and Product Data
6. Air distribution device curves and factors
F. General Report Data:  In addition to form titles and entries, include the following data in the final report, as applicable:
1. Title page.
2. Name and address of testing, adjusting, and balancing Agent.
3. Project name.
4. Project location.
5. Design Entity's name and address.
6. Engineer's name and address.
7. Contractor's name and address.
8. Report date.
9. Signature of testing, adjusting, and balancing Agent who certifies the report.
10. Summary of contents, including the following:
a. Design versus final performance.

b. Notable characteristics of systems.

c. Description of system operation sequence if it varies from the Contract Documents.

11. Nomenclature sheets for each item of equipment.
12. Data for terminal units, including manufacturer, type size, and fittings.
13. Notes to explain why certain final data in the body of reports vary from design values.
14. Test conditions for fans and pump performance forms, including the following:
a. Settings for outside, return, and exhaust air dampers.
b. Conditions of filters.
c. Cooling coil, wet and dry bulb conditions.
d. Face and bypass damper settings at coils.
e. Fan drive settings, including settings and percentage of maximum pitch diameter.
f. Inlet vane settings for variable air volume systems.
g. Settings for supply air, static pressure controller.
h. Other system operating conditions that affect performance.
15. System Control Performance Report:  Report shall include the operation of each of the control devices including valves, dampers, motors, flow metering devices and actuators during the occupied period.  The report shall be in two parts, interim and final report.  The report shall identify ASHRAE Standards 90.1 and 62-99 compliance and deviations shall be documented.  Report shall include performance of:
a. Control valves.
b. Control dampers.
c. Flow meters.
d. Sensors.
e. Central console.
f. Controller.
16. System Diagrams:  Include schematic layouts of air and hydronic distribution systems.  Present with single-line diagrams and include the following:
a. Quantities of outside, supply, return, and exhaust airflows and an air balance calculation.
b. Water and steam flow rates and mass flow balance calculation.
c. Duct, outlet, and inlet sizes.
d. Pipe and valve sizes and locations.
e. Terminal units.
f. Balancing stations.
17. Air Handling Unit Test Reports:  For air handling units with coils, include the following:
a. Unit Data:  Include the following:
1) Unit identification.
2) Location.
3) Make and type.
4) Model number and unit size.
5) Manufacturer's serial number.
6) Unit arrangement and class.
7) Discharge arrangement.
8) Sheave make, size in [inches] [mm], and bore.
9) Sheave dimensions, center-to-center and amount of adjustments in mm (inches).
10) Number of belts, make, and size.
11) Number of filters, type, and size.
b. Motor Data:  Include the following:
1) Make and frame type and size.
2) Horsepower and rpm.
3) Volts, phase, and hertz.
4) Full load amperage and service factor.
5) Sheave make, size in  [inches] [mm], and bore.
6) Sheave dimensions, center-to-center and amount of adjustments in [inches] [mm].
c. Test Data:  Include design and actual values for the following:
1) Total airflow rate in L/s (cfm).
2) Total system static pressure in [inches wg] [Pa].
3) Fan rpm.
4) Discharge static pressure in  [inches wg] [Pa].
5) Filter static pressure differential in  [inches wg] [Pa].
6) Preheat coil static pressure differential in  [inches wg] [Pa].
7) Cooling coil static pressure differential in  [inches wg] [Pa].
8) Heating coil static pressure differential in [inches wg] [Pa].
9) Outside airflow in [cfm] [L/s].
10) Return airflow in [cfm] [L/s].
11) Outside air damper position.
12) Return air damper position.
13) Vortex damper position.
18. Apparatus Coil Test Reports:  For apparatus coils, include the following:
a. Coil Data:  Include the following:
1) System identification.
2) Location.
3) Coil type.
4) Number of rows.
5) Fin spacing in fins per [inch] [mm] o.c.
6) Make and model number.
7) Face area in [sq. ft.] [sq. m].
8) Tube size in [NPS] [DN].
9) Tube and fin materials.
10) Circuiting arrangement.
b. Test Data:  Include design and actual values for the following:
1) Airflow rate in [cfm] [L/s].

2) Average face velocity in [fpm] [m/s].
3) Air pressure drop in [inches wg] [Pa].
4) Outside air, wet and dry bulb temperatures in [deg F] [deg C].
5) Return air, wet and dry bulb temperatures in [deg F] [deg C].
6) Entering air, wet and dry bulb temperatures in [deg F] [deg C].
7) Leaving air, wet and dry bulb temperatures in [deg F] [deg C].
8) Water flow rate in [gpm] [L/s].
9) Water pressure differential in feet of head or [psig] [kPa].
10) Entering water temperature in [deg F] [deg C].
11) Leaving water temperature in [deg F] [deg C].
12) Refrigerant expansion valve and refrigerant types.
13) Refrigerant suction pressure in [psig] [kPa]
14) Refrigerant suction temperature in [deg F] [deg C].
15) Inlet steam pressure in [psig] [kPa].
19. Gas and Oil Fired Heat Apparatus Test Reports:  In addition to the manufacturer's factory startup equipment reports, include the following:
a. Unit Data:  Include the following:
1) System identification.
2) Location.
3) Make and type.
4) Model number and unit size.
5) Manufacturer's serial number.
6) Fuel type in input data.
7) Output capacity in [Btuh] [kW].
8) Ignition type.
9) Burner control types.
10) Motor horsepower and rpm.
11) Motor volts, phase, and hertz.
12) Motor full load amperage and service factor.
13) Sheave make, size in [inches] [mm], and bore.
14) Sheave dimensions, center-to-center and amount of adjustments in [inches] [mm].
b. Test Data:  Include design and actual values for the following:
1) Total airflow rate in [cfm] [L/s].
2) Entering air temperature in [deg F] [deg C].
3) Leaving air temperature in [deg F] [deg C].
4) Air temperature differential in [deg F] [deg C].
5) Entering air static pressure in [inches wg] [Pa].
6) Leaving air static pressure in [inches wg] [Pa].
7) Air static pressure differential in [inches wg] [Pa].
8) Low fire fuel input in [Btuh] [kW].
9) High fire fuel input in [Btuh] [kW].
10) Manifold pressure in [psig] [kPa].
11) High temperature limit setting in [deg F] [deg C].
12) Operating set point in [Btuh] [kW].
13) Motor voltage at each connection.
14) Motor amperage for each phase.
15) Heating value of fuel in [Btuh] [kW].
20. Electric Coil Test Reports:  For electric furnaces, duct coils, and electric coils installed in central station air handling units, include the following:
a. Unit Data:  Include the following:
1) System identification.
2) Location.
3) Coil identification.
4) Capacity in [Btuh] [kW].
5) Number of stages.
6) Connected volts, phase, and hertz.
7) Rated amperage.
8) Airflow rate in [cfm] [L/s].
9) Face area in [sq. ft.] [sq. m].
10) Minimum face velocity in [fpm] [m/s].
b. Test Data:  Include design and actual values for the following:
1) Heat output in [Btuh] [kW].
2) Airflow rate in [cfm] [L/s].
3) Air velocity in [fpm] [m/s].
4) Entering air temperature in [deg F] [deg C].
5) Leaving air temperature in [deg F] [deg C].
6) Voltage at each connection.
7) Amperage for each phase.
21. Fan Test Reports:  For supply, return, and exhaust fans, include the following:
a. Fan Data:  Include the following:
1) System identification.
2) Location.
3) Make and type.
4) Model number and size.
5) Manufacturer's serial number.
6) Arrangement and class.
7) Sheave make, size in [inches] [mm], and bore.
8) Sheave dimensions, center-to-center and amount of adjustments in [inches] [mm].
b. Motor Data:  Include the following:
1) Make and frame type and size.
2) Horsepower and rpm.
3) Volts, phase, and hertz.
4) Full load amperage and service factor.
5) Sheave make, size in [inches] [mm], and bore.
6) Sheave dimensions, center-to-center and amount of adjustments in [inches] [mm].
7) Number of belts, make, and size.

c. Test Data:  Include design and actual values for the following:

1) Total airflow rate in [cfm] [L/s].
2) Total system static pressure in [inches wg] [Pa].
3) Fan rpm.
4) Discharge static pressure in [inches wg] [Pa].
5) Suction static pressure in [inches wg] [Pa].
22. Round, Flat Oval, and Rectangular Duct Traverse Reports:  Include a diagram with a grid representing the duct cross-section and record the following:
a. Report Data:  Include the following:
1) System and air handling unit number.
2) Location and zone.
3) Traverse air temperature in  [deg F] [deg C].
4) Duct static pressure in [inches wg] [Pa].
5) Duct size in [inches] [mm].
6) Duct area in [sq. ft.] [sq. m].
7) Design airflow rate in [cfm] [L/s].
8) Design velocity in [fpm] [m/s].
9) Actual airflow rate in [cfm] [L/s].
10) Actual average velocity in [fpm] [m/s].
11) Barometric pressure in [psig] [Pa].
23. Air Terminal Device Reports:  For terminal units, include the following:
a. Unit Data:  Include the following:
1) System and air handling unit identification.
2) Location and zone.
3) Test apparatus used.
4) Area served.
5) Air terminal device make.
6) Air terminal device number from system diagram.
7) Air terminal device type and model number.
8) Air terminal device size.
9) Air terminal device effective area in [sq. ft.] [sq. m].
b. Test Data:  Include design and actual values for the following:
1) Airflow rate in [cfm] [L/s].
2) Air velocity in [fpm] [m/s].
3) Preliminary airflow rate as needed in [cfm] [L/s].
4) Preliminary velocity as needed in [fpm] [m/s].
5) Final airflow rate in [cfm] [L/s].
6) Final velocity in [fpm] [m/s].
7) Space temperature in [deg F] [deg C].
24. System Coil Reports:  For reheat coils and water coils of terminal units, include the following:
a. Unit Data:  Include the following:
1) System and air handling unit identification.
2) Location and zone.
3) Room or riser served.
4) Coil make and size.
5) Flowmeter type.
b. Test Data:  Include design and actual values for the following:
1) Airflow rate in [cfm] [L/s].
2) Entering water temperature in [deg F] [deg C]. 
3) Leaving water temperature in [deg F] [deg C].
4) Water pressure drop in feet of head or [psig] [kPa].
5) Entering air temperature in [deg F] [deg C].
6) Leaving air temperature in [deg F] [deg C].
25. Packaged Chiller Reports:  For each chiller, include the following:
a. Unit Data:  Include the following:
1) Unit identification.
2) Make and model number.
3) Manufacturer's serial number.
4) Refrigerant type and capacity in [gal.] [L].
5) Starter type and size.
6) Starter thermal protection size.
b. Condenser Test Data:  Include design and actual values for the following:
1) Refrigerant pressure in [psig] [kPa].
2) Refrigerant temperature in [deg F] [deg C].
3) Entering water temperature in [deg F] [deg C].
4) Leaving water temperature in [deg F] [deg C].
5) Entering water pressure in feet of head or [psig] [kPa].
6) Water pressure differential in feet of head or [psig] [kPa].
26. Evaporator Test Reports:  Include design and actual values for the following:
a. Refrigerant pressure in [psig] [kPa].
1) Refrigerant temperature in [deg F] [deg C].
b. Entering water temperature in [deg F] [deg C].
c. Leaving water temperature in [deg F] [deg C].
d. Entering water pressure in feet of head or [psig] [kPa].
e. Water pressure differential in feet of head or [psig] [kPa].
27. Compressor Test Data:  Include design and actual values for the following:

a. Make and model number.
b. Manufacturer's serial number.
c. Suction pressure in [psig] [kPa].
d. Suction temperature in [deg F] [deg C].
e. Discharge pressure in [psig] [kPa].
f. Discharge temperature in [deg F] [deg C].
g. Oil pressure in [psig] [kPa].
h. Oil temperature in [deg F] [deg C].
i. Voltage at each connection.
j. Amperage for each phase.
k. The kW input.
l. Crankcase heater kW.
m. Chilled water control set point in [deg F] [deg C].
n. Condenser water control set point in [deg F] [deg C].
o. Refrigerant low pressure cutoff set point in [psig] [kPa].
p. Refrigerant high pressure cutoff set point in [psig] [kPa].
28. Refrigerant Test Data:  Include design and actual values for the following:
a. Oil level.
b. Refrigerant level.
c. Relief valve setting in [psig] [kPa].
d. Unloader set points in [psig] [kPa].
e. Percentage of cylinders unloaded.
f. Bearing temperatures in [deg F] [deg C].
g. Vane position.
h. Low temperature cutoff set point in [deg F] [deg C].
29. Compressor and Condenser Reports:  For refrigerant side of unitary systems, stand-alone refrigerant compressors, air-cooled condensing units, or water-cooled condensing units, include the following:
a. Unit Data:  Include the following:

1) Unit identification.
2) Location.
3) Unit make and model number.
4) Manufacturer's compressor serial numbers.
5) Compressor make.
6) Compressor model and serial numbers.
7) Refrigerant weight in [lb.] [kg].
8) Low ambient temperature cutoff in [deg F] [deg C].
b. Test Data:  Include design and actual values for the following:
1) Inlet duct static pressure in [inches wg] [Pa].
2) Outlet duct static pressure in [inches wg] [Pa].
3) Entering air, dry bulb temperature in [deg F] [deg C].
4) Leaving air, dry bulb temperature in [deg F] [deg C].
5) Condenser entering water temperature in [deg F] [deg C].
6) Condenser leaving water temperature in [deg F] [deg C].
7) Condenser water temperature differential in [deg F] [deg C].
8) Condenser entering water pressure in feet of head or [psig] [kPa].
9) Condenser leaving water pressure in feet of head or [psig] [kPa].
10) Condenser water pressure differential in feet of head or [psig] [kPa].
11) Control settings.
12) Unloader set points.
13) Low pressure cutout set point in [psig] [kPa].
14) High pressure cutout set point in [psig] [kPa].
15) Suction pressure in [psig] [kPa].
16) Suction temperature in [deg F] [deg C].
17) Condenser refrigerant pressure in [psig] [kPa].
18) Condenser refrigerant temperature in [deg F] [deg C].
19) Oil pressure in [psig] [kPa].
20) Oil temperature in [deg F] [deg C].
21) Voltage at each connection.
22) Amperage for each phase.
23) The kW input.
24) Crankcase heater kW.
25) Number of fans.
26) Condenser fan rpm.
27) Condenser fan airflow rate in [cfm] [L/s].
28) Condenser fan motor make, frame size, rpm, and horsepower.
29) Condenser fan motor voltage at each connection.
30) Condenser fan motor amperage for each phase.
30. Cooling Tower or Condenser Test Reports:  For cooling towers or condensers, include the following:
a. Unit Data:  Include the following:
1) Unit identification.
2) Make and type.
3) Model and serial numbers.
4) Nominal cooling capacity in [tons] [kW].
5) Refrigerant type and weight in [lbs.] [kg].
6) Water treatment chemical feeder and chemical.
7) Number and type of fans.
8) Fan motor make, frame size, rpm, and horsepower.
9) Fan motor voltage at each connection.
10) Sheave make, size in [inches] [mm], and bore.
11) Sheave dimensions, center-to-center and amount of adjustments in [inches] [mm].
12) Number of belts, make, and size.
Use pump data below for recirculating pump in evaporative condensers, not for system used with cooling towers.  For cooling towers, use pump test reports.

b. Pump Test Data:  Include design and actual values for the following:
1) Make and model number.
2) Manufacturer's serial number.
3) Motor make and frame size.
4) Motor horsepower and rpm.
5) Voltage at each connection.
6) Amperage for each phase.
7) Water flow rate in [gpm] [L/s].
c. Water Test Data:  Include design and actual values for the following:
1) Entering water temperature in [deg F] [deg C].
2) Leaving water temperature in [deg F] [deg C].
3) Water temperature differential in [deg F] [deg C].
4) Entering water pressure in feet of head or [psig] [kPa].
5) Leaving water pressure in feet of head or [psig] [kPa].
6) Water pressure differential in feet of head or [psig] [kPa].
7) Water flow rate in [gpm] [L/s].
8) Bleed water flow rate in [gpm] [L/s].
d. Air Data:  Include design and actual values for the following:
1) Duct airflow rate in [cfm] [L/s].
2) Inlet duct static pressure in [inches wg] [Pa].
3) Outlet duct static pressure in [inches wg] [Pa].
4) Average entering air, wet bulb temperature in [deg F] [deg C].
5) Average leaving air, wet bulb temperature in [deg F] [deg C].
6) Ambient wet bulb temperature in [deg F] [deg C].
31. Heat Exchanger/Converter Test Reports:  For steam and hot water heat exchangers, include the following:
a. Unit Data:  Include the following:
1) Unit identification.
2) Location.
3) Service.
4) Make and type.
5) Model and serial numbers.
6) Ratings.
b. Steam Test Data:  Include design and actual values for the following:

1) Inlet pressure in [psig] [kPa].
2) Condensate flow rate in [lb/h] [kW].
c. Primary Water Test Data:  Include design and actual values for the following:
1) Entering water temperature in [deg F] [deg C].
2) Leaving water temperature in [deg F] [deg C].
3) Entering water pressure in feet of head or [psig] [kPa].
4) Water pressure differential in feet of head or [psig] [kPa].
5) Water flow rate in [gpm] [L/s].
d. Secondary Water Test Data:  Include design and actual values for the following:
1) Entering water temperature in [deg F] [deg C].
2) Leaving water temperature in [deg F] [deg C].
3) Entering water pressure in feet of head or [psig] [kPa].
4) Water pressure differential in feet of head or [psig] [kPa].
5) Water flow rate in [gpm] [L/s].
Net positive suction head is important for pumps in open circuits and for pumps handling fluids at elevated temperatures.

32. Pump Test Reports:  For pumps, include the following data.  Calculate impeller size by plotting the shutoff head on pump curves.
a. Unit Data:  Include the following:
1) Unit identification.
2) Location.
3) Service.
4) Make and size.
5) Model and serial numbers.
6) Water flow rate in [gpm] [L/s].
7) Water pressure differential in kPa (feet of head or psig).
8) Required net positive suction head in kPa (feet of head or psig).
9) Pump rpm.
10) Impeller diameter in [inches] [mm].
11) Motor make and frame size.
12) Motor horsepower and rpm.
13) Voltage at each connection.
14) Amperage for each phase.
15) Full load amperage and service factor.
16) Seal type.
b. Test Data:  Include design and actual values for the following:
1) Static head in feet of head or [psig] [kPa].
2) Pump shutoff pressure in feet of head or [psig] [kPa].
3) Actual impeller size in [inches] [mm].
4) Full open flow rate in [gpm] [L/s].
5) Full open pressure in feet of head or [psig] [kPa].
6) Final discharge pressure in feet of head or [psig] [kPa].
7) Final suction pressure in feet of head or [psig] [kPa].
8) Final total pressure in feet of head or [psig] [kPa].
9) Final water flow rate in [gpm] [L/s].
10) Voltage at each connection.
11) Amperage for each phase.
Flue-gas analysis is normally not part of testing, adjusting, and balancing procedures but could be added.

33. Boiler Test Reports:  For boilers, include the following:
a. Unit Data:  Include the following:
1) Unit identification.

2) Location.

3) Service.

4) Make and type.

5) Model and serial numbers.

6) Fuel type and input in kW (Btuh).

7) Number of passes.

8) Ignition type.

9) Burner control types.

10) Voltage at each connection.

11) Amperage for each phase.

b. Test Data:  Include design and actual values for the following:

1) Operating pressure in [psig] [kPa].

2) Operating temperature in [deg F] [deg C].

3) Entering water temperature in [deg F] [deg C].

4) Leaving water temperature in [deg F] [deg C].

5) Number of safety valves and sizes in [NPS] [DN].
6) Safety valve settings in [psig] [kPa].

7) High limit setting in [psig] [kPa].

8) Operating control setting.

9) High fire set point.

10) Low fire set point.

11) Voltage at each connection.

12) Amperage for each phase.

13) Draft fan voltage at each connection.

14) Draft fan amperage for each phase.

15) Manifold pressure in [psig] [kPa].

34. Instrument Calibration Reports:  For instrument calibration, include the following:

a. Report Data:  Include the following:

1) Instrument type and make.

2) Serial number.

3) Application.

4) Dates of use.

5) Dates of calibration.

3.28 ADDITIONAL TESTS

A. Within 90 days of completing testing, adjusting, and balancing, perform additional testing and balancing to verify that balanced conditions are being maintained throughout and to correct unusual conditions.
B. The Owner reserves the right to request rechecking of up to 10% of the total of the air or water flows without additional costs.  If the recheck fails to substantiate the report values, the TAB shall be redone until the recheck verifies that the systems are balanced.
C. Seasonal Periods:  If initial testing, adjusting, and balancing procedures were not performed during near peak summer and winter conditions, perform additional inspections, testing, and adjusting during near peak summer and winter conditions as specified in Energy Validation below:
3.29 ENERGY VALIDATION

A. The contractor shall validate the peak summer and peak winter energy consumption and balancing conditions after occupancy of the facility by the owner.  Even though the initial testing and balancing may have been performed during a near peak summer or near peak winter period, each shall be validated after occupancy by the owner.  Sufficient funds will be withheld after these tests and validations have been completed and the results approved by the owner.
B. The contractor shall schedule and coordinate with the owner dates for both the summer and winter peak energy validation testing and balancing.  The contractor shall have the required instrumentation in place and sufficient personnel available to minimize disruption and inconvenience to the operation of the building and to the occupants of the building.
C. Using approved instrumentation, data shall be collected and recorded to  compute the energy consumed by each system in the building.  Totals shall be compared to the values indicated for the prime utilities supplied to the building.
D. Individual readings of flows, temperature, pressure, etc., taken with the contractor’s test instruments shall be compared with corresponding, permanently installed building instrumentation.  This data shall be included in the final test and balance report.
E. If an energy analysis was generated during the design, the theoretical and the actual shall be compared.  If more than a 10% difference in total energy consumptions is indicated, the differences shall be examined and a determination made as to the cause.  If the actual consumption is higher than predicted, a determination shall be made as to the cause and corrective measures listed for evaluation by the owner.
END OF SECTION 15990

TESTING, ADJUSTING, AND BALANCING
15990 - 36

