Copyright 2001 AIA
GSA VERSION MASTERSPEC
06/01 (GSA 03/05)

Copyright 2001, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15121 - PIPE EXPANSION FITTINGS AND LOOPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following pipe expansion joints and expansion compensation devices for mechanical piping systems:

Adjust list below to suit Project.

1. Metal-bellows expansion joints.

2. Expansion compensators.

3. Rubber expansion joints.

4. Flexible-hose expansion joints.

5. Packed slip expansion joints.

6. Flexible ball joints.

7. Pipe bends and loops.

8. Alignment guides and anchors.

1.3 DEFINITIONS

Retain definitions that remain after this Section has been edited.

A. BR:  Butyl rubber.

B. Buna-N:  Nitrile rubber.

C. CR:  Chlorosulfonated polyethylene synthetic rubber.

D. CSM:  Chlorosulfonyl-polyethylene rubber.

E. EPDM:  Ethylene-propylene-diene terpolymer rubber.

F. NR:  Natural rubber.

G. PTFE:  Polytetrafluoroethylene plastic.

1.4 PERFORMANCE REQUIREMENTS

A. Compatibility:  Products shall be suitable for piping system fluids, materials, working pressures, and temperatures.

B. Capability:  Products shall absorb 200 percent of maximum axial movement between anchors.

1.5 SUBMITTALS

A. Product Data:  For each type of pipe expansion joint and alignment guide indicated.

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  Calculate requirements for thermal expansion of piping systems and for selecting and designing expansion joints, loops, and bends.

2. Anchor Details:  Detail fabrication of each anchor indicated.  Show dimensions and methods of assembly and attachment to building structure.

3. Alignment Guide Details:  Detail field assembly and attachment to building structure.

4. Schedule:  Indicate type, manufacturer's number, size, material, pressure rating, end connections, and location for each expansion joint.

C. Product Certificates:  For each type of pipe expansion joint, signed by product manufacturer.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

E. Operation and Maintenance Data:  For pipe expansion joints to include in emergency, operation, and maintenance manuals.

F. CSA International listed for natural gas systems.

1.6 QUALITY ASSURANCE

Delete this Article if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding:  Qualify procedures and personnel according to the following:

Retain applicable standards below.

1. Steel Shapes and Plates:  AWS D1.1, "Structural Welding Code - Steel."

2. Welding to Piping:  ASME Boiler and Pressure Vessel Code:  Section IX.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.
B. Warranty Period:  Three years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.
2.2 EXPANSION JOINTS

Coordinate expansion-joint pressure and temperature ratings with piping systems.

A. Metal-Bellows Expansion Joints:  ASTM F 1120, circular-corrugated-bellows type with external tie rods.

1. Available Manufacturers:

a. Adsco Manufacturing, LLC.

b. Anamet, Inc.

c. Badger Industries.

d. Expansion Joint Systems, Inc.

e. Flex-Hose Co., Inc.

f. Flexicraft Industries.

g. Flex-Pression, Ltd.

h. Flex-Weld, Inc.

i. Hyspan Precision Products, Inc.

j. Metraflex, Inc.

k. Piping Technology & Products, Inc.

l. Proco Products, Inc.

m. Senior Flexonics, Inc.; Pathway Division.

n. Tozen America Corp.

o. Unaflex Inc.

p. WahlcoMetroflex.

q. <Insert manufacturer's name.>

2. Metal-Bellows Expansion Joints for Copper Piping:  [Single] [Single- or multiple] [Multiple]-ply phosphor-bronze bellows, copper pipe end connections, and brass shrouds.

3. Metal-Bellows Expansion Joints for Stainless-Steel Waterway:  Single-ply stainless-steel bellows, stainless-steel-pipe end connections, and steel shroud.

4. Metal-Bellows Expansion Joints for Steel Piping:  [Single] [Single- or multiple] [Multiple]-ply stainless-steel bellows, steel pipe end connections, and carbon-steel shroud.

5. Minimum Pressure Rating:  [1035 kPa (150 psig)] [1200 kPa (175 psig)] <Insert measurement>, unless otherwise indicated.

6. Configuration:  [Single] [Single- or double] [Double]-bellows type[ with base], unless otherwise indicated.

7. End Connections:  [Flanged] [Flanged or weld] [Weld].

B. Expansion Compensators:  Double-ply corrugated steel, stainless-steel, or copper-alloy bellows in a housing with internal guides, antitorque device, and removable end clip for positioning.

1. Available Manufacturers:

a. Adsco Manufacturing, LLC.

b. Flexicraft Industries.

c. Flex-Pression, Ltd.

d. Flex-Weld, Inc.

e. Hyspan Precision Products, Inc.

f. Metraflex, Inc.

g. Senior Flexonics, Inc.; Pathway Division.

h. Unaflex Inc.

i. <Insert manufacturer's name.>

2. Minimum Pressure Rating:  [1035 kPa (150 psig)] [1200 kPa (175 psig)] <Insert measurement>, unless otherwise indicated.

3. Configuration for Copper Piping:  Two-ply phosphor-bronze or stainless-steel bellows and bronze or stainless-steel shroud.

4. Configuration for Steel Piping:  Two-ply stainless-steel bellows and carbon-steel shroud.

5. End Connections for Copper Tubing DN 50 (NPS 2) and Smaller:  [Solder joint] [Solder joint or threaded] [Threaded].

6. End Connections for Copper Tubing DN 65 to DN 100 (NPS 2-1/2 to NPS 4):  [Solder joint] [Solder joint or threaded] [Threaded].

7. End Connections for Steel Pipe DN 50 (NPS 2) and Smaller:  Threaded.

8. End Connections for Steel Pipe DN 65 to DN 100 (NPS 2-1/2 to NPS 4):  [Flanged] [Flanged or threaded] [Threaded] [Weld].

C. Rubber Expansion Joints:  ASTM F 1123, fabric-reinforced rubber with external control rods and complying with FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

1. Available Manufacturers:

a. Flex-Hose Co., Inc.

b. Flexicraft Industries.

c. Flex-Weld, Inc.

d. Garlock Sealing Technologies.

e. General Rubber Corp.

f. Mason Industries, Inc.; Mercer Rubber Co.

g. Metraflex, Inc.

h. MG Piping Products Co.

i. Proco Products, Inc.

j. Red Valve Company, Inc.

k. Senior Flexonics, Inc.; Pathway Division.

l. Tozen America Corp.

m. Unaflex Inc.

n. Vibration Mountings & Controls, Inc.

o. <Insert manufacturer's name.>

2. Arch Type:  [Single] [Single or multiple] [Multiple] arches.

3. Spherical Type:  [Single] [Single or multiple] [Multiple] spheres.

Pressure-temperature ratings indicated in three subparagraphs below are generally minimum values.  Consult manufacturers' literature for options available.

a. Minimum Pressure and Temperature Ratings forDN 40 to DN 100 (NPS 1-1/2 to NPS 4):  [1035 kPa (150 psig) at 104 deg C (220 deg F)] <Insert other>.

b. Minimum Pressure and Temperature Ratings for DN 125 and DN 150 (NPS 5 and NPS 6):  [966 kPa (140 psig) at 93 deg C (200 deg F)] <Insert other>.

c. Minimum Pressure and Temperature Ratings forDN 200 to DN 300 (NPS 8 to NPS 12):  [966 kPa (140 psig) at 82 deg C (180 deg F)] <Insert other>.

Retain only those materials in first subparagraph below that are required.  Indicate materials on Drawings if more than one is required.  See Evaluations for discussion about rubber materials.

4. Material:  [BR] [Buna-N] [CR] [CSM] [EPDM] [NR].

5. End Connections:  Full-faced, integral, steel flanges with steel retaining rings.

The second option below provides greater degree of movement and also allows different elevations.

D. Flexible-Hose Expansion Joints:  Manufactured assembly with two flexible-metal-hose legs joined by long-radius, [180-degree return bend][ or][ center section of flexible hose]; with inlet and outlet elbow fittings, corrugated-metal inner hoses, and braided outer sheaths and drain connections.

1. Stainless steel flexible hose listed for compliance with UL 536[ for [flammable][ combustible][ gases][ liquids]].

2. Available Manufacturers:

a. Flex-Hose Co., Inc.

b. Flexicraft Industries.

c. Flex-Pression, Ltd.

d. Metraflex, Inc.

e. <Insert manufacturer's name.>

3. Flexible-Hose Expansion Joints for Copper Piping:  Copper-alloy fittings with [solder-] <Insert other> joint end connections.

a. DN 50 (NPS 2) and Smaller:  Bronze hoses and single-braid bronze sheaths with 3100 kPa at 21 deg C (450 psig at 70 deg F) and 2340 kPa at 232 deg C (340 psig at 450 deg F) ratings.

b. DN 65 to DN 100 (NPS 2-1/2 to NPS 4):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 2070 kPa at 21 deg C (300 psig at 70 deg F) and 1550 kPa at 232 deg C (225 psig at 450 deg F) ratings.

Retain last two subparagraphs above or first two subparagraphs below.

c. DN 50 (NPS 2) and Smaller:  Bronze hoses and double-braid bronze sheaths with 4830 kPa at 21 deg C (700 psig at 70 deg F) and 3450 kPa at 232 deg C (500 psig at 450 deg F) ratings.

d. DN 65 to DN 100 (NPS 2-1/2 to NPS 4):  Stainless-steel hoses and double-braid, stainless-steel sheaths with 2890 kPa at 21 deg C (420 psig at 70 deg F) and 2170 kPa at 232 deg C (315 psig at 450 deg F) ratings.

4. Flexible-Hose Expansion Joints for Steel Piping:  Carbon-steel fittings with threaded end connections for DN 50 (NPS 2) and smaller and [flanged] [weld] end connections for DN 65 (NPS 2-1/2) and larger.

a. DN 50 (NPS 2) and Smaller:  Stainless-steel hoses and single-braid, stainless-steel sheaths with 3100 kPa at 21 deg C (450 psig at 70 deg F) and 2250 kPa at 315 deg C (325 psig at 600 deg F) ratings.

b. DN 65 to DN 150 (NPS 2-1/2 to NPS 6):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 1380 kPa at 21 deg C (200 psig at 70 deg F) and 1000 kPa at 315 deg C (145 psig at 600 deg F) ratings.

c. DN 200 to DN 300 (NPS 8 to NPS 12):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 860 kPa at 21 deg C (125 psig at 70 deg F) and 625 kPa at 315 deg C (90 psig at 600 deg F) ratings.

Delete last three subparagraphs above or three subparagraphs below.

d. DN 50 (NPS 2) and Smaller:  Stainless-steel hoses and double-braid, stainless-steel sheaths with 4830 kPa at 21 deg C (700 psig at 70 deg F) and 3550 kPa at 315 deg C (515 psig at 600 deg F) ratings.

e. DN 65 to DN 150 (NPS 2-1/2 to NPS 6):  Stainless-steel hoses and double-braid, stainless-steel sheaths with 1900 kPa at 21 deg C (275 psig at 70 deg F) and 1380 kPa at 315 deg C (200 psig at 600 deg F) ratings.

f. DN 200 (NPS 8) and Larger:  Stainless-steel hoses and double-braid, stainless-steel sheaths with 1130 kPa at 21 deg C (165 psig at 70 deg F) and 830 kPa at 315 deg C (120 psig at 600 deg F) ratings.

5. Maximum working pressure: [865 kPa (125 psig)] [1725 kPa (250 psig)] <Insert value>.
6. Maximum temperature range: 200 deg C (400 deg F)
7. Accessories:

a. Hangar kits.

b. <Insert accessory here.>

Coordinate expansion-joint pressure and temperature ratings with piping systems.

E. Packed Slip Expansion Joints:  ASTM F 1007, carbon-steel, packing type designed for repacking under pressure and pressure rated for 1725 kPa at 204 deg C (250 psig at 400 deg F) minimum.  Include asbestos-free PTFE packing, compound limit stops, and drip connection if used for steam piping.

1. Available Manufacturers:

a. Adsco Manufacturing, LLC.

b. Advanced Thermal Systems, Inc.

c. Hyspan Precision Products, Inc.

d. <Insert manufacturer's name.>

2. Configuration:  [Single] [Single- and double] [Double]-joint class[ with base, unless otherwise indicated].

3. End Connections:  Flanged or weld ends to match piping system.

F. Flexible Ball Joints:  Carbon-steel assembly with asbestos-free composition packing, designed for 360-degree rotation and angular deflection, and 1725 kPa at 204 deg C (250 psig at 400 deg F) minimum pressure rating; complying with ASME Boiler and Pressure Vessel Code:  Section II, "Materials," and with ASME B31.9, "Building Services Piping," for materials and design of pressure-containing parts and bolting.

1. Angular Deflection for DN 150 (NPS 6) and Smaller:  30-degree minimum.

2. Angular Deflection for DN 200 (NPS 8) and Larger:  15-degree minimum.

NPS 2-1/2 (DN 65) and larger weld end connections are available if required.

3. End Connections for DN 50 (NPS 2) and Smaller:  Threaded.

4. End Connections for DN 65 (NPS 2-1/2) and Larger:  Flanged.

5. Available Manufacturers:

a. Advanced Thermal Systems, Inc.

b. Hyspan Precision Products, Inc.

c. <Insert manufacturer's name.>

2.3 ALIGNMENT GUIDES

Indicate alignment-guide length and maximum spider travel on Drawings.

A. Description:  Steel, factory fabricated, with bolted two-section outer cylinder and base for alignment of piping and two-section guiding spider for bolting to pipe.

1. Available Manufacturers:

a. Adsco Manufacturing, LLC.

b. Advanced Thermal Systems, Inc.

c. Flex-Hose Co., Inc.

d. Flexicraft Industries.

e. Flex-Weld, Inc.

f. Hyspan Precision Products, Inc.

g. Metraflex, Inc.

h. Piping Technology & Products, Inc.

i. Senior Flexonics, Inc.; Pathway Division.

j. <Insert manufacturer's name.>

2.4 MATERIALS FOR ANCHORS

A. Steel Shapes and Plates:  ASTM A 36/A 36M.

B. Bolts and Nuts:  ASME B18.10 or ASTM A 183, steel, hex head.

C. Washers:  ASTM F 844, steel, plain, flat washers.

D. Mechanical Fasteners:  Insert-wedge-type stud with expansion plug anchor for use in hardened portland cement concrete, and tension and shear capacities appropriate for application.

Stainless-steel studs are available.

1. Stud:  Threaded, zinc-coated carbon steel.

2. Expansion Plug:  Zinc-coated steel.

3. Washer and Nut:  Zinc-coated steel.

E. Chemical Fasteners:  Insert-type-stud bonding system anchor for use with hardened portland cement concrete, and tension and shear capacities appropriate for application.

1. Bonding Material:  ASTM C 881, Type IV, Grade 3, 2-component epoxy resin suitable for surface temperature of hardened concrete where fastener is to be installed.

Stainless-steel studs are available.

2. Stud:  ASTM A 307, zinc-coated carbon steel with continuous thread on stud, unless otherwise indicated.

3. Washer and Nut:  Zinc-coated steel.

F. Concrete:  Portland cement mix, 20.7 MPa (3000 psi) minimum.  Refer to [Division 3 Section "Cast-in-Place Concrete"] [Division 15 Section “Basic Mechanical Materials”]for formwork, reinforcement, and concrete.

G. Grout:  ASTM C 1107, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink, nonmetallic grout; suitable for interior and exterior applications.

1. Properties:  Nonstaining, noncorrosive, and nongaseous.

2. Design Mix:  34.5-MPa (5000-psi), 28-day compressive strength.

PART 3 -  EXECUTION

3.1 EXPANSION-JOINT INSTALLATION

A. Install manufactured, nonmetallic expansion joints according to FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

B. Install expansion joints of sizes matching size of piping in which they are installed.

C. Install alignment guides to allow expansion and to avoid end-loading and torsional stress.

3.2 PIPE BEND AND LOOP INSTALLATION

Refer to the ASHRAE HANDBOOK - "HVAC Systems and Equipment," which states that cold springing is not recommended for most HVAC piping.  
Coordinate paragraph below with structural Sections and Drawings if welding is included in structural work.

A. Attach pipe bends and loops to anchors.

1. Steel Anchors:  Attach by welding.  Comply with ASME B31.9 and ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

2. Concrete Anchors:  Attach by fasteners.  Follow fastener manufacturer's written instructions.

3.3 SWING CONNECTIONS

Delete this Article or edit to suit Project.

A. Connect risers and branch connections to mains with at least five pipe fittings, including tee in main.

B. Connect risers and branch connections to terminal units with at least four pipe fittings, including tee in riser.

C. Connect mains and branch connections to terminal units with at least four pipe fittings, including tee in main.

3.4 ALIGNMENT-GUIDE INSTALLATION

Show locations and quantity of guides on Drawings.

A. Install guides on piping adjoining pipe expansion joints and bends and loops.

Coordinate below with structural Sections and Drawings if welding is included in structural work.

B. Attach guides to pipe and secure to building structure.

3.5 ANCHOR INSTALLATION

A. Install anchors at locations to prevent stresses from exceeding those permitted by ASME B31.9 and to prevent transfer of loading and stresses to connected equipment.

Coordinate first paragraph below with structural Sections and Drawings if welding is included in structural work.

B. Fabricate and install steel anchors by welding steel shapes, plates, and bars to piping and to structure.  Comply with ASME B31.9 and AWS D1.1.

C. Construct concrete anchors of poured-in-place concrete of dimensions indicated and include embedded fasteners.

D. Install pipe anchors according to expansion-joint manufacturer's written instructions if expansion joints or compensators are indicated.

E. Use grout to form flat bearing surfaces for expansion fittings, guides, and anchors installed on or in concrete.

END OF SECTION 15121

PIPE EXPANSION FITTINGS AND LOOPS
15121 - 10

