Copyright 1999 AIA
GSA VERSION MASTERSPEC
3/99 (GSA 03/05)

Copyright 1999, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15183 - REFRIGERANT PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes refrigerant piping used for comfort air-conditioning applications.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 7 Section "Through-Penetration Firestop Systems" for materials and methods for sealing pipe penetrations through fire and smoke barriers.

2. Division 7 Section "Joint Sealants" for materials and methods for sealing pipe penetrations through exterior walls.

3. Division 15 Section "Hangers and Supports" for pipe supports and installation requirements.

Delete first subparagraph below if requirements in Division 15 Section "Basic Mechanical Materials and Methods" are sufficient.

4. Division 15 Section "Mechanical Identification" for labeling and identifying refrigerant piping.

5. Division 15 Section "Meters and Gages" for thermometers and pressure gages.

6. Division 15 Sections "Building Automation System" and “Temperature Controls” for thermostats, controllers, automatic-control valves, and sensors.

1.3 SUBMITTALS

A. Product Data:  For each type of valve and refrigerant piping specialty indicated.  Include pressure drop, based on manufacturer's test data, for thermostatic expansion valves, solenoid valves, and pressure-regulating valves.

B. Shop Drawings:  Show layout of refrigerant piping and specialties, including pipe, tube, and fitting sizes, flow capacities, valve arrangements and locations, slopes of horizontal runs, oil traps, double risers, wall and floor penetrations, and equipment connection details.  Show interface and spatial relationship between piping and equipment.

1. Refrigerant piping indicated is schematic only.  Size piping and design the actual piping layout, including oil traps, double risers, specialties, and pipe and tube sizes, to ensure proper operation and compliance with warranties of connected equipment.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding Certificates:  Copies of certificates for welding procedures and personnel.

D. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

E. Maintenance Data:  For refrigerant valves and piping specialties to include in maintenance manuals specified in Division 1.

1.4 QUALITY ASSURANCE

Delete first paragraph below if no welding.  Retain "Welding Certificates" Paragraph in "Submittals" Article if below is retained.

A. Welding:  Qualify procedures and personnel according to ASME Boiler and Pressure Vessel Code:  Section IX; "Welding and Brazing Qualifications."

B. ASHRAE Standard:  Comply with ASHRAE 15, "Safety Code for Mechanical Refrigeration."

C. ASME Standard:  Comply with ASME B31.5, "Refrigeration Piping."

D. UL Standard:  Provide products complying with UL 207, "Refrigerant-Containing Components and Accessories, Nonelectrical"; or UL 429, "Electrically Operated Valves."

1.5 COORDINATION

A. Coordinate layout and installation of refrigerant piping and suspension system components with other construction, including light fixtures, HVAC equipment, fire-suppression-system components, and partition assemblies.

B. Coordinate pipe sleeve installations for foundation wall penetrations.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

D. Coordinate pipe sleeve installations for penetrations in exterior and interior walls and floor assemblies.  Coordinate with requirements for firestopping specified in Division 7 Section "Through-Penetration Firestop Systems" for materials and methods for sealing pipe penetrations through fire and smoke barriers.

E. Coordinate pipe fitting pressure classes with products specified in related Sections.

1.6 EXTRA MATERIALS

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Refrigeration Oil Test Kits:  [Two] <Insert number> each, containing everything required to conduct one test.

2. Refrigerant:  [Two] <Insert number> containers each, with 9 kg (20 lb) of refrigerant.

3. Filter-Dryer Cartridges:  [Three] <Insert number> of each type.  A minimum of two per refrigerant system is required.
PART 2 -  PRODUCTS

2.1 MANUFACTURERS

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:  
2. Refrigerants:

a. Allied Signal, Inc./Fluorine Products; Genetron Refrigerants.

b. DuPont Company; Fluorochemicals Div.

c. Elf Atochem North America, Inc.; Fluorocarbon Div.

d. ICI Americas Inc./ICI KLEA; Fluorochemicals Bus.

3. Refrigerant Valves and Specialties:

a. Climate & Industrial Controls Group; Parker-Hannifin Corp.; Refrigeration & Air Conditioning Division.

b. Danfoss Electronics, Inc.

c. Emerson Electric Company; Alco Controls Div.

d. Henry Valve Company.

e. Sporlan Valve Company.

Coordinate the following two articles with "Piping Applications" Article in Part 3.  See "Writing Guide" Article in the Evaluations.  Delete materials not used.  The articles include examples of materials listed in ASHRAE's 2000 1996 ASHRAE HANDBOOK--"HVAC Systems and Equipment," Chapter 41, 40, "Pipe, Tubes, and Fittings."

2.2 COPPER TUBE AND FITTINGS

Type M copper tubing and cast-iron pipe are not permitted by the Pressure Piping Code for volatile refrigerant.  Type L (Type B) and Type K (Type A) shall be are used for underground installations.  Do Not use copper for R-717, Ammonia.
A. Drawn-Temper Copper Tube:  [ASTM B 280, Type ACR] [ASTM B 88M, Type B (ASTM B 88, Type L)]. [ASTM B 88M, Type A (ASTM B 88, Type K)].
B. Annealed-Temper Copper Tube:  [ASTM B 280, Type ACR] [ASTM B 88M, Type B (ASTM B 88, Type L)] [ASTM B 88M, Type A (ASTM B 88, Type K)].

C. Wrought-Copper Fittings:  ASME B16.22.

D. Wrought-Copper Unions:  ASME B16.22.

Use BAg-5 (silver) where the use of cadmium-containing filler metal is prohibited, especially in dairy and food industries.

E. Brazing Filler Metals:  AWS A5.8, Classification  [BAg-1 (silver)] [BAg-2 (silver)]

F. Flexible Connectors:  500-psig (3450-kPa) minimum operating pressure; seamless tin-bronze core, high-tensile bronze-braid covering, and solder-joint end connections; dehydrated, pressure tested, minimum 180mm (7 inches) long

2.3 STEEL PIPE AND FITTINGS

A. Steel Pipe:  ASTM A 53, Schedule 40, seamless black steel.

B. Wrought-Steel Fittings:  ASTM A 234/A 234M, for welded joints.

C. Steel Flanges and Flanged Fittings:  ASME B16.5, steel, including bolts, nuts, and gaskets, butt-welded end connection, and raised face.

D. Flanged Unions:  2760-kPa (400-psig) working pressure, 165 deg C (330 deg F) maximum operating temperature; 2 brass tailpiece adapters for solder-end connections to copper tubing; forged-steel flanges for DN 25 to DN 40 (NPS 1 to NPS 1-1/2) and ductile iron for DN 50 to DN 80 (NPS 2 to NPS 3) with 4 plated-steel bolts, with silicon bronze nuts and fiber gasket; and having factory-applied, rust-resistant coating on flanges and bolts.

E. Flexible connectors:  3450-kPa (500-psig) minimum operating pressure; stainless-steel core and high-tensile stainless-steel-braid covering; dehydrated, pressure tested, minimum 180 mm (7 inches) long.

1. NPS 2 (DN 50) and Smaller:  With thread-end connections.

2. NPS 2-1/2 (DN 65) and Larger:  With flanged-end connections.

2.4 VALVES

A. Diaphragm Packless Valves:  3450-kPa (500-psig) working pressure and 135 deg C (275 deg F) working temperature; globe design with straight-through or angle pattern; forged-brass or bronze body and bonnet, phosphor bronze and stainless-steel diaphragms, rising stem and handwheel, stainless-steel spring, nylon seat disc, and with solder-end connections.

B. Packed-Angle Valves:  3450-kPa (500-psig) working pressure and 135 deg C (275 deg F) working temperature; forged-brass or bronze body, forged-brass seal caps with copper gasket, back seating, rising stem and seat, molded stem packing, and with solder-end connections.

C. Check Valves Smaller Than DN 25 (NPS 1):  2760-kPa (400-psig) operating pressure and 141 deg C (285 deg F) operating temperature; cast-brass body, with removable piston, polytetrafluoroethylene seat, and stainless-steel spring; globe design.  Valve shall be straight-through pattern, with solder-end connections.

D. Check Valves, DN 25 (NPS 1) and Larger:  2760-kPa (400-psig) operating pressure and 141 deg C (285 deg F) operating temperature; cast-bronze body, with cast-bronze or forged-brass bolted bonnet; floating piston with mechanically retained polytetrafluoroethylene seat disc.  Valve shall be straight-through or angle pattern, with solder-end connections.

E. Service Valves:  3450-kPa (500-psig) pressure rating; forged-brass body with copper stubs, brass caps, removable valve core, integral ball check valve, and with solder-end connections.

Solenoid valves below are made normally closed and normally open.  Normally closed are direct acting and pilot operated.  Holding coils are available in several voltages.  Manual operator is optional.

F. Solenoid Valves:  Comply with ARI 760; 121 deg C (250 deg F) temperature rating and 2760-kPa (400-psig) working pressure; forged brass, with polytetrafluoroethylene valve seat, 2-way, straight-through pattern, and solder-end connections; manual operator; fitted with suitable NEMA 250 enclosure of type required by location, with 16-GRC (1/2-inch) conduit adapter and [24] [120]-V, normally [closed] [open] holding coil.

Select one of two paragraphs below unless both are required for Project.

G. Pressure-Regulating Valves:  Comply with ARI 770; pilot operated, forged brass or cast bronze, stainless-steel bottom spring, pressure-gage tappings, 24-V dc standard coil, and wrought-copper fittings for solder-end connections; suitable for refrigerant specified.

H. Pressure-Regulating Valves:  Comply with ARI 770; direct acting, brass; with pilot operator, stainless-steel diaphragm, standard coil, and solder-end connection; suitable for refrigerant specified.

I. Pressure Relief Valves:  Straight-through or angle pattern, brass body and disc, neoprene seat, and factory sealed and ASME labeled for standard pressure setting.

Thermostatic expansion valves below are factory adjusted to proper superheat settings for evaporator before shipment.  Fine tuning is not normally required unless application or operation conditions are different from those anticipated.

J. Thermostatic Expansion Valves:  Comply with ARI 750; brass body with stainless-steel parts; thermostatic-adjustable, modulating type; size and operating characteristics as recommended by manufacturer of evaporator, and factory set for superheat requirements; solder-end connections; with sensing bulb, distributor having side connection for hot-gas bypass line, and external equalizer line.

K. Hot-Gas Bypass Valve:  Pulsating-dampening design, stainless-steel bellows and polytetrafluoroethylene valve seat; adjustable; sized for capacity equal to last step of compressor unloading; with solder-end connections.

2.5 REFRIGERANT PIPING SPECIALITIES

A. Straight- or Angle-Type Strainers:  3450-kPa (500-psig) working pressure; forged-brass or steel body with stainless-steel wire or brass-reinforced Monel screen of 80 to 100 mesh in liquid lines up to 30 mm (1-1/8 inches), 60 mesh in larger liquid lines, and 40 mesh in suction lines; with screwed cleanout plug and solder-end connections.

Indicators are also available for working pressures of 430 and 460 psig (2960 and 3170 kPa).

B. Moisture/Liquid Indicators:  3450-kPa (500-psig) maximum working pressure and 93 deg C (200 deg F) operating temperature; all-brass body with replaceable, polished, optical viewing window with color-coded moisture indicator; with solder-end connections.

Filter-dryers below are also available for working pressures of 350 psig (2410 kPa).

C. Replaceable-Core Filter-Dryers:  3450-kPa (500-psig) maximum working pressure; heavy gage protected with corrosion-resistant-painted steel shell, flanged ring and spring, ductile-iron cover plate with steel cap screws; wrought-copper fittings for solder-end connections; with replaceable-core kit, including gaskets and the following:

Select one of three cartridges below.

1. Filter Cartridge:  Pleated media with integral end rings, stainless-steel support, ARI 730 rated for capacity.

2. Filter-Dryer Cartridge:  Pleated media with solid-core sieve with activated alumina, ARI 730 rated for capacity.

3. Wax Removal Cartridge:  Molded, bonded core of activated charcoal and desiccant with integral gaskets.

Filter-dryers below are also available for working pressures of 400 and 500 psig (2760 and 3450 kPa).

D. Permanent Filter-Dryer:  2410-kPa (350-psig) maximum operating pressure and 107 deg C (225 deg F) maximum operating temperature; steel shell and wrought-copper fittings for solder-end connections; molded-felt core surrounded by desiccant.

E. Mufflers:  3450-kPa (500-psig) operating pressure, welded-steel construction with fusible plug; sized for refrigeration capacity.

2.6 RECEIVERS

A. Receivers, 150-mm (6-Inch) Diameter and Smaller:  ARI 495, UL listed, steel, brazed, 2760-kPa (400-psig) pressure rating, with tappings for inlet, outlet, and pressure relief valve.

B. Receivers Larger Than 150-mm (6-Inch) Diameter:  ARI 495, welded steel, tested and stamped according to ASME Boiler and Pressure Vessel Code:  Section VIII; 2760-kPa (400-psig) pressure rating, with tappings for liquid inlet and outlet valves, pressure relief valve, and liquid-level indicator.

2.7 REFRIGERANTS

A. ASHRAE 34, R-123:  Dichlorotrifluoroethane.

B. ASHRAE 34, R-134a:  Tetrafluoroethane.

C. ASHRAE 34, R-22:  Monochlorodifluoromethane.

PART 3 -  EXECUTION

3.1 PIPING APPLICATIONS

A. Aboveground, within Building:  [Type ACR drawn-copper tubing] [Type B (Type L) drawn-copper tubing] [Steel pipe].

Select one of two options in paragraph below.

B. Belowground without joints for DN 50 (NPS 2) and smaller:  [Type B (Type L)] [Type A (Type K)] annealed-copper tubing.

C. Below ground when joints are necessary for DN 50 (NPS 2) and smaller:  [Type A (Type K)] drawn-copper tubing.

3.2 VALVE APPLICATIONS

A. Install diaphragm packless or packed-angle valves in suction and discharge lines of compressor, for gage taps at hot-gas bypass regulators, on each side of strainers.

B. Install check valves in compressor discharge lines and in condenser liquid lines on multiple condenser systems.

C. Install packed-angle valve in liquid line between receiver shutoff valve and thermostatic expansion valve for system charging.

D. Install diaphragm packless or packed-angle valves on each side of strainers and dryers, in liquid and suction lines at evaporators, and elsewhere as indicated.

E. Install a full-sized, three-valve bypass around each dryer.

F. Install solenoid valves upstream from each expansion valve and hot-gas bypass valve.

1. Install solenoid valves in horizontal lines with coil at top.

2. Electrical wiring for solenoid valves is specified in Division 16 Sections.  Coordinate electrical requirements and connections.

G. Install thermostatic expansion valves as close as possible to evaporator.

1. If refrigerant distributors are used, install them directly on expansion-valve outlet.

2. Install valve so diaphragm case is warmer than bulb.

Verify proper location for bulb with valve manufacturer.

3. Secure bulb to clean, straight, horizontal section of suction line using two bulb straps.  Do not mount bulb in a trap or at bottom of the line.

4. If external equalizer lines are required, make connection where it will reflect suction-line pressure at bulb location.

H. Install pressure-regulating and pressure relief valves as required by ASHRAE 15.  Pipe pressure relief valve discharge to outside.

3.3 SPECIALTY APPLICATIONS

A. Install liquid indicators in liquid line leaving condenser, in liquid line leaving receiver, and on leaving side of liquid solenoid valves.

B. Install strainers immediately upstream from each automatic valve, including expansion valves, solenoid valves, hot-gas bypass valves, and compressor suction valves.

C. Install strainers in main liquid line where multiple expansion valves with integral strainers are used.

D. Install strainers in suction line of steel pipe.

E. Install moisture-liquid indicators in liquid lines between filter-dryers and thermostatic expansion valves and in liquid line to receiver.

F. Install pressure relief valves on ASME receivers; pipe discharge to outdoors.

G. Install replaceable-core filter-dryers in vertical liquid line adjacent to receivers and before each solenoid valve.

H. Install permanent filter-dryers in low-temperature systems, in systems using hermetic compressors, and before each solenoid valve.

I. Install solenoid valves in liquid line of systems operating with single pump-out or pump-down compressor control, in liquid line of single or multiple evaporator systems, and in oil bleeder lines from flooded evaporators to stop flow of oil and refrigerant into suction line when system shuts down.

J. Install receivers, sized to accommodate pump-down charge, on systems 17.5 kW (5 tons) and larger and on systems with long piping runs.

K. Install flexible connectors at or near compressors.

3.4 PIPING INSTALLATION

A. Install refrigerant piping according to ASHRAE 15.

B. Basic piping installation requirements are specified in Division 15 Section "Basic Mechanical Materials and Methods."

C. Install piping as short and direct as possible, with a minimum number of joints, elbows, and fittings.

D. Arrange piping to allow inspection and service of compressor and other equipment.  Install valves and specialties in accessible locations to allow for service and inspection.

E. Install piping with adequate clearance between pipe and adjacent walls and hangers or between pipes for insulation installation.  Use sleeves through floors, walls, or ceilings, sized to permit installation of full-thickness insulation.

F. Belowground, install copper tubing in protective conduit.  Vent conduit outdoors.

G. Install copper tubing in rigid or flexible conduit in locations where copper tubing will be exposed to mechanical injury.

H. Slope refrigerant piping as follows:

See Evaluations for a discussion about oil entrainment.  Refer to ASHRAE's HANDBOOK--"Refrigeration" for a discussion on methods to manage oil entrainment in refrigerant gas and liquid.

1. Install horizontal hot-gas discharge piping with a uniform slope downward away from compressor.

2. Install horizontal suction lines with a uniform slope downward towards to compressor.

Use double-suction riser for maximum compressor efficiencies if load variation is expected.

3. Install traps and double risers to entrain oil in vertical runs.

4. Liquid lines may be installed level.

I. Install bypass around moisture-liquid indicators in lines larger than DN 50 (NPS 2).

J. Install unions to allow removal of solenoid valves, pressure-regulating valves, and expansion valves and at connections to compressors and evaporators.

K. When brazing, remove solenoid-valve coils and sight glasses; also remove valve stems, seats, and packing, and accessible internal parts of refrigerant specialties.  Do not apply heat near expansion valve bulb.

L. Hanger, support, and anchor products are specified in Division 15 Section "Hangers and Supports."

M. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal runs less than 6.0 m (20 feet) long.

2. Roller hangers and spring hangers for individual horizontal runs 6.0 m (20 feet) or longer.

3. Pipe rollers for multiple horizontal runs 6.0 m (20 feet) or longer, supported by a trapeze.

4. Spring hangers to support vertical runs.

N. Install hangers for copper tubing with the following maximum spacing and minimum rod sizes:

1. DN 15 (NPS 1/2):  Maximum span, 1500 mm (60 inches); minimum rod size, 6.4 mm (1/4 inch).

2. DN 18 (NPS 5/8):  Maximum span, 1500 mm (60 inches); minimum rod size, 6.4 mm (1/4 inch).

3. DN 25 (NPS 1):  Maximum span, 1800 mm (72 inches); minimum rod size, 6.4 mm (1/4 inch).

4. DN 32 (NPS 1-1/4):  Maximum span, 2400 mm (96 inches); minimum rod size, 9.5 mm (3/8 inch).

5. DN 40 (NPS 1-1/2):  Maximum span, 2400 mm (96 inches); minimum rod size, 9.5 mm (3/8 inch).

6. DN 50 (NPS 2):  Maximum span, 2400 mm (96 inches); minimum rod size, 9.5 mm (3/8 inch).

7. DN 65 (NPS 2-1/2):  Maximum span, 2700 mm (108 inches); minimum rod size, 9.5 mm (3/8 inch).

8. DN 80 (NPS 3):  Maximum span, 3 m (10 feet); minimum rod size, 9.5 mm (3/8 inch).

9. DN 100 (NPS 4):  Maximum span, 3.7 m (12 feet); minimum rod size, 13 mm (1/2 inch).

O. Install hangers for steel piping with the following maximum spacing and minimum rod sizes:

1. DN 15 (NPS 1/2):  Maximum span, 2100 mm (84 inches); minimum rod size, 6.4 mm (1/4 inch).

2. DN 20 (NPS 3/4):  Maximum span, 2100 mm (84 inches); minimum rod size, 6.4 mm (1/4 inch).

3. DN 25 (NPS 1):  Maximum span, 2100 mm (84 inches); minimum rod size, 6.4 mm (1/4 inch).

4. DN 40 (NPS 1-1/2):  Maximum span, 2700 mm (108 inches); minimum rod size, 9.5 mm (3/8 inch).

5. DN 50 (NPS 2):  Maximum span, 3 m (10 feet); minimum rod size, 9.5 mm (3/8 inch).

6. DN 65 (NPS 2-1/2):  Maximum span, 3.4 m (11 feet); minimum rod size, 9.5 mm (3/8 inch).

7. DN 80 (NPS 3):  Maximum span, 3.7 m (12 feet); minimum rod size, 9.5 mm (3/8 inch).

8. DN 100 (NPS 4):  Maximum span, 4.3 m (14 feet); minimum rod size, 13 mm (1/2 inch).

P. Support vertical runs at each floor.

3.5 PIPE JOINT CONSTRUCTION

A. Braze joints according to Division 15 Section "Basic Mechanical Materials and Methods."

B. Fill pipe and fittings with an inert gas (nitrogen or carbon dioxide) during brazing to prevent scale formation.

3.6 FIELD QUALITY CONTROL

A. Test and inspect refrigerant piping according to ASME B31.5, Chapter VI.

1. Test refrigerant piping, specialties, and receivers.  Isolate compressor, condenser, evaporator, and safety devices from test pressure.

2. Test high- and low-pressure side piping of each system at not less than the lower of the design pressure or the setting of pressure relief device protecting high and low side of system.

a. System shall maintain test pressure at the manifold gage throughout duration of test.

b. Test joints and fittings by brushing a small amount of soap and glycerine solution over joint.

c. Fill system with nitrogen to raise a test pressure of 1035 kPa (150 psig) or higher as required by authorities having jurisdiction.

d. Remake leaking joints using new materials and retest until satisfactory results are achieved.

3.7 ADJUSTING

A. Adjust thermostatic expansion valve to obtain proper evaporator superheat requirements.

B. Adjust high- and low-pressure switch settings to avoid short cycling in response to fluctuating suction pressure.

C. Adjust set-point temperature of the conditioned air or chilled-water controllers to the system design temperature.

D. Perform the following adjustments before operating the refrigeration system, according to manufacturer's written instructions:

1. Open shutoff valves in condenser water circuit.

2. Check compressor oil level above center of sight glass.

3. Open compressor suction and discharge valves.

4. Open refrigerant valves, except bypass valves that are used for other purposes.

5. Check compressor-motor alignment, and lubricate motors and bearings.

3.8 CLEANING

This Article is required if tubing other than Type ACR is allowed.

A. Before installing copper tubing other than Type ACR, clean tubing and fittings with trichloroethylene.

B. Replace core of filter-dryer after system has been adjusted and design flow rates and pressures are established.

3.9 SYSTEM CHARGING

A. Charge system using the following procedures:

1. Install core in filter-dryer after leak test but before evacuation.

Before charging with refrigerant, perform three successive evacuations with the entire system at an ambient temperature of 15C (60˚F).  If the ambient temperature is below 15C (60˚F), provide a sufficient number of heaters to keep the entire system at or above the specified temperature.  Break the first two evacuations with dry nitrogen or carbon dioxide.  Evacuate entire refrigerant system with a vacuum pump to a vacuum of 67 Pa (500 micrometers).  If vacuum holds for 12 hours, system is ready for charging.

2. Break the third vacuum with refrigerant gas, allowing pressure to build up to 14 kPa (2 psig).

3. Charge system with a new filter-dryer core in charging line.  Provide full-operating charge.

END OF SECTION 15183
REFRIGERANT PIPING
15183 - 12

