Copyright 2002 AIA
GSA VERSION MASTERSPEC
12/02 (GSA 03/05)

Copyright 2002, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15194 - FUEL GAS PIPING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes fuel gas piping and valves within the building.  Products include the following:

Adjust list below to suit Project.

1. Pipe, tube, fittings, and joining materials.

2. Protective pipe and fitting coating.

3. Piping specialties.

4. Specialty valves.

5. Service meters.

6. Pressure regulators.

B. Related Sections include the following:

List below only those sections that specify products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Natural Gas Distribution" for natural gas service piping, specialties, and accessories outside the building.

2. Division 2 Section "Liquid Petroleum Gas Distribution."

1.3 PROJECT CONDITIONS

Retain one of first four paragraphs below.  If retaining first paragraph, select one pressure range.

A. Gas System Pressure:  One pressure range.  [3.45 kPa (0.5 psig) or less] [More than 3.45 kPa (0.5 psig) but not more than 13.8 kPa (2.0 psig)] [More than 13.8 kPa (2.0 psig) but not more than 34.5 kPa (5.0 psig)].  More than 34.5 kPa (5.0 psig) but not more than 69 kPa (10.0 psig).
B. Gas System Pressures:  Two pressure ranges.  Primary pressure is more than 3.45 kPa (0.5 psig) but not more than 13.8 kPa (2.0 psig), and is reduced to secondary pressure of 3.45 kPa (0.5 psig) or less.

C. Gas System Pressures:  Two pressure ranges.  Primary pressure is more than 13.8 kPa (2.0 psig) but not more than 34.5 kPa (5.0 psig), and is reduced to secondary pressure of more than 3.45 kPa (0.5 psig) but not more than 13.8 kPa (2.0 psig).

D. Gas System Pressures:  Three pressure ranges.  Primary pressure is more than 13.8 kPa (2.0 psig) but not more than 34.5 kPa (5.0 psig), and is reduced to secondary pressures of more than 3.45 kPa (0.5 psig) but not more than 13.8 kPa (2.0 psig), and is reduced again to pressures of 3.45 kPa (0.5 psig) or less.

E. Gas System Pressures:  Four pressure ranges.  Primary pressure is more than 34.5 kPa (5.0 psig) but not more than 6.9 kPa (10.0 psig) and is reduced to a tertiary pressure that is more than 13.8 kPa (2.0 psig) but not more than 34.5 kPa (5.0 psig), and is reduced to secondary pressures of more than 3.45 kPa (0.5 psig) but not more than 13.8 kPa (2.0 psig), and is reduced again to pressures of 3.45 kPa (0.5 psig) or less.

F. Design values of fuel gas supplied for these systems are as follows:

Edit first two subparagraphs below as required for natural gas.  Verify values with gas utility.

Natural gas heating value options in subparagraph below should range between 900 and 1100 Btu/cu. ft. (33.5 and 41.0 MJ/cu. m).  1000 or 1050 Btu/cu. ft. (37.3 or 39.1 MJ/cu. m) is typical.

1. Nominal Heating Value:  [37.3 MJ/cu. m (1000 Btu/cu. ft.)] [39.1 MJ/cu. m (1050 Btu/cu. ft.)] <Insert heating value>.

Natural gas specific gravity in subparagraph below ranges between 0.55 and 1.0.  Specific gravity of 0.6 is typical.

2. Nominal Specific Gravity:  [0.6] <Insert specific gravity>.

Retain two subparagraphs above or two subparagraphs below.  Retain and edit below for liquefied petroleum gas.  Verify values with gas supplier.  Propane typical heating value is 2500 Btu/cu. ft. (93 MJ/cu. m).  Butane typical heating value is 3200 Btu/cu. ft. (119.4 MJ/cu. m).

3. Nominal Heating Value:  [93 MJ/cu. m (2500 Btu/cu. ft.)] [119.4 MJ/cu. m (3200 Btu/cu. ft.)] <Insert heating value>.

Propane typical specific gravity is 1.59.  Butane typical specific gravity is 2.11.  In subparagraph below, select proper values for specified fuel or insert values advertised by local suppliers.

4. Nominal Specific Gravity:  [1.59] [2.11] <Insert specific gravity>.

1.4 SUBMITTALS

A. Product Data:  For the following:

1. Corrugated, stainless-steel tubing systems.  Include associated components.

2. Specialty valves.  Include pressure rating, capacity, settings, and electrical connection data of selected models.

3. Service-meter bars.  Include service-meter size of selected models.

4. Service meters.  Include pressure rating and capacity of selected models.

5. Service-meter bypass fittings.

6. Pressure regulators.  Include pressure rating, capacity, and settings of selected models.

Delete option in paragraph below if whole system is same pressure.

B. Shop Drawings:  For fuel gas piping.  Include plans and attachments to other work.[  Show different pressure zones and indicate pressure for each zone.]

Retain subparagraph below if equipment includes wiring.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For natural gas specialties and accessories to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

Retain paragraph below for pipe welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding:  Qualify processes and operators according to ASME Boiler and Pressure Vessel Code:  Section IX.

Retain paragraph below for electrically operated components, devices, or accessories.

B. Electrical Components and Devices:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Authorities having jurisdiction may have gas codes more restrictive than NFPA 54 in paragraph below.

C. NFPA Standard:  Comply with NFPA 54, "National Fuel Gas Code."

D. International Building Code:  Comply with “International Fuel Gas Code”.

1.6 DELIVERY, STORAGE, AND HANDLING

Retain this Article for projects involving existing systems.

A. Handling Flammable Liquids:  Remove and legally dispose of liquids from drips in existing gas piping.  Handle cautiously to avoid spillage and ignition.  Notify fuel gas supplier.  Handle flammable liquids used by Installer with proper precautions and do not leave on premises from end of one day to beginning of next day.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2.2 PIPING MATERIALS

A. Refer to Part 3 "Piping Applications" Article for applications of pipe, tube, fitting, and joining materials.

2.3 CORRUGATED, STAINLESS-STEEL TUBING SYSTEMS

Systems in this Article are limited to 5 psig (34.5 kPa) and less and NPS 2 (DN 50) and smaller.  Contact authorities having jurisdiction and verify approval before specifying system and design pressure.

A. Description:  Comply with AGA LC 1 and include the following:

1. Tubing:  Corrugated stainless steel with plastic jacket or coating.

2. Fittings:  Copper alloy with ends made to fit corrugated tubing.  Include ends with threads according to ASME B1.20.1 if connection to threaded pipe or fittings is required.

3. Striker Plates:  Steel, designed to protect tubing from penetrations.

4. Manifolds:  Malleable iron or steel with protective coating.  Include threaded connections according to ASME B1.20.1 for pipe inlet and corrugated tubing outlets.

5. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. OmegaFlex, Inc.

b. Titeflex Corp.

c. Tru-Flex Metal Hose Corp.

d. Ward Industries, Inc.

e. <Insert manufacturer's name.>

2.4 PIPES, TUBES, FITTINGS, AND JOINING MATERIALS

See Evaluations for pipe material selection considerations.

A. Steel Pipe:  ASTM A 53/A 53M; Type E or S; Grade B; black.  Wall thickness of wrought-steel pipe shall comply with ASME B36.10M.

Retain one of applicable sub paragraphs of the first three subparagraphs below.

1. Malleable-Iron Threaded Fittings:  ASME B16.3, Class 150, standard pattern, with threaded ends according to ASME B1.20.1.

2. Steel Threaded Fittings:  ASME B16.11, forged steel with threaded ends according to ASME B1.20.1.

3. Steel Welding Fittings:  ASME B16.9, wrought steel or ASME B16.11, forged steel.

4. Unions:  ASME B16.39, Class 150, malleable iron with brass-to-iron seat, ground joint, and threaded ends according to ASME B1.20.1.

5. Cast-Iron Flanges and Flanged Fittings:  ASME B16.1, Class 125.

6. Joint Compound and Tape:  Suitable for natural gas.

7. Steel Flanges and Flanged Fittings:  ASME B16.5.

8. Gasket Material:  Thickness, material, and type suitable for natural gas.

Tube in paragraph below is available in 1/4- to 5/8-inch (6.3- to 15.8-mm) OD and is equivalent to NPS 1/8 to NPS 1/2 (DN 6 to DN 15).

2.5 PROTECTIVE COATING

Retain this Article if coating is required.  Indicate on Drawings where coating is required.

A. Furnish pipe and fittings with factory-applied, corrosion-resistant polyethylene coating for use in contact with materials that may corrode the pipe.

B. Wrap fittings and joints with a polyethylene tape approved by the supplier of the polyethylene coating.

2.6 PIPING SPECIALTIES

A. Flexible Connectors:  ANSI Z21.24, copper alloy.

B. Quick-Disconnect Devices:  ANSI Z21.41, convenience outlets and matching plug connector.

2.7 SPECIALTY VALVES

A. Valves, DN 50 (NPS 2) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

B. Valves, DN 65 (NPS 2-1/2) and Larger:  Flanged ends according to ASME B16.5 for steel flanges.

Valves in category below are limited to 0.5 psig (3.45 kPa), are used for shutoff service to appliances, and are NPS 3/4 (DN 20) and smaller.

C. Appliance Connector Valves:  ANSI Z21.15 and CSA International listed.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
The purpose of listing manufacturers is to inform contractors of manufacturers with the capacity to provide the product(s) specified.  Long lists should be edited to a modest length representing general geographical availability.

a. American Valve Inc.

b. B&K Industries, Inc.

c. Brass Craft Manufacturing Co.

d. Cimberio Valves, S. p. A.

e. Conbraco Industries, Inc.; Apollo Div.

f. E. M. Plastic and Electric Products, Ltd.; Neo Valve Div.

g. JMF Company.

h. Jomar International Ltd.

i. Key Gas Components, Inc.

j. Legend Valve and Fitting, Inc.

k. McDonald, A. Y. Mfg. Co.

l. Mueller Co.; Mueller Gas Products Div.

m. Newman Hattersley Ltd.; Specialty Valves Div.

n. Robert Manufacturing Co.

o. State Metals, Inc.

p. Watts Industries, Inc.; Water Products Div.

q. <Insert manufacturer's name.>

Gas stops below are NPS 2 (DN 50) and smaller and limited to 2 psig (13.8 kPa).  Use at appliances with 2-psig- (13.8-kPa-) maximum gas pressure systems.  No manufacturers are listed in "Manufacturers" Article for stops in paragraph below because of general availability, and no listing for these stops is required.

D. Gas Stops:  Bronze body with AGA stamp, plug type with bronze plug and flat or square head, ball type with chrome-plated brass ball and lever handle, or butterfly valve with stainless-steel disc and fluorocarbon elastomer seal and lever handle; 13.8-kPa (2-psig) minimum pressure rating.

Valves in first paragraph below are used for shut off.

E. Gas Valves, DN 50 (NPS 2) and Smaller:  ASME B16.33 and CSA International-listed bronze body and 860-kPa (125-psig) pressure rating.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
The purpose of listing manufacturers is to inform contractors of manufacturers with the capacity to provide the product(s) specified.  Long lists should be edited to a modest length representing general geographical availability.
a. BMI Canada, Inc.

b. Crane Valves.

c. Dungs, Karl, Inc.

d. Flow Control Equipment, Inc.

e. Grinnell Corp.

f. Honeywell International Inc.

g. Jomar International Ltd.

h. KITZ Corporation.

i. Legend Valve and Fitting, Inc.

j. Lyall, R. W. & Co., Inc.

k. McDonald, A. Y. Mfg. Co.

l. Milwaukee Valve Company.

m. Mueller Co.; Mueller Gas Products Div.

n. NIBCO INC.

o. Red-White Valve Corp.

p. Velan Inc.

q. Watts Industries, Inc.; Water Products Div.

r. <Insert manufacturer's name.>

Retain subparagraph below if required.  Verify that feature is available if specified.

2. Tamperproof Feature:  Include design for locking.

F. Plug Valves, DN 65 (NPS 2-1/2) and Larger:  ASME B16.38 and MSS SP-78 cast-iron, lubricated plug valves, with 860-kPa (125-psig) pressure rating.

Flow Control and Olson Technologies are also CSA International-listed valves.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Flow Control Equipment, Inc.

b. Milliken Valve Co., Inc.

c. Nordstrom Valves, Inc.

d. Olson Technologies, Inc.; Homestead Valve Div.

e. Walworth Co.

f. <Insert manufacturer's name.>

Retain subparagraph below if required.  Verify that feature is available if specified.

2. Tamperproof Feature:  Include design for locking.

No manufacturers are listed in "Manufacturers" Article for valves in paragraph and subparagraphs below because of large number of manufacturers.

G. General-Duty Valves, DN 65 (NPS 2-1/2) and Larger:  ASME B16.38, cast-iron body, suitable for fuel gas service, with "WOG" indicated on valve body, and 860-kPa (125-psig) pressure rating.

1. Gate Valves:  MSS SP-70, OS&Y type with solid wedge.

2. Butterfly Valves:  MSS SP-67, lug type with lever handle.

Valves in paragraph below are used in gas piping for automatic shutoff service when interlocked with a hazard-condition initiating device.  Select type of operation.

H. Automatic Gas Valves:  ANSI Z21.21, with [electrical] [mechanical] operator for actuation by appliance automatic shutoff device.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. ASCO General Controls.

b. ASCO Power Technologies, LP; Division of Emerson.

c. ASCO Valve Canada, Division of Emerson Electric Canada Limited.

d. Dungs, Karl, Inc.

e. Eaton Corporation; Controls Div.

f. Eclipse Combustion, Inc.

g. GPS Gas Protection Systems Inc.

h. Honeywell International Inc.

i. Johnson Controls.

j. <Insert manufacturer's name.>

Valves in first paragraph below are solenoid type and are used in gas piping for automatic shutoff service when interlocked with a hazard-condition initiating device.  Refer to UL 1002 for valves for use in hazardous locations.

I. Electrically Operated Gas Valves:  UL 429, bronze, aluminum, or cast-iron body solenoid valve; 120-V ac, 60 Hz, Class B, continuous-duty molded coil.  Include NEMA ISC 6, Type 4, coil enclosure and electrically opened and closed dual coils.  Valve position shall normally be closed.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. ASCO General Controls.

b. ASCO Power Technologies, LP; Division of Emerson.

c. Dungs, Karl, Inc.

d. Eclipse Combustion, Inc.

e. Goyen Valve Corp.; Tyco Environmental Systems.

f. Magnatrol Valve Corp.

g. Parker Hannifin Corporation; Climate & Industrial Controls Group; Skinner Valve Div.

h. Watts Industries, Inc.

i. <Insert manufacturer's name.>

J. Earthquake Valves:  Listed in CSA International's "Certified Product Listing Directory:  Components for Gas and Electrical Equipment" as complying with ASCE 25 and UL listed.

Retain one of three earthquake-valve types below or include two or more for Contractor's option.

1. Earthquake-Valve, Type 1:  Working-pressure rating is [172 kPa (25 psig)] [862 kPa (125 psig)].  Cast-aluminum body with stainless-steel internal parts.  Buna-N, reset-stem, O-ring seal.  Threaded end connections.

a. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1) Safe T Quake Corp.

2) <Insert manufacturer's name.>

2. Earthquake-Valve, Type 2:  Working-pressure rating is 34.5 kPa (5 psig).  Cast-aluminum body with nickel-plated chrome steel internal parts.  Nitrile valve washer.  Sight windows for visual indication of valve position.  Threaded end connections.  Wall mounting bracket with bubble level indicator.

a. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1) Vanguard Valves, Inc.

2) <Insert manufacturer's name.>

3. Earthquake-Valve, Type 3:  Working-pressure rating is [3.45 kPa (0.5 psig)] [48 kPa (7 psig)] [414 kPa (60 psig)].  Cast-aluminum body with stainless-steel internal parts.  Buna-N, reset-stem, O-ring seal.  Composition valve seat with clapper held by spring or magnet locking mechanism.  Valve position, open or closed, indicator.  Level indicator.  Threaded end connections through DN 50 (NPS 2), and flanged connections for DN 65 (NPS 2-1/2) and larger.

a. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1) Pacific Seismic Products, Inc.

2) <Insert manufacturer's name.>

2.8 SERVICE METERS

Meter bars or other supports, service meters, and service pressure regulators are usually provided by gas supplier.  Delete this Article if they are furnished by gas supplier, are specified in Division 2 Section "Natural Gas Distribution," or are not required.  Retain applicable paragraphs below if submeters are required.

A. Service Meters:  Positive-displacement type suitable for fuel gas service.  Include metal case, temperature compensation, corrosion-resistant internal components, and flow registered in liters (cubic feet).

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Diaphragm-Type Service Meters:

1) American Meter Company.

2) Badger Meter, Inc.; Utility Products Div.

3) Invensys.

4) National Meter Industries, Inc.

5) Schlumberger Limited; Gas Div.

6) <Insert manufacturer's name.>

b. Rotary-Type Service Meters:

1) American Meter Company.

2) Schlumberger Limited; Gas Div.

3) <Insert manufacturer's name.>

2. DN 50 (NPS 2) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

3. DN 65 (NPS 2-1/2) and Larger:  Flanged ends according to ASME B16.5 for steel flanges.

Retain one of three subparagraphs below or "Turbine Meters" Paragraph and subparagraphs below, or indicate types on Drawings if more than one type is required.

4. Type:  ANSI B109.1, diaphragm, with capacities 3935 mL/s (500 cfh) and less.

5. Type:  ANSI B109.2, diaphragm, with capacities more than 3935 mL/s (500 cfh).

6. Type:  ANSI B109.3, rotary.

B. Turbine Meters:  Axial-flow type suitable for fuel gas service.  Comply with construction criteria for axial-flow, gas turbine meters in ASME MFC-4M.  Include metal body, corrosion-resistant internal components, and flow registered in liters (cubic feet).

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. American Meter Company.

b. Invensys.

c. <Insert manufacturer's name.>

2. DN 50 (NPS 2) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

3. DN 65 (NPS 2-1/2) and Larger:  Flanged ends according to ASME B16.5 for steel flanges.

Service-meter bars in first paragraph below are normally limited to NPS 1 (DN 25) service meters.

C. Service-Meter Bars:  Malleable- or cast-iron frame for supporting service meter.  Include offset swivel pipes, meter nuts with O-ring seal, factory- or field-installed dielectric unions, and threaded ends complying with ASME B1.20.1.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. American Meter Company.

b. Lyall, R. W. & Co., Inc.

c. McDonald, A. Y. Mfg. Co.

d. Mueller Co.; Mueller Gas Products Div.

e. National Meter Industries, Inc.

f. Perfection Corporation.

g. Schlumberger Limited; Gas Div.

h. <Insert manufacturer's name.>

2. Exception:  Omit meter offset swivel pipes if service-meter bar dimensions match service-meter connections.

D. Service-Meter Bypass Fittings:  Ferrous, tee, pipe fitting with integral ball check valve and capped side inlet for temporary fuel gas supply.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Lyall, R. W. & Co., Inc.

b. Williamson, T. D., Inc.

c. <Insert manufacturer's name.>

2.9 PRESSURE REGULATORS

Service pressure regulators in first paragraph below are usually provided by gas supplier.  Delete paragraph and subparagraphs if service regulators are specified in Division 2 Section "Natural Gas Distribution" or are not required.

A. Description:  Single stage and suitable for fuel gas service.  Include steel jacket and corrosion-resistant components, elevation compensator, and atmospheric vent.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Regulators in list below are ANSI Z21.80 or CGA 6.22 line pressure regulators or CGA 6.18 service type.  Regulators with at least 100-psig (690-kPa) working-pressure rating are suitable for use as service regulators.

a. Service Pressure Regulators:

1) American Meter Company.

2) Fisher Controls International, Inc.; Division of Emerson.

3) Invensys.

4) National Meter Industries, Inc.

5) Richards Industries, Inc.; Jordan Valve Div.

6) Schlumberger Limited; Gas Div.

7) <Insert manufacturer's name.>

Regulators in list below are ANSI Z21.80 or CGA 6.22 line pressure regulators or CGA 6.18 service type.

b. Line Pressure Regulators:

1) American Meter Company.

2) Donkin, Bryan RMG Canada, Ltd.

3) Eclipse Combustion, Inc.

4) Fisher Controls International, Inc.; Division of Emerson.

5) Invensys.

6) Maxitrol Company.

7) National Meter Industries, Inc.

8) Richards Industries, Inc.; Jordan Valve Div.

9) Schlumberger Limited; Gas Div.

10) <Insert manufacturer's name.>

Regulators in list below are ANSI Z21.18 type.

c. Appliance Pressure Regulators:

1) Canadian Meter Co., Inc.

2) Eaton Corporation; Controls Div.

3) Harper Wyman Co.

4) Maxitrol Company.

5) SCP, Inc.

6) <Insert manufacturer's name.>

2. DN 50 (NPS 2) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

3. DN 65 (NPS 2-1/2) and Larger:  Flanged ends according to ASME B16.5 for steel flanges.

4. Service Pressure Regulators:  ANSI Z21.80.  Include [690-kPa- (100-psig-)] <Insert other> minimum inlet pressure rating.

5. Line Pressure Regulators:  ANSI Z21.80 with [13.8-kPa- (2-psig-) minimum] [34.5-kPa- (5-psig-) minimum] [68.9-kPa (10-psig)] inlet pressure rating.

Retain subparagraph above or first subparagraph below.  If retaining below, indicate each regulator with lower inlet pressure on Drawings.

6. Line Pressure Regulators:  ANSI Z21.80 with 68.9-kPa (10-psig) inlet pressure rating, unless otherwise indicated.

7. Appliance Pressure Regulators:  ANSI Z21.18.  Regulator may include vent limiting device, instead of vent connection, if approved by authorities having jurisdiction.

B. Pressure Regulator Vents:  Factory- or field-installed, corrosion-resistant screen in opening if not connected to vent piping.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for fuel oil piping system to verify actual locations of piping connections before equipment installation.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

Retain this Article for existing projects.

A. Close equipment shutoff valves before turning off fuel gas to premises or section of piping.  Perform leakage test as specified in "Field Quality Control" Article to determine that all equipment is turned off in affected piping section.

3.3 COORDINATION

Retain this Article for existing utilities.  Coordinate with requirements specified in Division 1 Section "Temporary Facilities and Controls" for temporary utilities.

A. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

1. Notify Architect not less than two days in advance of proposed utility interruptions.

2. Do not proceed with utility interruptions without Architect's written permission.

Edit paragraphs below to delete or add types of construction that penetrate or are supported by ceilings.

B. Coordinate layout and installation of fuel gas piping and piping support system components with other construction, including light fixtures, HVAC equipment, fire-suppression-system components, and partition assemblies.

C. Coordinate piping installation with roof curbs, equipment supports, and roof penetrations.  Roof specialties are specified in Division 7 Sections.

D. Coordinate pipe fitting pressure classes with products specified in related Sections.

E. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

F. Coordinate insulation of pipe sleeves for penetrations through fountain walls, exterior walls and floor assemblies.  Coordinate with requirements for firestopping specified in Division 7 Section “Through-Penetration Firestop Systems” for fire and smoke wall and floor assemblies.


3.4 SERVICE-METER ASSEMBLY INSTALLATION

Delete this Article if service meters are specified in Division 2 Section "Natural Gas Distribution," are furnished by gas supplier, or are not required.  Coordinate with "Service Entrance Piping" Article.

Install service-meter assemblies within building if gas contains moisture.

A. Install service-meter assemblies aboveground.

1. Set service-meter assembly on, or supported over, precast concrete bases.  Excavate earth and make level beds to support bases.  Set bases level with top surface projecting 75 mm (3 inches) above finished grade.  Concrete bases are specified in Division 15 Section "Basic Mechanical Materials and Methods."

B. Include gas valve or plug valve, [strainer,] [service pressure regulator,] [service-meter bar for service meter with connections DN 25 (NPS 1) and smaller,] [and service meter] for each assembly.

C. Install gas valve or plug valve and strainer upstream from each service pressure regulator.

D. Install service pressure regulators with vent outlet turned down and with corrosion-resistant-metal insect screen.

Select locations of gages from options in first paragraph below or delete if not required.

E. Install pressure gage [downstream] [upstream and downstream] from each service pressure regulator.  Pressure gages are specified in Division 15 Section "Meters and Gages."

F. Install service meters downstream from service pressure regulators.

1. Service meters with connections DN 25 (NPS 1) and smaller on meter bars.

2. Service meters with connections larger than DN 25 (NPS 1) supported from piping or set on concrete bases.

3.5 SERVICE ENTRANCE PIPING

Delete this Article if new piping will connect to existing piping within building, or retain, coordinate with "Service-Meter Assembly Installation" Article, and edit to suit Project.

A. Extend fuel gas piping and connect to fuel gas distribution for service entrance to building.

1. Exterior fuel gas distribution system piping, service pressure regulator and service meter will be provided by gas utility.

Retain subparagraph above or one of two subparagraphs below.

2. Natural gas distribution system piping, service pressure regulator and service meter are specified in Division 2 Section "Natural Gas Distribution."

3. LP-Gas distribution system piping is specified in Division 2 Section "Liquid Petroleum Gas Distribution."

B. Install dielectric fitting downstream from and adjacent to each service meter unless meter is supported from service-meter bar with integral dielectric fitting.  Install shutoff valve downstream from and adjacent to dielectric fitting.  Dielectric fittings are specified in Division 15 Section "Basic Mechanical Materials and Methods."

C. Install strainer upstream from each earthquake valve.  Strainers are specified in Division 15 Section "Plumbing Specialties."

3.6 PIPING APPLICATIONS

A. Flanges, unions, transition, and special fittings with pressure ratings same as or higher than system pressure rating may be used in applications below, unless otherwise indicated.

Select from piping materials below.  Coordinate with materials specified in Part 2.  Do not use sizes smaller than NPS 1/2 (DN 15), except for corrugated, stainless-steel tubing systems.

B. Fuel Gas Piping, 13.8 kPa (2 psig) or Less:

Minimum recommended steel pipe is NPS 3/4 (DN 20).  Contact authorities having jurisdiction and verify approval before specifying corrugated stainless-steel system.  If required, this system will usually be in addition to steel piping above.

1. [DN 15 (NPS 1/2)] <Insert pipe size> and Smaller:  [DN 20 (NPS 3/4) steel pipe, malleable-iron threaded fittings, and threaded joints] [Corrugated, stainless-steel tubing system and threaded joints].

Contact authorities having jurisdiction and verify approval before specifying corrugated stainless-steel system.  If required, this system will usually be in addition to steel piping above.

2. [DN 20 and DN 25 (NPS 3/4 and NPS 1)] <Insert pipe size range>:  [Steel pipe, malleable-iron threaded fittings, and threaded joints] [Corrugated, stainless-steel tubing system and threaded joints].

Threaded pipe joints are limited to NPS 2 4 (DN 50 100).

3. [DN 32 to DN 50 (NPS 1-1/4 to NPS 2)] <Insert pipe size range>:  Steel pipe, [malleable-iron threaded fittings, and threaded joints [steel welding fittings, and welded] joints.

4. [DN 65 (NPS 2-1/2)] <Insert pipe size> and Larger:  Steel pipe, steel welding fittings, and welded joints.

C. Fuel Gas Piping 13.8 to 34.5 kPa (2 to 5 psig):

Threaded pipe joints are limited to NPS 2 (DN 50).
1. [DN 50 (NPS 2 4)] <Insert pipe size> and Smaller:  Steel pipe, [malleable-iron threaded fittings, and threaded joints [steel welding fittings, and welded] joints.

2. Larger than DN 65 NPS 2-1/2:  Steel pipe, steel welding fittings, and welded joints.

D. Fuel Gas Piping 34.5 to 69 kPa (5 psig to 10 psig):

Threaded pipe joints are limited to NPS 2 (DN 50).

1.

[DN 50 (NPS 2)] <Insert pipe size> and Smaller:  Steel pipe, [malleable-iron threaded fittings, and threaded joints] [steel welding fittings, and welded] joints.

2.

Larger than DN 65 (NPS 2-1/2):  Steel pipe, steel welding fittings, and welded joints.

E. Underground Fuel Gas Piping:  Steel pipe, steel welding fittings, and welded joints.  Encase in containment conduit.

F. Containment Conduits:  Steel pipe, steel welding fittings, and welded joints.  Conduits shall be coated as specified in Part 2, paragraph “Protective Coating” above.
G. Gas Service Piping at Meters and Regulators, More Than 34.5 kPa (5 psig):  Steel pipe, steel welding fittings, and welded joints.

3.7 VALVE APPLICATIONS

A. Appliance Shutoff Valves for Pressure 3.45 kPa (0.5 psig) or Less:  Appliance connector valve or gas stop.

B. Appliance Shutoff Valves for Pressure 3.45 to 13.8 kPa (0.5 to 2 psig):  Gas stop or gas valve.

C. Appliance Shutoff Valves for Pressure 13.8 to 69 kPa (2 to 10 psig):  Gas valve.

D. Piping Line Valves, DN 50 (NPS 2) and Smaller:  Gas valve.

E. Piping Line Valves, DN 65 (NPS 2-1/2) and Larger:  Plug valve or general-duty valve.

F. Valves at Service Meter, DN 50 (NPS 2) and Smaller:  Gas valve.

G. Valves at Service Meter, DN 65 (NPS 2-1/2) and Larger:  Plug valve.

3.8 PIPING INSTALLATION

A. Basic piping installation requirements are specified in Division 15 Section "Basic Mechanical Materials and Methods."

B. Concealed Locations:  Except as specified below, install concealed gas piping in airtight conduit constructed of Schedule 40, seamless, black steel pipe with welded joints.  Vent conduit to outside and terminate with screened vent cap.  Ascertain if gas piping can be routed through return air plenums without containment conduits.
1. Above-Ceiling Locations:  Gas piping may be installed in accessible spaces, subject to approval of authorities having jurisdiction, whether or not such spaces are used as plenums.  Do not locate valves above ceilings.

2. In Floors:  Gas piping with welded joints and protective wrapping specified in Part 2 "Protective Coating" Article may be installed in floors, subject to approval of authorities having jurisdiction.  Surround piping cast in concrete slabs with minimum of 40 mm (1-1/2 inches) of concrete.  Piping may not be in physical contact with other metallic structures such as reinforcing rods or electrically neutral conductors.  Do not embed piping in concrete slabs containing quick-set additives or cinder aggregate.

3. In Floor Channels:  Gas piping may be installed in floor channels, subject to approval of authorities having jurisdiction.  Channels must have cover and be open to space above cover for ventilation.

4. In Partitions:  Do not install concealed piping in solid partitions.  Protect tubing from physical damage when installed inside partitions or hollow walls.

a. Exception:  Tubing passing through partitions or walls.

5. In Walls:  Gas piping with welded joints and protective wrapping specified in Part 2 "Protective Coating" Article may be installed in masonry walls, subject to approval of authorities having jurisdiction.

6. Prohibited Locations:  Do not install gas piping in or through circulating air ducts, clothes or trash chutes, chimneys or gas vents (flues), ventilating ducts, or dumbwaiter or elevator shafts.

a. Exception:  Accessible above-ceiling space specified above.

C. Drips and Sediment Traps:  Install drips at points where condensate may collect including outlets of service meters.  Locate where readily accessible for cleaning and emptying.  Do not install where condensate would be subject to freezing.

1. Construct drips and sediment traps using tee fitting with bottom outlet plugged or capped.  Use minimum-length nipple of 3 pipe diameters, but not less than 75 mm (3 inches) long, and same size as connected pipe.  Install with space between bottom of drip and floor for removal of plug or cap.

D. Conceal pipe installations in walls, pipe spaces, utility spaces, above ceilings, below grade or floors, and in floor channels, unless indicated to be exposed to view.

E. Install fuel gas piping at uniform grade of 0.1 percent slope upward toward risers.

F. Use eccentric reducer fittings to make reductions in pipe sizes.  Install fittings with level side down.

G. Connect branch piping from top or side of horizontal piping.

H. Install unions in pipes DN 50 (NPS 2) and smaller, adjacent to each valve, at final connection to each piece of equipment, and elsewhere as indicated.  Unions are not required on flanged devices.

I. Install flanges on valves, specialties, and equipment having DN 65 (NPS 2-1/2) and larger connections.

J. Install corrugated, stainless-steel tubing system according to manufacturer's written instructions.  Include striker plates to protect tubing from puncture where tubing is restrained and cannot move.

K. Install strainer on inlet of each line pressure regulator and automatic and electrically operated valve.

Select location of gages from options in first paragraph below or delete.

L. Install pressure gage [downstream] [upstream and downstream] from each line pressure regulator.  Pressure gages are specified in Division 15 Section "Meters and Gages."

M. Install vent piping for gas pressure regulators and gas trains, extend outside building, and vent to atmosphere.  Terminate vents with turned-down, reducing-elbow fittings with corrosion-resistant insect screens in large end.

N. Install containment conduits for gas piping below slabs, within building, in gastight conduits extending minimum of 100 mm (4 inches) outside building, and vented to atmosphere.  Terminate vents with turned-down, reducing-elbow fittings with corrosion-resistant insect screens in large end.  Prepare and paint outside of conduits with coal-tar, epoxy-polyamide paint according to SSPC-Paint 16.

3.9 JOINT CONSTRUCTION

A. Basic piping joint construction is specified in Division 15 Section "Basic Mechanical Materials and Methods."

B. Use materials suitable for fuel gas.

1. Brazed Joints:  Make with brazing alloy with melting point greater than 540 deg C (1000 deg F).  Brazing alloys containing phosphorus are prohibited.

Retain paragraph below if protective coatings on welded pipe are required.

C. Patch factory-applied protective coating as recommended by manufacturer at field welds and where damage to coating occurs during construction.

3.10 HANGER AND SUPPORT INSTALLATION

A. Pipe hanger and support and equipment support materials and installation requirements are specified in Division 15 Section "Hangers and Supports."

Maximum spans below are from NFPA 54 or MSS SP-69.  Most restrictive dimensions are described in first paragraph and subparagraphs below.

B. Install hangers for horizontal steel piping with the following maximum spacing and minimum rod sizes:

1. DN 25 (NPS 1) and Smaller:  Maximum span, 2438 mm (96 inches); minimum rod size, 10 mm (3/8 inch).

2. DN 32 (NPS 1-1/4):  Maximum span, 2743 mm (108 inches); minimum rod size, 10 mm (3/8 inch).

3. DN 40 and DN 50 (NPS 1-1/2 and NPS 2):  Maximum span, 2743 mm (108 inches); minimum rod size, 10 mm (3/8 inch).

4. DN 65 to DN 90 (NPS 2-1/2 to NPS 3-1/2):  Maximum span, 3 m (10 feet); minimum rod size, 13 mm (1/2 inch).

5. DN 100 (NPS 4) and Larger:  Maximum span, 3 m (10 feet); minimum rod size, 16 mm (5/8 inch).

C. Install hangers for horizontal corrugated, stainless-steel tubing with the following maximum spacing and minimum rod sizes:

1. DN 10 and DN 15 (NPS 3/8 and NPS 1/2):  Maximum span, 1219 mm (48 inches); minimum rod size, 10 mm (3/8 inch).

2. DN 20 and DN 25 (NPS 3/4 and NPS 1):  Maximum span, 1829 mm (72 inches); minimum rod size, 10 mm (3/8 inch).

3. Option:  Support tubing from structure according to manufacturer's written instructions.

3.11 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of fuel gas piping, fittings, and specialties.

B. Install piping adjacent to appliances to allow service and maintenance.

C. Connect piping to appliances using gas with shutoff valves and unions.  Install valve upstream from and within 1800 mm (72 inches) of each appliance.  Install union downstream from valve.

D. Sediment Traps:  Install tee fitting with capped nipple in bottom to form drip, as close as practical to inlet of each appliance using gas.

Retain two paragraphs and associated subparagraph below for electrically operated devices.

E. Ground equipment according to Division 16 Section "Grounding and Bonding."

1. Do not use gas pipe as grounding electrode.

F. Connect wiring according to Division 16 Section "Conductors and Cables."

3.12 LABELING AND IDENTIFYING

A. Equipment Nameplates and Signs:  Install engraved plastic-laminate equipment nameplate or sign on or near each service meter, pressure regulator, and specialty valve.

1. Text:  In addition to name of identified unit, distinguish between multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations.

2. Nameplates, pipe identification, and signs are specified in Division 15 Section "Mechanical Identification."

3.13 PAINTING

Delete this Article if no exterior service meters, pressure regulators, or piping.

A. Use materials and procedures in Division 9 painting Sections.

B. Paint exterior service meters, pressure regulators, and specialty valves.

1. Color:  [Gray] <Insert color>.

3.14 FIELD QUALITY CONTROL

A. Test, inspect, and purge piping according to NFPA 54 and requirements of authorities having jurisdiction.

B. Repair leaks and defects with new materials and retest system until satisfactory results are obtained.

Verify capacities and pressure ratings of service meters, pressure regulators, valves, and specialties.

C. Verify correct pressure settings for pressure regulators.

D. Verify that specified piping tests are complete.

END OF SECTION 15194
FUEL GAS PIPING
15194 - 1

