Copyright 2002 AIA
GSA VERSION MASTERSPEC
06/02 (R 09/03) (GSA 03/05)

Copyright 2002 (09/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15737 - SELF-CONTAINED AIR-CONDITIONING UNITS (LARGER THAN 15 TONS)
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged air-conditioning units with refrigerant compressors and controls, intended for indoor installations, with [water] [externally mounted air]-cooled condensers.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Samples for Initial Selection:  For units with factory-applied color finishes.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For self-contained air-conditioning units to include in emergency, operation, and maintenance manuals.

F. Warranty:  Special warranty specified in this Section.

Retain paragraph and subparagraph below if HCFC-free refrigerants are required for LEED Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

G. LEED Submittals:

1. Credit EA 4:  Manufacturers' product data for refrigerants, including printed statement that refrigerants are free of HCFCs.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Energy-Efficiency Ratio:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings."

C. Coefficient of Performance:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings."

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  R-407C and R-410A are HCFC-free refrigerants.  R-22 seems still seems to be the staple of the industry, but the number of products utilizing these new refrigerants is growing.  Insure the specified refrigerant allows competition between unit manufacturers.  Consider the following requirement carefully.
D. Units shall be designed to operate with HCFC-free refrigerants.

1.5 COORDINATION

A. Coordinate size and location of concrete bases for units.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

Retain paragraph below for units with remote-mounted air-cooled condensers.

B. Coordinate size, location, and connection details with roof curbs, equipment supports, and roof penetrations specified in Division 7 Section "Roof Accessories."
1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of self-contained air-conditioning units that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period:  [Five] <Insert other number> years from date of Substantial Completion.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise two subparagraphs below to suit Project.

1. Filters:  One set of filters for each unit.

2. Fan Belts:  One set of belts for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS
A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1.


1. Self-Contained Air-Conditioning Units:

a. Carrier Air Conditioning; Div. of Carrier Corporation.

b. Engineered Air.

c. McQuay International.

d. Trane Company (The); North American Commercial Group.

e. <Insert manufacturer's name.>

2.2 PACKAGED UNITS

A. Description:  Self-contained, factory-assembled and -wired unit; consisting of cabinet, compressor, evaporator fan, evaporator coil, air filters, and controls; and fully charged with refrigerant and oil.

1. Condenser:  [Integral water] [Remote air]-cooled condenser.

2. Performance efficiency for air-cooled units: 

a. Units 53 kW through 70 kW (180,000 through 240,000 Btuh): 9.5 EER

b. Units 70 kW through 222 kW (240,000 through 760,000 Btuh): 9.3 EER, 9.7 IPLV

c. Units greater than 222 kW (760,000 Btuh): 9.0 EER, 9.2 IPLV

3. Performance efficiency for water-cooled units: 

a. Units 53 kW through 70 kW (180,000 through 240,000 Btuh): 10.8 EER

b. Units greater than 70 kW (240,000 Btuh): 10.8 EER, 10.1 IPLV

B. Disconnect Switch:  Factory mounted [in control panel] [on equipment].

2.3 CABINET

A. Frame and Panels:  Structural-steel frame with galvanized-steel panels with baked-enamel finish in color selected by Architect, and with access doors or panels.

B. Insulation:  Minimum 25-mm- (1-inch-) thick, non-fibrous acoustic duct liner on cabinet interior and control panel.

C. Drain Pan:  Stainless steel.

D. Condensate Drain Pans:  Formed sections of Type 304 stainless steel sheet complying with requirements in ASHRAE 62.  Pans to extend minimum 305 mm (12 inches) past coil.  Fabricate pans with slopes in a minimum of two planes to collect condensate from cooling coils (including coil piping connections and return bends) and humidifiers when units are operating at maximum catalogued face velocity across cooling coil.

1. Double Wall Construction:  Fill space between walls with foam insulation and seal moisture tight.

2. Drain Connections:  Both ends of pan.

3. Units with stacked coils shall have an intermediate drain pan or drain trough to collect condensate from top coil.

4. Insulation:  Polystyrene or polyurethane insulation

5. Slope to drain

6. Traps at each drain.  Drain traps with depth and height differential between inlet and outlet equal or greater to the design static pressure plus 25.4 mm (1 inch w.g.)  Include slab height in trap calculation.

Paragraph below is optional.  Revise static deflection to suit Project.

E. Isolation:  Spring isolators for mounting under base of unit, with minimum static deflection of 25 mm (1 inch).

Two paragraphs below are optional accessories.

F. Discharge Plenum:  Cabinet extension with duct openings for air discharge and lined with a minimum of 50-mm- (2-inch-) thick non-fibrous duct liner.

G. Corrosion-Resistant Treatment:  Phenolic coating on unit interior and exterior.

2.4 EVAPORATOR FAN

A. Material:  Galvanized steel.

B. Configuration:  Double-width, double-inlet, [forward-curved] [airfoil] centrifugal fan; statically and dynamically balanced.

C. Drive:  Belt; with cast-iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed.

D. Motor Sheave:  Variable and adjustable pitch selected so required rpm are obtained when set at midposition.

E. Rating:  As recommended by the manufacturer or a minimum of one and one-half times nameplate rating of motor.

F. Bearings:  Grease lubricated with grease lines extended to exterior of unit.

Retain one of two optional paragraphs below for variable air volume.

G. Variable Air Volume:  Variable-frequency motor controller.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

H. Fan Motors:  Comply with requirements in Division 15 Section "Motors."

I. Motors:  [Open-dripproof] [Totally enclosed fan-cooled] type.

Retain subparagraph below for open-dripproof type where appropriate.

1. Special Motor Features:  Premium efficiency, as defined in Division 15 Section "Motors."

J. Isolation:  Mount fan and motor on common subbase and mount assembly on spring isolators with minimum static deflection of [25 mm (1 inch)] <Insert other static deflection>.

2.5 COMPRESSOR

A. Description:  Hermetically sealed, 3600 rpm maximum, and resiliently mounted with positive lubrication and internal motor protection.

B. Compressor Type:  [Reciprocating] [Scroll].

2.6 EVAPORATOR COIL

A. Direct-Expansion Coil:  Seamless copper tubes expanded into aluminum fins.

Subparagraph below is optional.

1. Corrosion-Resistant Treatment:  Phenolic coating applied with multiple dips and baked.

B. Refrigerant Circuits:  A separate circuit for each compressor, with externally equalized thermal-expansion valve with adjustable superheat, filter-dryer, sight glass, high-pressure relief valve, and charging valves.

Retain one of two condenser articles below.

2.7 WATER-COOLED CONDENSER

A. Description:  Copper tubes in steel shell with removable heads, for 2760-kPa (400-psig) waterside working pressure.

Subparagraphs below are optional.

1. ASME Compliance:  Fabricate and label water-cooled condensers to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, "Pressure Vessels," Division 1.

2. Water-Flow Switch:  Indicates flow.

2.8 REMOTE AIR-COOLED CONDENSER

A. Description:  Factory assembled and tested; consisting of condenser coil, fans and motors, and operating controls; suitable for roof mounting.

1. Condenser Coil:  Aluminum-fin copper tube with integral subcooler; leak tested to 3110 kPa (450 psig).

2. Condenser Fans:  Direct-drive propeller type.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add subparagraphs below to suit Project.

3. Fan Motors:  Three-phase, permanently lubricated, ball-bearing motors with built-in thermal-overload protection.  Comply with requirements in Division 15 Section "Motors."

4. Terminate suction and liquid refrigerant piping with service valves within unit.

Retain one of two subparagraphs below or delete both if not required.

5. Low Ambient Control:  Cycles fans to permit operation down to 7 deg C (45 deg F).

6. Low Ambient Control:  Cycles fans and modulates condenser fan damper assembly to permit operation down to minus 18 deg C (0 deg F).

Subparagraph below is an optional accessory.

7. Coil Guard:  Painted galvanized steel with louvered grilles.

2.9 REFRIGERATION SYSTEM

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  R-407C and R-410A are HCFC-free refrigerants.  R-22 seems still seems to be the staple of the industry, but the number of products utilizing these new refrigerants is growing.  Insure the specified refrigerant allows competition between unit manufacturers.  
A. Description:  Factory assembled and tested, and charged with[ HCFC-free] refrigerant; consisting of piping and accessories connecting compressor, evaporator coil, and condenser coil, and including the following:

First subparagraph below is required for heat pump units only.  Retain other appropriate components to suit Project.

1. Four-way reversing valve and suction-line accumulator.

2. Expansion valve with replaceable thermostatic element.

3. Refrigerant dryer.

4. High-pressure switch.

5. Low-pressure switch.

6. Thermostat for coil freeze-up protection during low-ambient temperature operation or loss of air.

7. Low-ambient switch.

8. Brass service valves installed in discharge and liquid lines.

2.10 HEATING COIL

Retain this Article if unit includes heating.  Retain and edit one of two paragraphs below.

A. [Water] [Steam] Coil:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm); leak tested to 300 psig (2070 kPa) underwater; and having a two-position control valve.

B. Electric Coil:  Helical, nickel-chrome, resistance-wire heating elements with refractory ceramic support bushings; automatic-reset thermal cutout; built-in magnetic contactors; manual-reset thermal cutout; airflow proving device; and one-time fuses in terminal box for overcurrent protection.
2.11 AIR FILTERS

Retain and edit desired filters in first two paragraphs below.  LEED Credit EQ 3.1 requires minimum MERV-13 filters.  Verify availability of MERV-13 filters with rooftop unit manufacturers.

A. Disposable Filters:  50-mm- (2-inch-) thick, glass-fiber, [flat] [pleated] panel filters.

B. Extended-Surface, Disposable Panel Filters:  [50-mm- (2-inch-)] [4-inch- (100-mm-)] thick,, dry, filters with fibrous media material formed into deep-V-shaped pleats and held by self-supporting wire grid holding frames, with nonflammable cardboard media and media-grid frame.

C. Air-Pressure Switch:  Indicates dirty filters.

2.12 CONTROLS

A. Factory-installed,[ native ASHRAE 135, BACnet][ LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.

B. Control equipment and sequence of operation are specified in Division 15 Sections "Building Automation System" and "Sequence of Operation."

Retain paragraph above and delete remainder of this Article if controls are part of overall temperature control system.

C. Control Package:  Factory wired, including contactor, high- and low-pressure cutouts, internal-winding thermostat for compressor, control-circuit transformer, and noncycling reset relay.

D. Time-Delay Relay:  Five-minute delay to prevent compressor cycling.

E. Adjustable Thermostat:  [Unit mounted] [Remote] to control the following:

1. Supply fan.

2. Compressor.

3. Condenser.

4. Hot-water coil valve.

F. System Selector Switch:  [Heat-off-cool] [Off-heat-auto-cool].

G. Fan Control Switch:  Auto-on.

Paragraph below is an optional accessory.

H. Time Clock:  Cycle unit on and off.

Retain one of two paragraphs and associated subparagraphs below.

I. Microprocessor Control Panel:  Controls unit functions, including refrigeration and safety controls, and the following:

Edit list below to suit unit configuration.

1. Supply fan.

2. Supply-fan motor speed.

3. Compressors.

4. Air-cooled condenser.

5. Cooling tower pump.

6. Modulating, hot-water coil valve.

7. Time-of-day control to cycle unit on and off.

8. Night-heat, morning warm-up cycle.

J. Microprocessor Control Panel:  Controls unit functions, including refrigeration and safety controls, and the following:

Edit list below to suit unit configuration.

1. Supply fan.

2. Supply-fan motor speed.

3. Economizer control.

4. Compressors.

5. Air-cooled condenser.

6. Cooling tower pump.

7. Modulating, hot-water coil valve.

8. Panel-mounted control switch to operate unit in remote or local control mode, or to stop or reset.

9. Panel-mounted indication of the following:

a. Operating status.

b. System diagnostics and safety alarms.

c. Supply-air temperature set point.

d. Zone heating-temperature set point.

e. Supply-air pressure set point.

f. Economizer minimum position set point.

g. Supply-air-pressure, high-limit set point.

LEED Credit EA 5 requires continuous metering equipment for monitoring building energy consumption performance over time.  Retain first five subparagraphs below if required to comply with the requirements for this credit.  Verify availability of control features with rooftop unit manufacturers.

h. Monitor constant and variable motor loads.

i. Monitor variable frequency drive operation.

j. Monitor economizer cycle.

k. Monitor cooling load.

l. Monitor air distribution static pressure and ventilation air volumes.

10. Time-of-day control to cycle unit on and off.

11. Night-heat, morning warm-up cycle.

2.13 ECONOMIZER OPTIONS

A. Air-Side Economizer:  Damper assembly allowing induction of up to 100 percent outside air to maintain a selected mixed-air temperature; and exhaust damper and spring-return, low-voltage, modulating damper motor with minimum position adjustment.

B. Water-Side Economizer : Mechanically cleanable, aluminum-fin, copper-tube coil assembly, [two] [four] rows deep, allowing precooling of inlet air using condenser water; with piping and bypass control valves.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb.

B. Anchor units to structure.

Retain paragraph below if Project is in a seismic area.

C. Install seismic restraints.

Retain first paragraph below for units equipped with inlet-vanes.

D. Install static-pressure probe.

E. Install water-cooled units with thermometer and pressure gage at the water supply and return connection.

Retain paragraph below if vibration isolators under the entire units will not be supplied by unit manufacturer.

F. Install vibration spring isolators under base of unit, with minimum static deflection of [25 mm (1 inch)] <Insert other static deflection>.  Refer to Division 15 Section "Mechanical Vibration Controls and Seismic Restraints."

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Retain subparagraph below for units with hot-water coils.

1. Water Coil Connections:  Comply with requirements in Division 15 Section "Hydronic Piping."  Connect to supply and return coil with shutoff-duty valve and union or flange on the supply connection and with throttling-duty valve and union or flange on the return connection.

Retain subparagraph below for units with remote water-cooled condenser.

2. Remote Water-Cooled Condenser Connections:  Comply with requirements in Division 15 Section "Hydronic Piping."  Connect to supply and return with shutoff-duty valve and union or flange on the supply connection and with throttling-duty valve and union or flange on the return connection.

Retain subparagraph below for units with steam coils.

3. Steam Coil Connections:  Comply with requirements in Division 15 Section "Steam and Condensate Piping."  Connect to steam piping with shutoff valve and union or flange; for condensate piping, starting from the coil connection, connect with union or flange, strainer, trap, and shutoff valve.

Retain first paragraph below for units with remote air-cooled condensers.

B. Refrigerant Piping:  Comply with applicable requirements in Division 15 Section "Refrigerant Piping."  Connect to supply and return coil tappings with shutoff valve and union or flange at each connection.

C. Install piping adjacent to unit to allow service and maintenance.

Retain first paragraph below for units connected to ducts.  Coordinate duct installation requirements with schematics on Drawings and with requirements specified for duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

D. Duct Connections:  Duct installation requirements are specified in Division 15 Section "Metal Ducts."  Drawings indicate the general arrangement of ducts.  Connect supply[ and return] ducts to self-contained air-conditioning units with flexible duct connectors.  Flexible duct connectors are specified in Division 15 Section "Duct Accessories."

E. Ground equipment according to Division 16 Section "Grounding and Bonding."

F. Electrical Connections:  Comply with requirements in Division 16 Sections for power wiring, switches, and motor controls.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.4 STARTUP SERVICE

Delete this Article if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. <Insert startup steps if any.>

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15737
SELF-CONTAINED AIR-CONDITIONING UNITS (LARGER THAN 15 TONS)
15737 - 1

