Copyright 2003 AIA
GSA VERSION MASTERSPEC
12/03 (GSA 03/05)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15752 - HUMIDIFIERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following humidifiers:

1. Water-Pressure Atomizing

2. Ultrasonic

3. Steam Injection

4. Self-contained.

5. Heated pan.

6. Heat exchanger.

1.3 DEFINITION

Retain definition that remains after this Section has been edited.

A. Low Voltage:  As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  Detail fabrication and installation of humidifiers.  Include piping details, plans, elevations, sections, details of components, manifolds, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Detail humidifiers and adjacent equipment.  Show support locations, type of support, weight on each support, required clearances, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Structural members to which humidifiers will be attached.

2. Size and location of initial access modules for acoustical tile.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For humidifiers to include in operation and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with ARI 640, "Commercial and Industrial Humidifiers."

1.6 EXTRA MATERIALS

Retain this Article for self-contained humidifiers with electrode cylinders.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Supply one replacement electrode cylinder with each self-contained humidifier.

1.7 COORDINATION

A. Coordinate location and installation of humidifiers with manifolds in ducts and air-handling units or occupied space.  Revise locations and elevations to suit field conditions and to ensure proper humidifier operation.

PART 2 -  PRODUCTS

2.1 WATER-PRESSURE ATOMIZING HUMIDIFIERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Carel USA, LLC.

2. Herrmidifier.

3. Mee Industries Inc.

4. <Insert manufacturer's name.>

B. Nozzles:  ASTM A 666, Type [304] [316] stainless steel.

C. Manifold:  ASTM A 269, Type [304] [316] stainless-steel piping.

Retain paragraph below if manifold discharges into air in a duct.

D. Droplet Filter:  Biocide-treated polyethylene with maximum 75-Pa (0.30-inch wg) resistance.

Makeup with mineral-free water to avoided calcium carbonate dust precipitate in the occupied space.  Stainless-steel piping is typically used with demineralized water.

E. Piping and Fittings:  ASTM A 269, Type [304] [316] stainless-steel pipe and fittings.

F. Water Pump:  Enclosed belt-drive ceramic plunger pump with [stainless-steel] [bronze] heads, and [single] [variable]-speed, totally enclosed, fan-cooled motor.

G. Final Water-Filter Efficiency:  Minimum [98] <Insert number> percent retention of suspended particles [10] [20] <Insert size> microns and larger from makeup water.

H. Final Water-Filter Pressure Drop:  Maximum [14 kPa (2 psig)] <Insert value> at design flow when clean[, and <Insert value> when dirty].

I. Pump Controls:

1. [Cycle] [Vary speed of] motor to satisfy humidistat.

2. High-pressure solenoid valve for each control zone shown on Drawings.

3. Building automation system interface for each control zone for start/stop and status indication and control at central workstation.

Retain first paragraph and subparagraphs below if humidifier discharges directly into occupied space.

J. Dispersion Fan:

1. Aluminum blade propeller fan with finger guard and single-speed motor interlocked to operate with humidifier.

2. Fan Mounting:  Above and behind manifold on bracket integral to wall-mounting manifold.

K. Accessories:

1. Humidistat:  [Wall] [Return-duct]-mounting, solid-state, electronic-sensor controller capable of full-modulation or cycling control.

2. Duct-mounting, high-limit humidistat.

3. Airflow switch for preventing humidifier operation without airflow.

If Project has more than one type or size of humidifier, delete paragraph and subparagraphs below and schedule humidifiers on Drawings.

L. Capacities and Characteristics:

1. Humidification Rate:  <Insert g/s (lb/h).>

2. Dry-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

3. Wet-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

4. Number of Nozzles:  <Insert number.>

5. Nozzle Spacing:  <Insert mm (inches).>

6. Maximum Absorption Distance:  <Insert mm (inches).>

7. Minimum Makeup Water Supply Pressure:  <Insert kPa (psig).>

8. Water Pump:

a. Discharge Pressure:  [6894 kPa (1000 psig)] [13 790 kPa (2000 psig)] <Insert pressure>.

b. Motor Horsepower:  <Insert horsepower.>

Retain first subparagraph and associated subparagraphs below if humidifier discharges directly into occupied space.

9. Dispersion Fan:

a. Airflow:  <Insert L/s (cfm).>

b. Motor Horsepower:  <Insert horsepower.>

10. Electrical Characteristics:  Single point of connection.

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.2 ULTRASONIC HUMIDIERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Stulz Air Technology Systems, Inc.

2. <Insert manufacturer's name.>

B. Description: Packaged, factory-assembled system of water-bed immersed piezoelectric transducers producing water vapor by high frequency oscillation.
C. Droplet diameter: 0.001 mm.

D. Mounting:[ Ductwork][ Rack in air-handling unit][ Stand-alone for[ wall][ floor][ shelf] mounting[ as indicated]].

E. Nozzles:  ASTM A 666, Type [304] [316] stainless steel.

F. Manifold:  ASTM A 269, Type [304] [316] stainless-steel piping.

G. Piping and Fittings:  ASTM A 269, Type [304] [316] stainless-steel pipe and fittings.

H. Inlet water demineralization: 

1. Process: Mixed cation/anion resin bed.

2. Water quality: 0.2 megaohm.

I. Accessories:

1. Humidistat:  [Wall] [Return-duct]-mounting, solid-state, electronic-sensor controller capable of full-modulation or cycling control.

2. Duct-mounting, high-limit humidistat.

3. Airflow switch for preventing humidifier operation without airflow.

4. Mounting racks for use in air-handling units.

5. Deionized water bottles.

6. Water bottle[ cabinet][ rack].

2.3 STEAM-INJECTION HUMIDIFIERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Armstrong International, Inc.

2. Carel USA, LLC.

3. DRI-STEEM Humidifier Company.

4. Herrmidifier.

5. Hygromatik; Spirax Sarco, Inc.

6. Nortec Industries Inc.

7. Pure Humidifier Company.

8. <Insert manufacturer's name.>

Retain one of first two paragraphs and associated subparagraphs below.  Retain first for duct-mounting or plenum-mounting humidifier, second if humidifier discharges directly into occupied space.

B. Manifold:  ASTM A 666, Type 304 stainless steel[, steam jacketed;] [; insulated with 13-mm (1/2-inch) fiberglass and stainless-steel jacket; and ]extending the full width of duct or plenum with mounting brackets at ends.

C. Discharge Nozzle and Dispersion Fan:

1. Steam-jacketed discharge nozzle, aluminum blade propeller fan with finger guard, and single-speed motor interlocked to operate with humidifier.

2. Fan Mounting:  Above and behind discharge outlet on bracket integral to discharge outlet.

D. Steam Separator:  [Cast iron] [ASTM A 666, Type 304 stainless steel] with [separate ]humidifier control valve.

E. Humidifier Control Valve:

Retain one of two subparagraphs below.

1. Actuator:  [Pneumatic] [Electric] modulating with spring return.

2. Actuator:  As specified in Division 15 Section "HVAC Instrumentation and Controls."

F. Steam Trap:  Inverted-bucket type, sized for a minimum of 3 times the maximum rated condensate flow of humidifier at 3.4-kPa (1/2-psig) inlet pressure.

G. Accessories:

Delete first two subparagraphs below if humidistats and aquastat are specified in Division 15 Section "HVAC Instrumentation and Controls."

1. [Wall] [Return-duct]-mounting humidistat.

2. Duct-mounting, high-limit humidistat.

3. Aquastat mounted on steam condensate return piping to prevent cold operation of humidifier.

4. In-line strainer.

5. Airflow switch for preventing humidifier operation without airflow.

If Project has more than one type or size of humidifier, delete paragraph and subparagraphs below and schedule humidifiers on Drawings.

H. Capacities and Characteristics:

1. Humidification Rate:  <Insert g/s (lb/h).>

2. Steam Supply Pressure:  <Insert kPa (psig).>

3. Dry-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

4. Wet-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

5. Maximum Absorption Distance:  <Insert mm (inches).>

Delete subparagraph below if humidifier discharges directly into occupied space.

6. Number of Manifolds:  <Insert number.>

Retain first subparagraph and associated subparagraphs below if humidifier discharges directly into occupied space.

7. Dispersion Fan:

a. Airflow:  <Insert L/s (cfm).>

b. Motor Horsepower:  <Insert horsepower.>

8. Electrical Characteristics:  Single point of connection.

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.4 SELF-CONTAINED HUMIDIFIERS

Electrode canisters must be replaced periodically.  Containment cylinders, and resistance cylinders must be clean periodically.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Armstrong International, Inc.

2. Carel USA, LLC.

3. Carnes Co., Inc.

4. Herrmidifier.

5. Hygromatik; Spirax Sarco, Inc.

6. Nortec Industries Inc.

7. <Insert manufacturer's name.>

Retain one of first three paragraphs and associated subparagraphs below.  Verify heater type and features with humidifier manufacturer.  Some heater features are proprietary.

B. Electric-Resistance Heater Container:  Cleanable, ASTM A 666, Type [304] [316] stainless steel.  Comply with UL 499.

Ionic bed inserts are a proprietary product of Armstrong.

C. Electrode Cylinder:  Replaceable plastic assembly[ with disposable ionic bed inserts].  Comply with UL 499.

Retain one of first two paragraphs below.  Retain first if humidifier discharges directly into occupied space.

D. Manifold:  Stainless-steel tube with integral fan to discharge vapor directly into occupied space.

E. Manifold:  ASTM A 666, Type [304] [316] stainless-steel tube extending across entire width of duct or plenum and equipped with mounting brackets on ends.

F. Cabinet:  Sheet metal enclosure for housing heater cylinder, electrical wiring, components, controls, and control panel.  Enclosure shall include baked-enamel finish, hinged or removable access door, and threaded outlet in bottom of cabinet for drain piping.

Ionic bed inserts are a proprietary product of Armstrong.

G. Control Panel:

1. Factory-wired disconnect switch.

2. Liquid-crystal display.

3. Programmable keyboard.

4. Set-point adjustment.

5. Warning signal indicating end of replaceable cylinder[ or ionic bed insert] life.

6. Low-voltage, control circuit.

7. Diagnostic, maintenance, alarm, and status features.

8. High-water [sensor] [float] to prevent overfilling.

H. Controls:

1. Microprocessor-based control system for modulating or cycling control, and start/stop and status monitoring for interface to central Building Automation System.

2. Solenoid-fill and automatic drain valves to maintain water level and temper hot drain water.

3. Field-adjustable timer to control drain cycle for flush duration and interval.

4. Controls shall drain tanks if no demand for humidification for more than 72 hours.

5. [Conductivity] [Float]-type level controls.

I. Accessories:

Delete first two subparagraphs below if humidistats are specified in Division 15 Section "Building Automation System."

1. Humidistat:  [Wall] [Return-duct]-mounting, solid-state, electronic-sensor controller capable of full modulation or cycling control.

2. Duct-mounting, high-limit humidistat.

3. Airflow switch for preventing humidifier operation without airflow.

If Project has more than one type or size of humidifier, delete paragraph and subparagraphs below and schedule humidifiers on Drawings.

J. Capacities and Characteristics:

1. Humidification Rate:  <Insert g/s (lb/h).>

2. Dry-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

3. Wet-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

4. Number of Manifolds:  <Insert number.>

5. Maximum Absorption Distance:  <Insert mm (inches).>

6. Minimum Makeup Water Supply Pressure:  <Insert kPa (psig).>

Retain subparagraph and associated subparagraphs below for electric-resistance or electrode-type heater.

7. Electric-Resistance Heater Container or Electrode Cylinder:

a. Power Input per Container or Cylinder:  <Insert kilowatts.>

b. Number of Containers or Cylinders:  <Insert number.>

Retain subparagraph and associated subparagraphs below for gas-fired generator.

8. Gas-Fired Generator:

a. Fuel Input:  <Insert kW (Btu/h).>

b. Fuel Pressure:  <Insert kPa (inches wg).>

Retain first subparagraph and associated subparagraphs below if humidifier discharges directly into occupied space.

9. Dispersion Fan:

a. Airflow:  <Insert L/s (cfm).>

b. Motor Horsepower:  <Insert horsepower.>

10. Electrical Characteristics:  Single point of connection.

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.5 HEATED-PAN HUMIDIFIERS

Install this type humidifier in air-handling unit casing or immediately adjacent to the duct.  Drain the evaporator pan when not in use to minimize biological growth.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Armstrong International, Inc.

2. DRI-STEEM Humidifier Company.

3. Nortec Industries Inc.

4. Pure Humidifier Company.

5. <Insert manufacturer's name.>

B. Heat Source:  [Hot water] [Steam] [Electric resistance].

Retain paragraph below for electric-resistance heat source.

C. Comply with UL 499.

Ionic bed inserts are a proprietary product of Armstrong.

D. Pan and Heat-Exchange Piping:  ASTM A 666, Type [304] [316] stainless steel with corrosion-resistant coating, overflow, and drain fittings.[ Include disposable ionic bed inserts.]

Retain one of first three paragraphs below for manifold in duct or plenum or for wall or ceiling mounting in occupied space.  If manifold is not required, delete all three paragraphs.

E. Manifold:  ASTM A 666, Type [304] [316] stainless-steel, duct-mounting, single- or manifold-grid connected to heated-pan housing with flexible hose and extending across width of duct or plenum.  Manifold shall have mounting brackets at both ends.

F. Manifold:  Inverted, ASTM A 666, Type [304] [316] stainless-steel U-tube with humidifier mounted directly under the duct.

G. Manifold:  ASTM A 666, Type [304] [316] stainless-steel tube with flexible hose to connect to humidifier, integral fan to discharge vapor directly into occupied space, and wall- or ceiling-mounting brackets.

H. Controls:

1. Solenoid-fill and automatic drain valves to maintain water level and temper hot drain water.

2. Field-adjustable timer to control drain cycle for flush duration and interval.

3. [Conductivity] [Float]-type level controls.

Retain paragraph below for steam heated-pan humidifier.

I. Piping Specialties:  Inlet strainer, control valve, and steam trap.

Retain first paragraph below for hot-water, heated-pan humidifier.

J. Piping Specialties:  Inlet strainer and control valve.

K. Accessories:

Delete first two subparagraphs below if humidistats are specified in Division 15 Section "Building Automation System."

1. Humidistat:  [Wall] [Return-duct]-mounting, solid-state, electronic-sensor controller capable of full modulation or cycling control.

2. Duct-mounting, high-limit humidistat.

3. Airflow switch for preventing humidifier operation without airflow.

If Project has more than one type or size of humidifier, delete paragraph and subparagraphs below and schedule humidifiers on Drawings.

L. Capacities and Characteristics:

1. Humidification Rate:  <Insert g/s (lb/h).>

2. Dry-Bulb Air Temperature at Pan or Discharge:  <Insert deg C (deg F).>

3. Wet-Bulb Air Temperature at Pan or Discharge:  <Insert deg C (deg F).>

4. Pan Length:  <Insert mm (inches).>

5. Pan Width:  <Insert mm (inches).>

6. Number of Manifolds:  <Insert number.>

7. Maximum Absorption Distance:  <Insert mm (inches).>

8. Minimum Makeup Water Supply Pressure:  <Insert kPa (psig).>

9. Hot Water:

a. Water Flow:  <Insert L/s (gpm).>

b. Pressure Loss Including Control Valve:  <Insert kPa (feet).>

c. Entering Temperature:  <Insert deg C (deg F).>

d. Leaving Temperature:  <Insert deg C (deg F).>

10. Steam:

a. Supply Pressure at Control Valve Inlet:  <Insert kPa (psig).>

b. Condensing Rate:  <Insert g/s (lb/h).>

Retain subparagraph and associated subparagraphs below for electric-resistance or electrode-type heater.

11. Electric-Resistance Heater Container or Electrode Cylinder:

a. Power Input:  <Insert kilowatts.>

b. Number of Steps:  <Insert number.>

Retain first subparagraph and associated subparagraphs below if humidifier discharges directly into occupied space.

12. Dispersion Fan:

a. Airflow:  <Insert L/s (cfm).>

b. Motor Horsepower:  <Insert horsepower.>

13. Electrical Characteristics:  Single point of connection.

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.6 HEAT-EXCHANGER HUMIDIFIERS

Consider this type of humidifier if steam is treated with condensate-return corrosion inhibitors.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Armstrong International, Inc.

2. Nortec Industries Inc.

3. Pure Humidifier Company.

4. <Insert manufacturer's name.>

B. Fabricate and label steam generator to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Ionic bed inserts are a proprietary product of Armstrong.

C. Heat Exchanger:  ASTM A 666, Type [304] [316] stainless steel with corrosion-resistant coating, overflow, and drain fittings.[ Include disposable ionic bed inserts.]

Retain one of first two paragraphs below.

D. Manifold:  ASTM A 666, Type [304] [316] stainless-steel[, steam-jacketed], duct-mounting, single- or manifold-grid connected to steam generator with flexible hose and extending across width of duct or plenum.  Manifold shall have mounting brackets for both ends.[ Insulate with 13-mm (1/2-inch) fiberglass and stainless-steel jacket extending full width of duct or plenum with mounting brackets at ends.]

E. Manifold:  ASTM A 666, Type [304] [316] stainless-steel tube with flexible hose to connect to humidifier and integral fan to discharge vapor directly into occupied space.  Manifold shall have wall- or ceiling-mounting brackets.

F. Controls:

1. Solenoid-fill and automatic drain valves to maintain water level and temper hot drain water.

2. Field-adjustable timer to control drain cycle for flush duration and interval.

3. [Conductivity] [Float]-type level controls.

G. Accessories:

Delete first two subparagraphs below if humidistats are specified in Division 15 Section "Building Automation System."

1. Humidistat:  [Wall] [Return-duct]-mounting, solid-state, electronic-sensor controller capable of full modulation.

2. Duct-mounting, high-limit humidistat.

3. Airflow switch for preventing humidifier operation without airflow.

If Project has more than one type or size of humidifier, delete paragraph and subparagraphs below and schedule humidifiers on Drawings.

H. Capacities and Characteristics:

1. Humidification Rate:  <Insert g/s (lb/h).>

2. Dry-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

3. Wet-Bulb Air Temperature at Discharge:  <Insert deg C (deg F).>

4. Manifold Steam Supply Pressure:  <Insert kPa (psig).>

5. Number of Manifolds:  <Insert number.>

6. Maximum Absorption Distance:  <Insert mm (inches).>

7. Minimum Makeup Water Supply Pressure:  <Insert kPa (psig).>

8. Steam:

a. Supply Pressure at Control Valve Inlet:  <Insert kPa (psig).>

b. Condensing Rate:  <Insert g/s (lb/h).>

Retain first subparagraph and associated subparagraphs below if humidifier discharges directly into occupied space.

9. Dispersion Fan:

a. Airflow:  <Insert L/s (cfm).>

b. Motor Horsepower:  <Insert horsepower.>

10. Electrical Characteristics:  Single point of connection.

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine ducts, air-handling units, and conditions for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in for piping systems to verify actual locations of piping connections before humidifier installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install humidifiers with required clearance for service and maintenance.

B. Seal humidifier manifold duct or plenum penetrations with flange.

C. Install humidifier manifolds in metal ducts and casings constructed according to SMACNA's "HVAC Duct Construction Standards, Metal and Flexible."

D. Install [galvanized] [stainless]-steel drain pan under each manifold mounted in duct.

1. Construct drain pans to comply with ASHRAE 62.

2. Connect to condensate trap and drainage piping.

3. Extend drain pan upstream and downstream from manifold a minimum of [600 mm (24 inches)] <Insert length> or as recommended by manufacturer.

Retain paragraph below for self-contained, heated-pan, and heat-exchanger humidifiers.

E. Install manifold supply piping pitched to drain condensate back to humidifier.

Retain paragraph below for steam-injection and heat-exchanger humidifiers.

F. Install drip leg upstream from steam trap a minimum of [300 mm (12 inches)] <Insert height> tall for proper operation of trap.

Retain first three paragraphs and associated subparagraphs below for gas-fired, self-contained or heat-exchanger humidifiers, or others that may be floor mounted.

G. Install steam generator level on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods."

H. Concrete Bases:  Anchor steam generator to concrete base.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 450-mm (18-inch) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Cast-in-place concrete materials and placement requirements are specified in Division 3.

Retain paragraph below if authorities having jurisdiction require seismic anchors and restraints.

I. Install seismic restraints on humidifiers.  Seismic restraints are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Retain paragraph below for gas-fired, self-contained humidifiers.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

1. Install piping adjacent to humidifiers to allow service and maintenance.

Retain subparagraph below for all humidifier types except steam injection.

2. Install shutoff valve, strainer, backflow preventer, and union in humidifier makeup line.

B. Install electrical devices and piping specialties furnished by manufacturer but not factory mounted.

Retain first four paragraphs below for gas-fired, self-contained humidifiers.

C. Install piping from safety relief valves to nearest floor drain.

D. Connect breeching full size to steam-generator outlet.  Venting materials are specified in Division 15 Section "Breechings, Chimneys, and Stacks."

E. Connect combustion-air inlet to intake terminal using PVC piping with solvent-cemented joints.  Run from boiler connection to outside and terminate adjacent to flue termination.

F. Ground equipment according to Division 16 Section "Grounding and Bonding."

G. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain one of first two paragraphs below.  Retain first paragraph to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by either of the entities in two paragraphs above.

C. Tests and Inspections:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

D. Remove and replace malfunctioning units and retest as specified above.

3.5 SIGNAGE

A. For heated pan humidifiers, provide[ vinyl][ metal] sign, installed on the equipment [or nearby wall] reading “Drain evaporator pan when not in use to minimize biological growth.”

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain humidifiers.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15752
HUMIDIFIERS
15752 - 1

