Copyright 2000 AIA
GSA VERSION MASTERSPEC(
9/00 (R09/01)(GSA 03/05)

Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15815 - METAL DUCTS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.
Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes metal ducts for supply, return, outside, and exhaust air-distribution systems in pressure classes from minus 500 to plus 2500 Pa (minus 2- to plus 10-inch wg).  Metal ducts include the following:

1. Single-wall, rectangular ducts and fittings.

2. Double-wall, rectangular ducts and fittings.

3. Single-wall, round[, and flat-oval] spiral-seam ducts and formed fittings.

4. Double-wall, round[, and flat-oval] spiral-seam ducts and formed fittings.

5. Duct between-wall insulation.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section, “Noise Control Devices”.

2. Division 15 Section "Duct Accessories" for dampers, sound-control devices, duct-mounting access doors and panels, turning vanes, and flexible ducts.

1.3 DEFINITIONS

Retain acronym and abbreviation that remain after this Section has been edited.

A. FRP:  Fiberglass-reinforced plastic.

B. NUSIG:  National Uniform Seismic Installation Guidelines.

C. Transverse Joints: Connections of two duct or fitting elements oriented perpendicular to air flow and include, but are not limited to, spin-ins, taps, and other branch connections, access doors frames, and duct connection to equipment.
1.4 SYSTEM DESCRIPTION

Retain this Article to convey basic design intent or delete if Drawings show enough detail to clarify intent.
A. Duct system design, as indicated, has been used to select size and type of air-moving and -distribution equipment and other air system components.  Changes to layout or configuration of duct system must be specifically approved in writing by Architect.  Accompany requests for layout modifications with calculations showing that proposed layout will provide original design results without increasing system total pressure.

1.5 SUBMITTALS

Detailed Shop Drawings are a cost factor for Contractor and require considerable time for review.  Require them only if Drawings do not show enough detail, or for complex areas.  List those areas.

A. Shop Drawings:  [CAD-generated and drawn] [Drawn] to [1:50 (1/4 inch equals 1 foot)] [1:100 (1/8 inch equals 1 foot)] <Insert scale> scale.  Show fabrication and installation details for metal ducts.

1. <Insert lists of areas or systems requiring Shop Drawings.>

2. Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

3. Duct layout indicating sizes and pressure classes.

4. Indicate single wall, double wall, and insulated duct sections.

5. Elevations of top and bottom of ducts.

6. Dimensions of main duct runs from building grid lines.

7. Fittings.

8. Reinforcement and spacing.

9. Seam and joint construction.

10. Penetrations through fire-rated and other partitions.

11. Equipment installation based on equipment being used on Project.

12. Duct accessories, including access doors and panels.

13. Hangers and supports, including methods for duct and building attachment, vibration isolation, and seismic restraints.

14. <Insert additional items.>

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

B. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Other systems installed in same space as ducts.

3. Ceiling- and wall-mounting access doors and panels required to provide access to dampers and other operating devices.

4. Ceiling-mounting items, including lighting fixtures, diffusers, grilles, speakers, sprinklers, access panels, and special moldings.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

D. Performance data on ducts and fittings.

E. Field quality-control test reports.

1.6 QUALITY ASSURANCE

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.  Welding is required for ducts connecting commercial kitchen hoods, some material-handling exhaust systems, and some high pressure classes.  Generally, this welding does not require certification.  Delete structural welding code references if welding of steel or aluminum plates and shapes is not required.

A. Welding:  Qualify procedures and personnel according to [AWS D1.1, "Structural Welding Code--Steel," for hangers and supports] [AWS D1.2, "Structural Welding Code--Aluminum," for aluminum supporting members] [and] [AWS D9.1, "Sheet Metal Welding Code," for duct joint and seam welding].

B. NFPA Compliance:

1. NFPA 90A, "Installation of Air Conditioning and Ventilating Systems."

2. NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

Retain paragraph below if range hood exhaust ducts are in Project.

C. Comply with NFPA 96, "Ventilation Control and Fire Protection of Commercial Cooking Operations," Ch. 3, "Duct System," for range hood ducts, unless otherwise indicated.

D. Fire-Test-Response Characteristics:  Sealants, coatings, and related materials shall have fire-test-response characteristics indicated, as determined by testing identical products per ASTM E 84, by a testing and inspecting agency acceptable to authorities having jurisdiction.  

Revise subparagraphs below to suit Project and products selected.

1. Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

Retain paragraph and subparagraphs below if required for pressure classes higher than 2-inch wg (500 Pa) or for special construction.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

E. Mockups:

1. Before installing duct systems, build mockups representing pressure classes higher than [500 Pa (2-inch wg)] <Insert pressure class>.  Build mockups to comply with the following requirements, using materials indicated for the completed Work, and include each of the following features and fittings:

a. [Five] <Insert number> transverse joints.

b. [One] <Insert number> access door(s).

c. [Two] <Insert number> typical branch connections, each with at least one elbow.

d. [Two] <Insert number> typical flexible duct or flexible connector connections for each duct and apparatus.

Retain subparagraph below if field quality-control testing is in the Contract.  See Part 3 "Field Quality Control" Article.

e. Perform tests specified in Part 3 "Field Quality Control" Article.  Modify mockup construction and perform additional tests as required to achieve specified minimum acceptable results.

Retain below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 1 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

2. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.
Most ductwork is constructed in fabrication shops and often assembled on-site.  Some manufactured products are available; listing these may increase quality control of Project.

2.2 SHEET METAL MATERIALS

See Evaluations for discussion on coatings.

A. Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods, unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

Anti-microbial coating is not suitable for outdoor installations.

First option within the antimicrobial option is for perforated inner wall; the second is for solid inner wall.
B. Galvanized Sheet Steel:  Lock-forming quality; complying with ASTM A 924/A 924M,  ASTM A 653/A 653M and having [Z180 (G60)] [Z275 (G90)] coating designation; ductwork shall have mill-phosphatized finish for surfaces exposed to view.  [Factory coated on [both sides of inner wall and inside of outer wall] [inside of inner wall] with minimum 0.2 mil epoxy containing AgIONTM  antimicrobial compound.]
C. ]PVC-Coated Galvanized Steel:  Lock-forming-quality, galvanized sheet steel complying with ASTM A 653M/A 653 and having [Z180 (G60)] coating designation.  Factory-applied PVC coatings shall be 0.10 mm (4 mils) thick on both sides of ductwork exposed to [corrosive conditions[] or ][underground installation]. 
D. Carbon-Steel Sheets:  ASTM A 366/A 366M, cold-rolled sheets; commercial quality; with oiled, matte finish for exposed ducts.

Anti-microbial coating is not suitable for outdoor installations.

First option within the antimicrobial option is for perforated inner wall; the second is for solid inner wall.

E. Stainless Steel:  ASTM 167, ASTM A 480/A 480M, Type [316] [304], and having a [No. 2D] finish for concealed ducts and [No. 4] <Insert finish designation> for exposed ducts.  [Factory coated on [both sides of inner wall and inside of outer wall] [inside of inner wall] with minimum 0.2 mil epoxy containing AgIONTM  antimicrobial compound.]

F. Aluminum Sheets:  ASTM B 209M (ASTM B 209), alloy 3003, temper H14; with mill finish for concealed ducts and standard, 1-side bright finish for exposed ducts.

See Evaluations for discussion on attachment of galvanized-steel hangers, specified in first paragraph below, to aluminum ducts.

G. Reinforcement Shapes and Plates:  Galvanized-steel reinforcement where installed on galvanized sheet metal ducts.

1. Tie Rods:  Galvanized steel, 6-mm (1/4-inch) minimum diameter for lengths 900 mm (36 inches) or less; 10-mm (3/8-inch) minimum diameter for lengths longer than 900 mm (36 inches).

2.3 SEALANT MATERIALS

A. Joint and Seam Sealants, General:  The term "sealant" is not limited to materials of adhesive or mastic nature but includes tapes and combinations of open-weave fabric strips and mastics.

Refer to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for a detailed discussion on seam and joint sealing methods and their applications.  First three two paragraphs below describe proprietary systems.  Edit to suit Project.

Retain the following for outdoor installations.

B. Water-Based Joint and Seam Sealant:  Flexible, adhesive sealant, resistant to UV light when cured, UL 723 listed, and complying with NFPA requirements for Class 1 ducts.

The following is needed for underground duct.

C. Solvent-Based Joint and Seam Sealant:  One-part, nonsag, solvent-release-curing, polymerized butyl sealant formulated with a minimum of 75 percent solids.

D. Flanged Joint Mastic:  One-part, acid-curing, silicone, elastomeric joint sealant complying with ASTM C 920, Type S, Grade NS, Class 25, Use O.

E. Flange Gaskets:  Butyl rubber or EPDM polymer with polyisobutylene plasticizer.

2.4 HANGERS AND SUPPORTS

Verify attachment selection and spacing with structural engineer.

A. Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 100 mm (4 inches) thick.

2. Exception:  Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 100 mm (4 inches) thick.

B. Hanger Materials:  Galvanized sheet steel or threaded steel rod.

1. Hangers Installed in Corrosive Atmospheres:  Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

2. Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for steel sheet width and thickness and for steel rod diameters.

3. Galvanized-steel straps attached to aluminum ducts shall have contact surfaces painted with zinc-chromate primer.

C. Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

D. Trapeze and Riser Supports:  Steel shapes complying with ASTM A 36/A 36M.

1. Supports for Galvanized-Steel Ducts:  Galvanized-steel shapes and plates.

2. Supports for Stainless-Steel Ducts:  Stainless-steel support materials.

3. Supports for Aluminum Ducts:  Aluminum support materials unless materials are electrolytically separated from ducts.

2.5 SINGLE WALL RECTANGULAR DUCT FABRICATION

A. Fabricate ducts, elbows, transitions, offsets, branch connections, and other construction according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" and complying with requirements for metal thickness, reinforcing types and intervals, tie-rod applications, and joint types and intervals.

1. Lengths:  Fabricate rectangular ducts in [standard nominal two-meter (six-foot)]lengths appropriate to reinforcement and rigidity class required for pressure class.  
2. Deflection:  Duct systems shall not exceed deflection limits according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."
3. Ship in L-shaped sections for field assembly.

B. Transverse Joints:  Prefabricated slide-on joints and components constructed using manufacturer's guidelines for material thickness, reinforcement size and spacing, and joint reinforcement.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ductmate Industries, Inc.

b. Nexus Inc.

c. Ward Industries, Inc.

d. <Insert manufacturer's name.>

C. Longitudinal Joints:  Button punch, snap-lock, or Pittsburgh-lock] seams.

D. Formed-On Flanges:  Construct according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," Figure 1-4, using corner, bolt, cleat, and gasket details.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ductmate Industries, Inc.

b. Lockformer.

c. Ward Industries, Inc.

d. <Insert manufacturer's name.>

Higher pressures can be specified when there are corner pieces (refer to SMACNA HVAC Duct Construction figure 1-15.

2. Duct Size:  Maximum 750 mm (30 inches) wide and up to 500-Pa (2-inch wg) pressure class without corner pieces.

3. Longitudinal Seams:  Pittsburgh lock sealed with noncuring polymer sealant.

E. Cross Breaking or Cross Beading:  Cross break or cross bead duct sides 480 mm (19 inches) and larger and 0.9 mm (0.0359 inch) thick or less, with more than 0.93 sq. m (10 sq. ft.) of nonbraced panel area unless ducts are lined.  Not required for ductwork with insulation covering [or acoustical liner].
2.6 DOUBLE WALL RECTANGULAR DUCT FABRICATION

A. Fabricate ducts, elbows, transitions, offsets, branch connections, and other construction according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" and complying with requirements for metal thickness, reinforcing types and intervals, tie-rod applications, and joint types and intervals.

1. Lengths:  Fabricate rectangular ducts in [standard nominal two-meter (six-foot)]lengths appropriate to reinforcement and rigidity class required for pressure class.  

2. Deflection:  Duct systems shall not exceed deflection limits according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

3. Ship in L-shaped sections for field assembly.

B. Transverse Joints:  Prefabricated slide-on joints and components constructed using manufacturer's guidelines for material thickness, reinforcement size and spacing, and joint reinforcement.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ductmate Industries, Inc.

b. Nexus Inc.

c. Ward Industries, Inc.

d. <Insert manufacturer's name.>

C. Longitudinal Joints:  Button punch, snap-lock, or Pittsburgh-lock] seams.

D. Formed-On Flanges:  Construct according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," Figure 1-4, using corner, bolt, cleat, and gasket details.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ductmate Industries, Inc.

b. Lockformer.

c. Ward Industries, Inc.

d. <Insert manufacturer's name.>

Higher pressures can be specified when there are corner pieces (refer to SMACNA HVAC Duct Construction figure 1-15.

2. Duct Size:  Maximum 750 mm (30 inches) wide and up to 500-Pa (2-inch wg) pressure class without corner pieces.

3. Longitudinal Seams:  Pittsburgh lock sealed with noncuring polymer sealant.

E. Cross Breaking or Cross Beading:  Cross break or cross bead duct sides 480 mm (19 inches) and larger and 0.9 mm (0.0359 inch) thick or less, with more than 0.93 sq. m (10 sq. ft.) of nonbraced panel area.  Not required for ductwork with insulation covering [or acoustical liner].

2.7 DUCT INSULATION

A. Polyimide Foam Insulation:  Pinned or mechanical fastened attached, 19 mm (3/4 inch) thick polyimide foam insulation complying with UL 181 erosion requirements, 

a. Thermal conductivity k Value:  0.35 at 75 deg F mean temperature.

b. Fire Hazard Classification:  Maximum flame spread index of 25 and smoke developed index of 50 when tested according to ASTM C 411.

c. Microbial growth not supported according to ASTM C 1071, ASTM G 21, and ASTM G 22.

B. Fibrous-Glass Insulation:  Comply with NFPA 90A or NFPA 90B and with NAIMA AH124.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. CertainTeed Corp.; Insulation Group.

b. Johns Manville International, Inc.

c. Knauf Fiber Glass GmbH.

d. Owens Corning.

e. <Insert manufacturer's name.>

2. Materials:  ASTM C 1071; surfaces exposed to airstream shall be coated to prevent erosion of glass fibers.

a. Thickness:  [13 mm (1/2 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)].

b. Thermal Conductivity (k-Value):  0.037 at 24 deg C (0.26 at 75 deg F) mean temperature.

c. Fire-Hazard Classification:  Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

d. Liner Adhesive:  Comply with NFPA 90A or NFPA 90B and with ASTM C 916.

e. Mechanical Fasteners:  Galvanized steel suitable for adhesive attachment, mechanical attachment, or welding attachment to duct without damaging liner when applied as recommended by manufacturer and without causing leakage in duct.

1) Tensile Strength:  Indefinitely sustain a 23-kg- (50-lb-) tensile, dead-load test perpendicular to duct wall.

2) Fastener Pin Length:  As required for thickness of insulation and without projecting more than 3 mm (1/8 inch) into airstream.

3) Adhesive for Attaching Mechanical Fasteners:  Comply with fire-hazard classification of duct liner system.

Flexible elastomeric duct liner is not suitable for temperatures higher than 220 deg F (104 deg C).

C. Flexible Elastomeric Duct Insulation:  Comply with NFPA 90A or NFPA 90B.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Armstrong World Industries, Inc.

b. <Insert manufacturer's name.>

2. Materials:  Unicellular polyethylene thermal plastic, preformed sheet insulation complying with ASTM C 534, Type II, except for density.

a. Thickness:  [9 mm (3/8 inch)] [13 mm (1/2 inch)] [19 mm (3/4 inch)] [25 mm (1 inch)].

b. Thermal Conductivity (k-Value):  0.034 at 24 deg C (0.24 at 75 deg F) mean temperature.

c. Fire-Hazard Classification:  Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM C 411.

2.8 APPLICATION OF INSULATION IN DUCTS

Delete paragraph below if air velocities do not exceed 2500 fpm (12.7 m/s).

A. Insulation Liner Adhesive:  As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

B. Terminate inner ducts with buildouts attached to fire-damper sleeves, dampers, turning vane assemblies, or other devices.  Fabricated buildouts (metal hat sections) or other buildout means are optional; when used, secure buildouts to duct walls with bolts, screws, rivets, or welds.

2.9 SINGLE-WALL ROUND AND FLAT-OVAL DUCT AND FITTING FABRICATION

A. Diameter as applied to flat-oval ducts in this Article is the diameter of a round duct with the same pressure loss per unit length at the same volume flow rate as the flat-oval duct.
B. Round, [Longitudinal] [Spiral Lock] [Longitudinal- and Spiral Lock]-Seam Ducts:  Fabricate supply ducts of galvanized steel according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

C. Flat-Oval, [Longitudinal] [Spiral Lock] [Longitudinal- and Spiral Lock]-Seam Ducts:  Fabricate supply ducts according to Chapter 3 SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."[ Fabricate ducts larger than 2100 mm (84 inches) in diameter with butt-welded longitudinal seams.]

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. McGill AirFlow LLC.

b. SEMCO Incorporated.

c. <Insert manufacturer's name.>

D. Duct Joints:

1. Ducts up to 900 mm (36 Inches) in Diameter:  Interior, center-beaded slip coupling, sealed before and after fastening, attached with sheet metal screws.

2. Ducts 950 to 1800 mm (38 to 72 Inches) in Diameter:  Three-piece, gasketed, flanged joint consisting of two internal flanges with sealant and one external closure band with gasket.

3. Ducts Larger Than 1800 mm (72 Inches) in Diameter:  Companion angle flanged joints per SMACNA "HVAC Duct Construction Standards--Metal and Flexible," Figure 3-2.

4. Round Ductwork:  Prefabricated connection system consisting of double-lipped, EPDM rubber gasket.  Manufacture ducts according to connection system manufacturer's tolerances.

a. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1) McGill Airflow LLC.
2) Lindab Inc.

3) SEMCO Incorporated.

4) <Insert manufacturer's name.>

5. Round and Flat-Oval Ducts:  Prefabricated connection system consisting of two flanges and one synthetic rubber gasket conforming to[ T-24][ T-24A] of SMACNA figure 1-4.
a. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1) Ductmate Industries, Inc.

2) McGill AirFlow LLC.

3) SEMCO Incorporated.

4) <Insert manufacturer's name.>

Fittings specified in the remainder of this Article are for pressure classes from minus 2- to plus 10-inch wg (minus 500 to plus 2500 Pa).

E. 90-Degree Laterals, Boots, and Conical Tees:  Fabricate to comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," with metal thicknesses specified for longitudinal-seam straight ducts.

F. Diverging- and Converging- Flow Fittings:  Fabricate with reduced entrance to branch taps and with no excess material projecting from fitting onto branch tap entrance.

SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" defines centerline bend radius based on air velocity in ducts.  

G. Fabricate elbows using die-formed, gored, pleated, standing seams, or mitered construction. Bend radius of shall be 1-1/2 times duct diameter.  Use mitered elbows only where air velocity is less than 10 m/s (2000 fpm).  Unless elbow construction type is indicated, fabricate elbows as follows:

1. Gored Elbow Radius and Number of Pieces:  Welded construction complying with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," unless otherwise indicated.

SMACNA requires that metal thickness of fittings be equal to or greater than that of ducts.  First two subparagraphs and associated subparagraphs below are extracted from manufacturer's catalog where metal thickness exceeds that of straight ducts.

2. Round Gored Elbows:  Welded construction with the following metal thickness for pressure classes from minus 500 to plus 500 Pa (minus 2- to plus 2-inch wg):

a. Ducts 75 to 915 mm (3 to 36 Inches) in Diameter:  0.85 mm (0.034 inch).

b. Ducts 940 to 1270 mm (37 to 50 Inches) in Diameter:  1.0 mm (0.040 inch).

c. Ducts 1320 to 1525 mm (52 to 60 Inches) in Diameter:  1.3 mm (0.052 inch).

d. Ducts 1575 to 2130 mm (62 to 84 Inches) in Diameter:  1.6 mm (0.064 inch).

3. Round Mitered Elbows:  Welded construction with the following metal thickness for pressure classes from 500 to 2500 Pa (2- to 10-inch wg):

a. Ducts 75 to 660 mm (3 to 26 Inches) in Diameter:  0.85 mm (0.034 inch).

b. Ducts 685 to 1270 mm (27 to 50 Inches) in Diameter:  1.0 mm (0.040 inch).

c. Ducts 1320 to 1525 mm (52 to 60 Inches) in Diameter:  1.3 mm (0.052 inch).

d. Ducts 1575 to 2130 mm (62 to 84 Inches) in Diameter:  1.6 mm (0.064 inch).

4. Flat-Oval Gored Elbows:  Welded construction with same metal thickness as longitudinal-seam flat-oval duct.

5. 90-Degree, 2-Piece, Mitered Elbows:  Use only for supply systems or for material-handling Class A or B exhaust systems and only where space restrictions do not permit using radius elbows.  Fabricate with [single-][double-]thickness turning vanes.

6. Round Elbows 300 mm (12 Inches) and Less in Diameter:  Fabricate die-formed elbows for 45- and 90-degree elbows and pleated elbows for 30, 45, 60, and 90 degrees only.  Fabricate nonstandard bend-angle configurations or nonstandard diameter elbows with gored construction.

7. Round Elbows 225 through 355 mm (9 through 14 Inches) in Diameter:  Fabricate gored or pleated elbows for 30, 45, 60, and 90 degrees unless space restrictions require mitered elbows.  Fabricate nonstandard bend-angle configurations or nonstandard diameter elbows with gored construction.  All Pressures 1.0 mm (0.040 inch) thick with 2-piece welded construction.
8. Round Elbows Larger Than 355 mm (14 Inches) in Diameter and All Flat-Oval Elbows:  Fabricate gored elbows unless space restrictions require mitered elbows.

9. Round Gored-Elbow Metal Thickness:  Same as non-elbow fittings specified above.

10. Flat-Oval Elbow Metal Thickness:  Same as longitudinal-seam flat-oval duct specified above.

11. Pleated Elbows for Sizes through 355 mm (14 Inches) in Diameter and Pressures through 2500 Pa (10-Inch wg):  0.55 mm (0.022 inch).

H. PVC-Coated Elbows and Fittings:  Fabricate elbows and fittings as follows:

1. Round Elbows 100 to 200 mm (4 to 8 Inches) in Diameter:  Two piece, die stamped, with longitudinal seams spot welded, bonded, and painted with PVC aerosol spray.

2. Round Elbows 225 to 660 mm (9 to 26 Inches) in Diameter:  Standing-seam construction.

3. Round Elbows 710 to 1525 mm (28 to 60 Inches) in Diameter:  Standard gored construction, riveted and bonded.

4. Other Fittings:  Riveted and bonded joints.

5. Couplings:  Slip-joint construction with a minimum 50-mm (2-inch) insertion length.

2.10 DOUBLE-WALL ROUND AND FLAT-OVAL DUCT AND FITTING FABRICATION

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Lindab Inc.

2. McGill AirFlow LLC.

3. SEMCO Incorporated.

4. <Insert manufacturer's name.>

B. Ducts:  Fabricate double-wall (insulated) ducts with an outer shell and an inner duct.  Dimensions indicated are for inner ducts.

1. Outer Shell:  Base metal thickness on outer-shell dimensions.  Fabricate outer-shell lengths 50 mm (2 inches) longer than inner duct and insulation and in metal thickness specified for single-wall duct.
Insulation below is also available in 2- and 3-inch (50- and 75-mm) thicknesses.

2. Insulation:  [25-mm- (1-inch-)] [50-mm- (2-inch-)][75-mm- (3-inch-)]thick fibrous glass, unless otherwise indicated.  Terminate insulation where double-wall duct connects to single-wall duct or uninsulated components, and reduce outer shell diameter to inner duct diameter.

a. Thermal Conductivity (k-Value):  0.037 at 24 deg C (0.26 at 75 deg F) mean temperature.

3. Solid Inner Ducts:  Use the following sheet metal thicknesses and seam construction:

a. Ducts 75 to 200 mm (3 to 8 Inches) in Diameter:  0.5 mm (0.019 inch) with standard spiral-seam construction.

b. Ducts 225 to 1070 mm (9 to 42 Inches) in Diameter:  0.5 mm (0.019 inch) with single-rib spiral-seam construction.

c. Ducts 1120 to 1525 mm (44 to 60 Inches) in Diameter:  0.55 mm (0.022 inch) with single-rib spiral-seam construction.

d. Ducts 1575 to 2235 mm (62 to 88 Inches) in Diameter:  0.85 mm (0.034 inch) with standard spiral-seam construction.

Retain either the subparagraph above or below.

4. Perforated Inner Ducts:  Fabricate with 0.028-inch-0.7-mm- thick sheet metal having 2.4-mm- (3/32-inch-) diameter perforations, with overall open area of 23 percent.

5. Maintain concentricity of inner duct to outer shell by mechanical means.  Prevent dislocation of insulation by mechanical means.

Fittings specified below are for pressure classes from minus 2- to plus 10-inch wg (minus 500 to plus 2500 Pa).

C. Fittings:  Fabricate double-wall (insulated) fittings with an outer shell and an inner duct.

1. Solid Inner Ducts:  Use the following sheet metal thicknesses:

a. Ducts 75 to 865 mm (3 to 34 Inches) in Diameter:  0.7 mm (0.028 inch).

b. Ducts 890 to 1475 mm (35 to 58 Inches) in Diameter:  0.85 mm (0.034 inch).

c. Ducts 1525 to 2235 mm (60 to 88 Inches) in Diameter:  1.0 mm (0.040 inch).

Retain either the subparagraph above or below.

2. Perforated Inner Ducts:  Fabricate with 0.7-mm- (0.028-inch-) thick sheet metal having 2.4-mm- (3/32-inch-) diameter perforations, with overall open area of 23 percent.

PART 3 -  EXECUTION

3.1 DUCT APPLICATIONS

A. Static-Pressure Classes:  Unless otherwise indicated, construct ducts according to the following:

Revise pressure classes in subparagraphs below to suit Project, or delete if pressure classes are indicated on Drawings.  If not indicated, contractors will assume a default pressure class of 1-inch wg (250 Pa) according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

1. Supply Ducts: [750 Pa (3-inch wg)]<Insert pressure class>.

Retain paragraph above or below.

2. Supply Ducts (before Air Terminal Units):  [750 Pa (3-inch wg)] [1500 Pa (6-inch wg)]<Insert pressure class>.

3. Supply Ducts (after VAV Air Terminal Units):  [250 Pa (1-inch wg)] <Insert pressure class>.

4. Supply Ducts (in Mechanical Equipment Rooms):  [750 Pa (3-inch wg)] <Insert pressure class>.

5. Return Ducts (Negative Pressure):   [250 Pa (1-inch wg)] <Insert pressure class>.

6. Exhaust Ducts (Negative Pressure):  [250 Pa (1-inch wg)] [500 Pa (2-inch wg)] <Insert pressure class>.

B. Notify the Architect if the following velocities are exceeded:

1. For Type I Kitchen Hoods: 8.5 m/s (2500 fpm)
2. For ducts equal to and less than 1000 Pa (4-inch wg): 10 m/s (2000 fpm)
3. For 1500 Pa (6-inch wg) ducts: 15 m/s (3000 fpm)
4. For 2500 Pa (10-inch wg) ducts: 20 m/s (4000 fpm)
C. All ducts shall be galvanized steel except as follows:

1. Type I Kitchen Hood Exhaust Ducts:  Comply with NFPA 96.

a. Concealed:  Carbon-steel sheet.  Minimum thickness: [1.4 mm (0.055-inch)]
b. Exposed:  Type 304, stainless steel with finish to match kitchen equipment and range hood.  Minimum thickness: [1.1 mm (0.044-inch)]
c. Weld and flange seams and joints.

Retain paragraph above or paragraph below.

2. Type I Kitchen Hood Exhaust Ducts:  Comply with NFPA 96.

a. Construction:  Double wall

b. Inner wall:  20 gage Type 304 stainless steel.

c. Exterior shell:  24 gage aluminized steel.

d. Space between walls: [ 25 mm (1 inch)]
e. Insulation: 

f. Weld and flange seams and joints.

3. Dishwasher Hood Exhaust Ducts:

a. Type 304, stainless steel with finish to match kitchen equipment and range hood.  Weld and flange seams and joints.

Select subparagraph above or first subparagraph below.

b. Aluminum, with seams and laps arranged on top of duct.

4. Shower Exhaust Ducts:

a. Type 304, stainless steel with finish to match kitchen equipment and range hood.  Weld and flange seams and joints.

Select subparagraph above or first subparagraph below.

b. Aluminum, with seams and laps arranged on top of duct.

5. Acid-Resistant (Fume-Handling) Ducts:  Type [316] [304], stainless-steel sheet with [No. 2B] [No. 4] [No. 3] <Insert finish> finish.

Select subparagraph above or first subparagraph below.

6. Acid-Resistant (Fume-Handling) Ducts:  PVC-coated galvanized steel with thicker coating on duct interior.

7. Underground Ducts:  [Concrete-encased galvanized steel] [PVC-coated galvanized steel with thicker coating on duct exterior and corrugated] [Concrete-encased PVC-coated galvanized steel with thicker coating on duct exterior and corrugated].

3.2 SEAM AND JOINT SEALING

A. Indoor Rectangular Ducts:

1. Supply Ducts: Seal transverse joints, longitudinal seams, and duct wall penetrations to include those by screws, non-self-sealing fasteners, pipes, tubing, rods, and wires.

2. Return and Exhaust Ducts: Seal transverse joints and longitudinal seams.

B. Outdoor Rectangular Ducts:

1. Seal transverse joints, longitudinal seams, and duct wall penetrations to include those by screws, non-self-sealing fasteners, pipes, rods, and wires.

C. Round and flat oval spiral lock: Coat after assembly.

D. Seal ducts before external insulation is applied.

3.3 DUCT INSTALLATION

Coordinate duct installation and accessory arrangement with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Construct and install ducts according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," unless otherwise indicated.

B. Test duct construction for leakage prior to installation.  Each test section must have a minimum of 6.17 m (20 foot) straight run, two elbows and a connection to the terminal.

C. Install round and flat-oval ducts in lengths not less than 3.7 m (12 feet) unless interrupted by fittings.

D. Install ducts with fewest possible joints.

E. Install fabricated fittings for changes in directions, size, and shape and for connections.

F. Install couplings tight to duct wall surface with a minimum of projections into duct.  Secure couplings with sheet metal screws.  Install screws at intervals of 300 mm (12 inches), with a minimum of 3 screws in each coupling.

G. Install ducts, unless otherwise indicated, vertically and horizontally and parallel and perpendicular to building lines; avoid diagonal runs.

H. Stiffen ducts at damper locations to achieve rigidity.

I. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

J. Install ducts with a clearance of 25 mm (1 inch), plus allowance for insulation thickness.

K. Conceal ducts from view in finished spaces.  Do not encase horizontal runs in solid partitions unless specifically indicated.

L. Coordinate layout with suspended ceiling, fire- and smoke-control dampers, lighting layouts, and similar finished work.

M. Seal all joints and seams.  Apply sealant to male end connectors before insertion, and afterward to cover entire joint and sheet metal screws.

N. Electrical Equipment Spaces:  Route ducts to avoid passing through transformer vaults and electrical equipment spaces and enclosures.

O. Non-Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls and are exposed to view, conceal spaces between construction openings and ducts or duct insulation with sheet metal flanges of same metal thickness as ducts.  Overlap openings on 4 sides by at least 38 mm (1-1/2 inches).

P. Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls, install appropriately rated fire dampers, sleeves, and firestopping sealant.  Fire and smoke dampers are specified in Division 15 Section "Duct Accessories."  Firestopping materials and installation methods are specified in Division 7 Section "Through-Penetration Firestop Systems."

Retain first paragraph below for projects in seismic areas.

Q. Install ducts with hangers and braces designed to withstand, without damage to equipment, seismic force required by applicable building codes.  Refer to [SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."] [NUSIG.]

R. Protect duct interiors from the elements and foreign materials until building is enclosed.  [Follow SMACNA's "Duct Cleanliness for New Construction."]

S. Paint interiors of metal ducts, that do not have duct liner, for 600 mm (24 inches) upstream of registers and grilles.  Apply one coat of flat, black, latex finish coat over a compatible galvanized-steel primer.  Paint materials and application requirements are specified in Division 9 painting Sections.

3.4 PVC-COATED DUCT, SPECIAL INSTALLATION REQUIREMENTS

A. Repair damage to PVC coating with manufacturer's recommended materials.

3.5 UNDERSLAB DUCTS, SPECIAL INSTALLATION REQUIREMENTS

A. Verify undamaged condition of ducts before enclosure with fill or encasement.

B. Protect ducts from damage by equipment used in placing fill materials and concrete on or around ducts.

C. Protect duct openings from damage and prevent entrance of foreign materials.

3.6 RANGE HOOD EXHAUST DUCTS, SPECIAL INSTALLATION REQUIREMENTS

A. Install ducts to allow for thermal expansion through 1110 deg C (2000 deg F) temperature range.

B. Install ducts without dips or traps that may collect residues unless traps have continuous or automatic residue removal.

C. Install access openings at each change in direction and at intervals defined by NFPA 96; locate on sides of duct a minimum of 38 mm (1-1/2 inches) from bottom; and fit with grease-tight covers of same material as duct.

D. Do not penetrate fire-rated assemblies except as permitted by applicable building codes.

3.7 HANGING AND SUPPORTING

A. Support horizontal ducts within 600 mm (24 inches) of each elbow and within 1200 mm (48 inches) of each branch intersection.

B. Support vertical ducts at maximum intervals of 5 m (16 feet) and at each floor.

C. Install upper attachments to structures with an allowable load not exceeding one-fourth of failure (proof-test) load.

Retain two paragraphs and associated subparagraph below for installations in concrete structures.

D. Install concrete inserts before placing concrete.

E. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

1. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 100 mm (4 inches) thick.

3.8 CONNECTIONS

Coordinate duct installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Make connections to equipment with flexible connectors according to Division 15 Section "Duct Accessories."

B. Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for branch, outlet and inlet, and terminal unit connections.

3.9 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections according to SMACNA's "HVAC Air Duct Leakage Test Manual" before insulation is applied and prepare test reports:

1. Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

2. Conduct tests at static pressures equal to maximum design pressure of system or section being tested.  If pressure classes are not indicated, test entire system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.  Give seven days' advance notice for testing.

3. Maximum Allowable Leakage:  Comply with requirements for Leakage Class 3 for round and flat-oval ducts, Leakage Class 12 for rectangular ducts in pressure classes lower than and equal to 500 Pa (2-inch wg) (both positive and negative pressures), and Leakage Class 6 for pressure classes from 500 to 2500 Pa (2- to 10-inch wg).

4. Remake leaking joints and retest until leakage is equal to or less than maximum allowable.

If adjusting and balancing of air-distribution systems are required, include Division 15 Section "Testing, Adjusting, and Balancing."

3.10 CLEANING NEW SYSTEMS

A. Mark position of dampers and air-directional mechanical devices before cleaning, and perform cleaning before air balancing.

B. Use service openings, as required, for physical and mechanical entry and for inspection.

1. Create other openings to comply with duct standards.

2. Disconnect flexible ducts as needed for cleaning and inspection.

3. Remove and reinstall ceiling sections to gain access during the cleaning process.

C. Vent vacuuming system to the outside.  Include filtration to contain debris removed from HVAC systems, and locate exhaust down wind and away from air intakes and other points of entry into building.

D. Clean the following metal duct systems by removing surface contaminants and deposits:

1. Air outlets and inlets (registers, grilles, and diffusers).

2. Supply, return, and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

3. Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

4. Coils and related components.

5. Return-air ducts, dampers, and actuators except in ceiling plenums and mechanical equipment rooms.

6. Supply-air ducts, dampers, actuators, and turning vanes.

E. Mechanical Cleaning Methodology:

1. Clean metal duct systems using mechanical cleaning methods that extract contaminants from within duct systems and remove contaminants from building.

2. Use vacuum-collection devices that are operated continuously during cleaning.  Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

3. Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of metal ducts, duct liner insulation, or duct accessories.

4. Clean coils and coil drain pans according to NADCA 1992.  Keep drain pan operational.  Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

F. Cleanliness Verification:

1. Visually inspect metal ducts for contaminants.

2. Where contaminants are discovered, re-clean and reinspect ducts.

3.11 CLEANING EXISTING SYSTEMS

A. Use service openings, as required, for physical and mechanical entry and for inspection.

1. Use existing service openings where possible.

2. Create other openings to comply with duct standards.

3. Disconnect flexible ducts as needed for cleaning and inspection.

4. Reseal rigid fiberglass duct systems according to NAIMA recommended practices.

5. Remove and reinstall ceiling sections to gain access during the cleaning process.

B. Mark position of dampers and air-directional mechanical devices before cleaning, and restore to their marked position on completion.

C. Particulate Collection and Odor Control:

1. When venting vacuuming system inside the building, use HEPA filtration with 99.97 percent collection efficiency for 0.3-micron size (or larger) particles.

2. When venting vacuuming system to the outside, use filtration to contain debris removed from HVAC system, and locate exhaust down wind and away from air intakes and other points of entry into building.

D. Clean the following metal duct systems by removing surface contaminants and deposits:

1. Air outlets and inlets (registers, grilles, and diffusers).

2. Supply, return, and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

3. Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

4. Coils and related components.

5. Return-air ducts, dampers, and actuators except in ceiling plenums and mechanical equipment rooms.

6. Supply-air ducts, dampers, actuators, and turning vanes.

7. Dedicated exhaust and ventilation components and makeup air systems.

E. Mechanical Cleaning Methodology:

1. Clean metal duct systems using mechanical cleaning methods that extract contaminants from within duct systems and remove contaminants from building.

2. Use vacuum-collection devices that are operated continuously during cleaning.  Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

3. Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of metal ducts, duct liner insulation, or duct accessories.

4. Clean coils and coil drain pans according to NADCA 1992.  Keep drain pan operational.  Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

5. Provide operative drainage system for washdown procedures.

6. Biocidal Agents and Coatings:  Apply biocidal agents if fungus is present.  Apply biocidal agents according to manufacturer's written instructions after removal of surface deposits and debris.

F. Cleanliness Verification:

1. Verify cleanliness after mechanical cleaning and before application of treatment, including biocidal agents and protective coatings.

2. Visually inspect metal ducts for contaminants.

3. Where contaminants are discovered, re-clean and reinspect ducts.

Retain first paragraph and subparagraphs below if required for Project.

G. Gravimetric Analysis:  At discretion and expense of Owner, sections of metal duct system, chosen randomly by Owner, may be tested for cleanliness according to NADCA vacuum test gravimetric analysis.

1. If analysis determines that levels of debris are equal to or lower than suitable levels, system shall have passed cleanliness verification.

2. If analysis determines that levels of debris exceed suitable levels, system cleanliness verification will have failed and metal duct system shall be re-cleaned and re-verified.

H. Verification of Coil Cleaning:  Cleaning must restore coil pressure drop to within 10 percent of pressure drop measured when coil was first installed.  If original pressure drop is not known, coil will be considered clean only if it is free of foreign matter and chemical residue, based on thorough visual inspection.

END OF SECTION 15815

METAL DUCTS
15815 - 9

