Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

SECTION 07620 – SHEET METAL FLASHING AND TRIM
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

1. Formed wall flashing and trim.

1.2 SUBMITTALS
A. Product Data:  For each product indicated.

B. Shop Drawings:  Show layouts, profiles, shapes, seams, dimensions, and details for fastening, joining, supporting, and anchoring sheet metal flashing and trim.

Below assumes manufacturer's standard-size Samples are acceptable.  Revise to suit Project.

C. Samples:  For each type of sheet metal flashing and trim.

1.3 QUALITY ASSURANCE

A. Sheet Metal Flashing and Trim Standard:  Comply with SMACNA's "Architectural Sheet Metal Manual." Conform to dimensions and profiles shown unless more stringent requirements are indicated.

PART 2 -  PRODUCTS
2.1 SHEET METALS

A. Stainless-Steel Sheet:  ASTM A 240/A 240M, Type 304, No.  2B finish, or

B. Zinc Sheet:  Electrolytic, 99 percent pure zinc alloyed with 1 percent titanium and copper.

1. Finish:  Preweathered.

2.2 MISCELLANEOUS MATERIALS

A. General:  Provide materials and types of fasteners, solder, welding rods, protective coatings, separators, sealants, and other miscellaneous items as required for complete sheet metal flashing and trim installation.

B. Felt Underlayment:  ASTM D 226, Type II (No. 30), asphalt-saturated organic felt, nonperforated.

1. Slip Sheet:  Rosin-sized paper, minimum 3 lb/100 sq. ft. (0.16 kg/sq. m).

C. Fasteners:  Wood screws, annular threaded nails, self-tapping screws, self-locking rivets and bolts, and other suitable fasteners designed to withstand design loads.

Retain subparagraphs below to suit Project.

1. Fasteners for Flashing and Trim:  Blind fasteners or self-drilling screws, gasketed, with hex washer head.

D. Solder for Stainless Steel:  ASTM B 32, Grade Sn60, with acid flux of type recommended by stainless-steel sheet manufacturer.

E. Solder for Zinc:  ASTM B 32, 60 percent lead and 40 percent tin with low antimony, as recommended by manufacturer.

F. Sealing Tape:  Pressure-sensitive, 100 percent solids, polyisobutylene compound sealing tape with release-paper backing.  Provide permanently elastic, nonsag, nontoxic, nonstaining tape.

G. Elastomeric Sealant:  ASTM C 920, elastomeric polyurethane, polysulfide, or silicone polymer sealant; of type, grade, class, and use classifications required to seal joints in sheet metal flashing and trim and remain watertight.

H. Bituminous Coating:  Cold-applied asphalt mastic, SSPC-Paint 12, compounded for 15-mil (0.4-mm) dry film thickness per coat.

2.3 REGLETS

A. Reglets:  Units of type, material, and profile required, formed to provide secure interlocking of separate reglet and counterflashing pieces, and compatible with flashing with factory- mitered and -welded corners and junctions.
Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Material:  Stainless steel, 0.0187 inch (0.5 mm) thick, or zinc, 0.040 inch (1.0 mm)
2.4 FABRICATION, GENERAL

A. General:  Custom fabricate sheet metal flashing and trim to comply with recommendations in SMACNA's "Architectural Sheet Metal Manual" that apply to design, dimensions, metal, and other characteristics of item indicated.  Shop fabricate items where practicable.  Obtain field measurements for accurate fit before shop fabrication.

B. Fabricate sheet metal flashing and trim without excessive oil canning, buckling, and tool marks and true to line and levels indicated, with exposed edges folded back to form hems.

1. Seams for Other Than Aluminum:  Fabricate nonmoving seams in accessories with flat-lock seams.  Tin edges to be seamed, form seams, and solder.

C. Sealed Joints:  Form nonexpansion but movable joints in metal to accommodate elastomeric sealant to comply with SMACNA recommendations.

D. Expansion Provisions:  Where lapped or bayonet-type expansion provisions in the Work cannot be used, form expansion joints of intermeshing hooked flanges, not less than 1 inch (25 mm) deep, filled with elastomeric sealant concealed within joints.

E. Conceal fasteners and expansion provisions where possible on exposed-to-view sheet metal flashing and trim, unless otherwise indicated.

F. Fabricate cleats and attachment devices from same material as accessory being anchored or from compatible, noncorrosive metal, and in thickness not less than that of metal being secured.

2.5 WALL SHEET METAL FABRICATIONS

A. Through-Wall Flashing:  Fabricate continuous flashings in minimum 96-inch- (2400-mm-) long, but not exceeding 12 foot (3.6 m) long, sections, under copings, at shelf angles, and where indicated.  Fabricate discontinuous lintel, sill, and similar flashings to extend 6 inches (150 mm) beyond each side of wall openings.  Form with 2-inch- (50-mm-) high end dams.  Fabricate from the following material:

1. Stainless Steel:  0.0156 inch (0.4 mm) thick, or
2. Zinc:  0.031 inch (0.80 mm) thick.

PART 3 -  EXECUTION
3.1 INSTALLATION, GENERAL

A. General:  Anchor sheet metal flashing and trim and other components of the Work securely in place, with provisions for thermal and structural movement.  Use fasteners, solder, welding rods, protective coatings, separators, sealants, and other miscellaneous items as required to complete sheet metal flashing and trim system.

1. Torch cutting of sheet metal flashing and trim is not permitted.

B. Metal Protection:  Where dissimilar metals will contact each other or corrosive substrates, protect against galvanic action by painting contact surfaces with bituminous coating or by other permanent separation as recommended by fabricator or manufacturers of dissimilar metals.

C. Install exposed sheet metal flashing and trim without excessive oil canning, buckling, and tool marks.

D. Install sheet metal flashing and trim true to line and levels indicated.  Provide uniform, neat seams with minimum exposure of solder, welds, and elastomeric sealant.

E. Install sheet metal flashing and trim to fit substrates and to result in watertight performance.  Verify shapes and dimensions of surfaces to be covered before fabricating sheet metal.

1. Space cleats not more than 12 inches (300 mm) apart.  Anchor each cleat with two fasteners. Bend tabs over fasteners.

F. Expansion Provisions:  Provide for thermal expansion of exposed flashing and trim.  Space movement joints at a maximum of 10 feet (3 m) with no joints allowed within 24 inches (600 mm) of corner or intersection.  Where lapped or bayonet-type expansion provisions cannot be used or would not be sufficiently watertight, form expansion joints of intermeshing hooked flanges, not less than 1 inch (25 mm) deep, filled with elastomeric sealant concealed within joints.

G. Fasteners:  Use fasteners of sizes that will penetrate substrate not less than 1-1/4 inches (32 mm) for nails and not less than 3/4 inch (19 mm) for wood screws.

1. Zinc:  Use stainless-steel fasteners.

H. Seal joints with elastomeric sealant as required for watertight construction.

I. Soldered Joints:  Clean surfaces to be soldered, removing oils and foreign matter.  Pretin edges of sheets to be soldered to a width of 1-1/2 inches (38 mm) except where pretinned surface would show in finished Work.

Delete metals in two subparagraphs below that are not specified in Part 2.

1. Do not solder prepainted, metallic-coated steel sheet.

3.2 WALL FLASHING INSTALLATION

A. General:  Install sheet metal wall flashing to intercept and exclude penetrating moisture according to SMACNA recommendations and as indicated.  Coordinate installation of wall flashing with installation of wall-opening components such as windows, doors, and louvers.

B. Reglets:  Installation of reglets is specified in Division 04 Section "Unit Masonry Assemblies."

END OF SECTION 07620

SHEET METAL FLASHING AND TRIM

07620 - 4

