Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 09111 – NON-LOAD-BEARING STEEL FRAMING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Non-load-bearing steel framing members for the following applications:

a. Interior framing systems (e.g., supports for partition walls, framed soffits, furring, etc.).

b. Interior suspension systems (e.g., supports for ceilings, suspended soffits, etc.).

1.2 SUBMITTALS

A. Product Data:  For each type of product indicated.

1.3 QUALITY ASSURANCE

A. Fire-Test-Response Characteristics:  For fire-resistance-rated assemblies that incorporate non-load-bearing steel framing, provide materials and construction identical to those tested in assembly indicated according to ASTM E 119 by an independent testing agency.

Retain paragraph below where framing is part of STC-rated assemblies.  Indicate design designations of specific assemblies on Drawings.

B. Sound Transmission Characteristics:  For STC-rated assemblies that incorporate non-load-bearing steel framing, provide materials and construction identical to those tested in assembly indicated according to ASTM E 90 and classified according to ASTM E 413 by an independent testing agency.

PART 2 -  PRODUCTS

2.1 NON-LOAD-BEARING STEEL FRAMING, GENERAL

A. Framing Members, General:  Comply with ASTM C 754 for conditions indicated.

1. Steel Sheet Components:  Comply with ASTM C 645 requirements for metal, unless otherwise indicated.

See "Corrosion Protection of Steel Framing" Article in the Evaluations for a discussion of corrosion-resistant coatings on components.

2. Protective Coating:  ASTM A 653/A 653M, G60 (Z180), hot-dip galvanized  zinc coating, unless otherwise indicated.

2.2 SUSPENSION SYSTEM COMPONENTS

Delete this Article if no suspended or furred ceilings or soffits.

A. Tie Wire:  ASTM A 641/A 641M, Class 1 zinc coating, soft temper, 0.0625-inch- (1.59-mm-) diameter wire, or double strand of 0.0475-inch- (1.21-mm-) diameter wire.

B. Hanger Attachments to Concrete:

Retain anchors or powder-actuated fasteners below for hanger attachment to concrete decks.  Coordinate with hangers specified and verify safety factors with Project's structural engineer.

1. Anchors:  Fabricated from corrosion-resistant materials with holes or loops for attaching wire hangers and capable of sustaining, without failure, a load equal to 5 times that imposed by construction as determined by testing according to ASTM E 488 by an independent testing agency.

a. Type:  Cast-in-place anchor, designed for attachment to concrete forms or Postinstalled, chemical anchor.

2. Powder-Actuated Fasteners:  Suitable for application indicated, fabricated from corrosion-resistant materials with clips or other devices for attaching hangers of type indicated, and capable of sustaining, without failure, a load equal to 10 times that imposed by construction as determined by testing according to ASTM E 1190 by an independent testing agency.

C. Wire Hangers:  ASTM A 641/A 641M, Class 1 zinc coating, soft temper, 0.162-inch (4.12-mm) diameter.

Retain hanger paragraph above or below, or insert requirements to suit Project.  Verify requirements of authorities having jurisdiction.  If more than one type of hanger is required, indicate locations of each on Drawings.

D. Carrying Channels:  Cold-rolled, commercial-steel sheet with a base-metal thickness of 0.0538 inch (1.37 mm) and minimum 1/2-inch- (12.7-mm-) wide flanges.

1. Depth:  2-1/2 inches (64 mm) .

E. Furring Channels (Furring Members):

Retain one of four furring channel subparagraphs and associated subparagraphs below or, if more than one is required, indicate locations of each on Drawings.

1. Hat-Shaped, Rigid Furring Channels:  ASTM C 645, 7/8 inch (22.2 mm) deep.

a. Minimum Base Metal Thickness:  0.0312 inch (0.79 mm).

2. Resilient Furring Channels:  1/2-inch- (12.7-mm-) deep members designed to reduce sound transmission.

a. Configuration:  Asymmetrical or hat shaped.

Grid suspension systems are suitable for use with gypsum board.  They might not be acceptable for gypsum veneer plaster; consult gypsum veneer plaster and grid suspension system manufacturers before specifying them.

F. Grid Suspension System for Ceilings:  ASTM C 645, direct-hung system composed of main beams and cross-furring members that interlock.

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  If naming products, retain subparagraph above for nonproprietary or first subparagraph below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

a. Armstrong World Industries, Inc.; Drywall Grid Systems.

b. Chicago Metallic Corporation; Drywall Furring System.

c. USG Corporation; Drywall Suspension System.

2.3 STEEL FRAMING FOR FRAMED ASSEMBLIES

A. Steel Studs and Runners:  ASTM C 645.

GA-600 recommends 0.0312-inch- (0.79-mm-) thick studs at fire-door frames supporting standard and heavyweight doors, but it includes an alternate detail for nested 0.0179-inch (0.45-mm) studs for standard-weight doors.

For framing supporting ceramic tile substrates, 0.0312-inch- (0.79-mm-) thick studs are generally recommended.

If runners must have a heavier base-metal thickness than studs, revise subparagraph below.

1. Minimum Base-Metal Thickness:  0.0312 inch (0.79 mm).

For slip joint at stud and top-track interface (head joint) that avoids axial loading of partition by overhead structure, retain paragraph and one or all of the following types of head joints.  See "Crack Control" Article in the Evaluations.

B. Slip-Type Head Joints:  Where indicated, provide one of the following:

If retaining single-track systems below, indicate type of bridging required on Drawings or by inserts.  Strap and 1-1/2-inch (38.1-mm) cold-rolled channel are commonly used.

1. Single Long-Leg Runner System:  ASTM C 645 top runner with 2-inch- (50.8-mm-) deep flanges in thickness not less than indicated for studs, installed with studs friction fit into top runner and with continuous bridging located within 12 inches (305 mm) of the top of studs to provide lateral bracing.

If retaining double-runner system below and if deflection might be great, evaluate the lateral stability of outer-runner flanges and consider using steel channels for tracks instead of nonstructural runners.

2. Double-Runner System:  ASTM C 645 top runners, inside runner with 2-inch- (50.8-mm-) deep flanges in thickness not less than indicated for studs and fastened to studs, and outer runner sized to friction fit inside runner.

3. Deflection Track:  Steel sheet top runner manufactured to prevent cracking of finishes applied to interior partition framing resulting from deflection of structure above; in thickness not less than indicated for studs and in width to accommodate depth of studs.

a. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

If naming products, retain last subparagraph above for nonproprietary or first subparagraph below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

1) Steel Network Inc. (The); VertiClip SLD or VertiTrack VTD Series.

2) Superior Metal Trim; Superior Flex Track System (SFT).

Firestop tracks are proprietary top tracks for isolating partition framing from structure above in specific fire-resistance-rated assemblies.  If retaining paragraph below, coordinate with Division 07 Section "Fire-Resistive Joint Systems" and indicate design designations of joint assemblies on Drawings or in Specifications.

C. Firestop Track:  As specified in Division 07 Section "Fire-Resistive Joint Systems."

Retain paragraph and subparagraph below for flat-strap blocking and bracing for fixture attachment.  Indicate locations, lengths, and widths on Drawings.

D. Flat Strap and Backing Plate:  Steel sheet for blocking and bracing in length and width indicated.

1. Minimum Base-Metal Thickness:  0.0312 inch (0.79 mm).

Retain first paragraph and subparagraphs below for channel bridging for fixture attachment or lateral bracing.  Indicate locations and details of installation on Drawings.

E. Cold-Rolled Channel Bridging:  0.0538-inch (1.37-mm) bare-steel thickness, with minimum 1/2-inch- (12.7-mm-) wide flanges.

1. Depth:  1-1/2 inches (38.1 mm).

2. Clip Angle:  Not less than 1-1/2 by 1-1/2 inches (38.1 by 38.1 mm), 0.068-inch- (1.73-mm-) thick, galvanized steel.

F. Hat-Shaped, Rigid Furring Channels:  ASTM C 645.

1. Minimum Base Metal Thickness:  0.0179 inch (0.45 mm) .

2. Depth:  As indicated on Drawings .

G. Resilient Furring Channels:  1/2-inch- (12.7-mm-) deep, steel sheet members designed to reduce sound transmission.

1. Configuration:  Asymmetrical or hat shaped .

H. Cold-Rolled Furring Channels:  0.0538-inch (1.37-mm) bare-steel thickness, with minimum 1/2-inch- (12.7-mm-) wide flanges.

1. Depth:  As indicated on Drawings .

2. Furring Brackets:  Adjustable, corrugated-edge type of steel sheet with minimum bare-steel thickness of 0.0312 inch (0.79 mm).

3. Tie Wire:  ASTM A 641/A 641M, Class 1 zinc coating, soft temper, 0.0625-inch- (1.59-mm-) diameter wire, or double strand of 0.0475-inch- (1.21-mm-) diameter wire.

Z-shaped furring is available in 1-, 1-1/2-, 2-, 2-1/2-, and 3-inch (25.4-, 38.1-, 50.8-, 63.5-, and 76.2-mm) depths.  Coordinate Z-shaped furring requirements with insulation specified in Division 07 Section "Thermal Insulation."

2.4 AUXILIARY MATERIALS

A. Fasteners for Metal Framing:  Of type, material, size, corrosion resistance, holding power, and other properties required to fasten steel members to substrates.

B. Isolation Strip at Exterior Walls:  Provide the following:

Retain both subparagraphs below and option in paragraph above to allow Contractor to choose type of isolation strip.

1. Foam Gasket:  Adhesive-backed, closed-cell vinyl foam strips that allow fastener penetration without foam displacement, 1/8 inch (3.2 mm) thick, in width to suit steel stud size.

PART 3 -  EXECUTION

3.1 INSTALLATION, GENERAL

A. Installation Standard:  ASTM C 754.

Standards listed in four subparagraphs below include framing installation requirements not in ASTM C 754.  Retain applicable subparagraphs to suit Project.

1. Gypsum Board Assemblies:  Also comply with requirements in ASTM C 840 that apply to framing installation.

3.2 INSTALLING SUSPENSION SYSTEMS

A. Isolate suspension systems from building structure where they abut or are penetrated by building structure to prevent transfer of loading imposed by structural movement.

B. Suspend hangers from building structure as follows:

1. Install hangers plumb and free from contact with insulation or other objects within ceiling plenum that are not part of supporting structural or suspension system.

a. Splay hangers only where required to miss obstructions and offset resulting horizontal forces by bracing, countersplaying, or other equally effective means.

2. Where width of ducts and other construction within ceiling plenum produces hanger spacings that interfere with locations of hangers required to support standard suspension system members, install supplemental suspension members and hangers in the form of trapezes or equivalent devices.

a. Size supplemental suspension members and hangers to support ceiling loads within performance limits established by referenced installation standards.

Delete inapplicable construction types below.

Delete first subparagraph below if steel roof deck can carry ceiling loads; verify with structural engineer.  In 2002, SDI changed its recommendation against suspending loads from roof deck.  It deleted commentary in SDI Publication No. 30 that stated, "Suspended ceilings, light fixtures, ducts, or other utilities shall not be supported by the steel deck."

3. Do not attach hangers to steel roof deck.

4. Do not attach hangers to permanent metal forms.  Furnish cast-in-place hanger inserts that extend through forms.

5. Do not attach hangers to rolled-in hanger tabs of composite steel floor deck.

6. Do not connect or suspend steel framing from ducts, pipes, or conduit.

Furring channels must be wire tied to supports in most fire-resistance-rated assemblies.  Verify requirements of fire-resistance-rated assemblies and revise paragraph below to suit Project.

C. Fire-Resistance-Rated Assemblies:  Wire tie furring channels to supports.

Grid suspension systems are suitable for use with gypsum board.  They might not be acceptable for gypsum veneer plaster; consult gypsum veneer plaster and grid suspension system manufacturers before specifying them.

D. Grid Suspension Systems:  Attach perimeter wall track or angle where grid suspension systems meet vertical surfaces.  Mechanically join main beam and cross-furring members to each other and butt-cut to fit into wall track.

Example tolerance below is based on ASTM C 636 for acoustical ceilings.

E. Installation Tolerances:  Install suspension systems that are level to within 1/8 inch in 12 feet (3 mm in 3.6 m) measured lengthwise on each member that will receive finishes and transversely between parallel members that will receive finishes.

3.3 INSTALLING FRAMED ASSEMBLIES

Retain first paragraph below if studs will abut dissimilar metals at exterior walls or exterior masonry walls that may become damp.

A. Where studs are installed directly against exterior masonry walls or dissimilar metals at exterior walls, install isolation strip between studs and exterior wall.

B. Install tracks (runners) at floors and overhead supports.  Extend framing full height to structural supports or substrates above suspended ceilings, except where partitions are indicated to terminate at suspended ceilings.  Continue framing around ducts penetrating partitions above ceiling.

Indicate locations and details of slip-type and fire-rated head joints on Drawings.  See "Crack Control" Article in the Evaluations.

1. Slip-Type Head Joints:  Where framing extends to overhead structural supports, install to produce joints at tops of framing systems that prevent axial loading of finished assemblies.

2. Door Openings:  Screw vertical studs at jambs to jamb anchor clips on door frames; install runner track section (for cripple studs) at head and secure to jamb studs.

Usually retain subparagraph below.  For heavy doors, 200 to 300 lb (91 to 136 kg) that are up to 48 inches (1219 mm) wide, GA-600 recommends using 0.0312-inch- (0.79-mm-) thick studs.  Design framing for doors more than 48 inches (1219 mm) wide, double doors, and extra-heavy doors to meet loading conditions.

a. Install two studs at each jamb, unless otherwise indicated.

Retain subparagraph below if one-piece control joints are required at heads of doors.

Retain subparagraph below if suspended ceilings cannot withstand forces generated by opening and closing doors.

b. Extend jamb studs through suspended ceilings and attach to underside of overhead structure.

Delete first subparagraph below if no framed openings other than doors, or revise to suit Project.  Fully detail framing for large openings on Drawings.

3. Other Framed Openings:  Frame openings other than door openings the same as required for door openings, unless otherwise indicated.  Install framing below sills of openings to match framing required above door heads.

4. Fire-Resistance-Rated Partitions:  Install framing to comply with fire-resistance-rated assembly indicated and support closures and to make partitions continuous from floor to underside of solid structure.

Indicate locations and details of firestop track on Drawings.

a. Firestop Track:  Where indicated, install to maintain continuity of fire-resistance-rated assembly indicated.

5. Sound-Rated Partitions:  Install framing to comply with sound-rated assembly indicated.

C. Direct Furring:

1. Attach to concrete or masonry with stub nails, screws designed for masonry attachment, or powder-driven fasteners spaced 24 inches (610 mm) o.c.

D. Installation Tolerance:  Install each framing member so fastening surfaces vary not more than 1/8 inch (3 mm) from the plane formed by faces of adjacent framing.

END OF SECTION 09111

NON-LOAD-BEARING STEEL FRAMING

09111 - 1

