Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


MASTERSPEC Short Form Copyright 2003 (R 06/01) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16442 - PANELBOARDS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes distribution panelboards and lighting and appliance branch-circuit panelboards.

1.2 SUBMITTALS

A. Product Data:  For each type of panelboard, overcurrent protective device, accessory, and component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each panelboard and related equipment.

1. Dimensioned plans, elevations, sections, and details.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Enclosure types and details for types other than NEMA 250, Type 1.

b. Bus configuration, current, and voltage ratings.

c. Short-circuit current rating of panelboards and overcurrent protective devices.

Retain first subparagraph below if series rating of overcurrent protective devices is used.

d. UL listing for series rating of installed devices.

e. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

2. Wiring Diagrams:  Power, signal, and control wiring.

3. Field quality-control test reports.

4. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NEMA PB 1.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

1. Panelboards, Overcurrent Protective Devices, Controllers, Contactors, and Accessories:

a. Eaton Corporation; Cutler-Hammer Products.

b. General Electric Co.; Electrical Distribution & Protection Div.

c. Siemens Energy & Automation, Inc.

d. Square D.

2.2 MANUFACTURED UNITS

A. Enclosures:  Surface mounted cabinets.  NEMA PB 1, Type 1.

1. Rated for environmental conditions at installed location.

a. Outdoor, Wet or Damp Indoor Locations:  NEMA 250, Type 4X Stainless Steel
Enclosures in hazardous locations must be carefully selected to meet the division and group listing of the environment.

2. Front:  Secured to box with concealed trim clamps.  For surface-mounted fronts, match box dimensions; for flush-mounted fronts, overlap box.

Retain subparagraph above or first subparagraph below.

B. Phase and Ground Buses:  Hard-drawn copper, 98 percent conductivity.
C. Conductor Connectors:  Suitable for use with conductor material.

1. Ground Lugs and Bus Configured Terminators:  Compression type.

Retain paragraph below for panelboards incorporating one or more main service disconnect switches.

D. Service Equipment Label:  UL labeled for use as service equipment for panelboards with main service disconnect switches.

Retain first paragraph below if future provisions are required.

E. Future Devices:  Mounting brackets, bus connections, and necessary appurtenances required for future installation of devices.

F. Panelboard Short-Circuit Rating:

Retain one of two subparagraphs below for series-rated system or system that has panelboards and circuit breakers rated for full value of short-circuit current available at location of equipment.  Coordinate with Drawings.

1. UL label indicating series-connected rating with integral or remote upstream overcurrent protective devices.  Include size and type of upstream device allowable, branch devices allowable, and UL series-connected short-circuit rating.

2. Fully rated to interrupt symmetrical short-circuit current available at terminals.

2.3 DISTRIBUTION PANELBOARDS

Coordinate this Article with Drawings.

A. Doors:  Secured with vault-type latch with tumbler lock; keyed alike.  Omit for fused-switch panelboards.

B. Main Overcurrent Protective Devices:  Circuit breaker.
C. Branch Overcurrent Protective Devices:

Retain one of three subparagraphs below.

1. For Circuit-Breaker Frame Sizes 125 A and Smaller:  Bolt-on circuit breakers.

2. For Circuit-Breaker Frame Sizes Larger Than 125 A:  Bolt-on circuit breakers; plug-in circuit breakers where individual positive-locking device requires mechanical release for removal.

3. Fused switches.

2.4 LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

A. Branch Overcurrent Protective Devices:  Bolt-on circuit breakers, replaceable without disturbing adjacent units.

Coordinate paragraph below with Drawings.

B. Doors:  Concealed hinges; secured with flush latch with tumbler lock; keyed alike.

2.5 OVERCURRENT PROTECTIVE DEVICES

Coordinate this Article with schedules and Drawings.

A. Molded-Case Circuit Breaker:  UL 489, with interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. GFCI Circuit Breakers:  Single- and two-pole configurations with 30-mA trip sensitivity.

3. Molded-Case Circuit-Breaker Features and Accessories:  Standard frame sizes, trip ratings, and number of poles.

a. Lugs:  Mechanical style, suitable for number, size, trip ratings, and conductor materials.

b. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

c. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at 55 percent of rated voltage.

B. Fused Switch:  NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

C. Fuses are specified in Division 16 Section "Fuses."

2.6 ACCESSORY COMPONENTS AND FEATURES

Retain two paragraphs below for overcurrent protective devices that require these items; delete if these items are specified elsewhere, such as in Division 16 Section "Switchboards."

A. Furnish accessory set including tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

B. Furnish portable test set to test functions of solid-state trip devices without removal from panelboard.

Retain paragraph below for installations in humid environments.

C. Fungus Proofing:  Permanent fungicidal treatment for panelboard interior, including overcurrent protective devices and other components.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install panelboards and accessories according to NEMA PB 1.1.

Retain first paragraph below if seismic controls are required for Project.  Coordinate with Drawings.

B. Mount top of trim 74 inches (1880 mm) above finished floor, unless otherwise indicated.

C. Mount plumb and rigid without distortion of box.  Mount recessed panelboards with fronts uniformly flush with wall finish.

D. Install overcurrent protective devices and controllers.

Subaragraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

1. Set field-adjustable switches and circuit-breaker trip ranges.

E. Install filler plates in unused spaces.

Retain first paragraph below unless ceilings are not accessible.

F. Stub four 1-inch (27-GRC) empty conduits from panelboard into accessible ceiling space or space designated to be ceiling space in the future.  Stub four 1-inch (27-GRC) empty conduits into raised floor space or below slab not on grade.

G. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section Electrical Identification.
H. Panelboard Nameplates:  Label each panelboard with engraved metal or laminated-plastic nameplate mounted with corrosion-resistant screws.

Coordinate two paragraphs below with Drawings.

I. Ground equipment according to Division 16 Section "Grounding and Bonding."

J. Connect wiring according to Division 16 Section "Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

B. Perform the following field tests and inspections and prepare test reports:

1. Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Section 7.5 for switches and Section 7.6 for molded-case circuit breakers.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

END OF SECTION 16442

PANELBOARDS
16442 - 4

