Louisiana Army National Guard

Preliminary Review Documents
141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications


SECTION 03300 - CAST-IN-PLACE CONCRETE

PART 1 - GENERAL

1.1 
SUMMARY

A.
Scope:  The work to be done under this section of the specifications includes all labor, materials, equipment, and services necessary for cast-in-place concrete including formwork, reinforcing, mix design, placement procedures, finishes, as indicated on drawings and herein specified.

1.2  
CAST-IN-PLACE CONCRETE:  Includes the following:

A.
All concrete shown on the drawings.

B.
Equipment pads and bases.

1.
Include all concrete pads and supports for mechanical and electrical equipment 

where indicated.  Unless otherwise shown, these pads shall include concrete of 

the size required to support the equipment purchased and 500 lbs. of reinforcing 

steel per cubic yard of concrete. 
 SEQ CHAPTER \h \r 11.3
    REFERENCES

      A.
    American Society for Testing and Materials (ASTM)           

       
1.   
C31



Making and Curing Concrete Test  Specimens in the Field

   2.   
C39   


Test for Compressive Strength of Cylindrical Concrete Specimens

      
3.   
C143 


Test for Slump of Portland Cement Concrete

       
4.   
C150 

 

Portland Cement



5.   
C260 




Air-Entraining Admixtures for Concrete



 SEQ CHAPTER \h \r 16.   

C494

 


Chemical Admixtures for Concrete

       

7.  
   C33



Concrete Aggregates

      
8.   
C618 
  

Fly Ash for Use in Concrete

       
9.   
C94 



Ready-Mixed Concrete 

            
10.
D2103



Polyethylene Film and Sheeting    

            
11.
E1155



Test Method for Determining FF Floor Flatness and FL Floor Levelness






 


Numbers
      
     B.
  
American Concrete Institute (ACI)  




 1.  
ACI 214-89

Recommended Practice for Evaluation of Compression Test Results for                              



Field  Concrete

       


2.   
ACI 301-89
Specifications for Structural Concrete for Buildings

      


3.   
ACI 304-89
Recommended Practice for Measuring, Mixing, Transporting, and Placing Concrete

      


4.   
ACI 308-92
Standard Practice for Curing Concrete

      


5.   
ACI 318-95
Building Code Requirements for Reinforced Concrete

      


6.  
SP-66  
ACI       Detailing Manual 





7.     AC1 117

Tolerances for Concrete Construction and Materials
8.
AC1 302.1R
Guide for Concrete Floor and Slab Construction
1.4 
SUBMITTALS

A.
General:  Submit the following according to Conditions of the Contract and Division 1 Specification Sections.

B.
Product data for proprietary materials and items, including reinforcement and forming accessories, admixtures, patching compounds, waterstops, joint systems, curing compounds, dry-shake finish materials, and others if requested by Architect.

C.
Shop drawings for reinforcement detailing fabricating, bending, and placing concrete  reinforcement. Comply with ACI 315 "Manual of Standard Practice for Detailing Reinforced Concrete Structures" showing bar schedules, stirrup spacing, bent bar diagrams, and arrangement of concrete reinforcement.  Include special reinforcing required for openings through concrete structures.  Reproductions made from contract documents will not be allowed.  Submit two prints and one reproducible.

D.
Samples of materials as requested by Architect, including names, sources, and descriptions.

E.
Laboratory test reports for concrete materials and mix design test.

F.
Material certificates in lieu of material laboratory test reports when permitted by Architect.  Material certificates shall be signed by manufacturer and Contractor, certifying that each material item complies with or exceeds specified requirements.  Provide certification from admixture manufacturers that chloride content complies with specification requirements.

1.5 
QUALITY ASSURANCE

A.
Codes and Standards:  Comply with provisions of the following codes, specifications, and standards, except where more stringent requirements are shown or specified:
1.
American Concrete Institute (ACI) 301-89, "Specifications for Structural Concrete 

for Buildings."



2.
ACI 318, "Building Code Requirements for Reinforced Concrete," current edition.

3.
Concrete Reinforcing Steel Institute (CRSI) "Manual of Standard Practice,"current

edition.

B.
Concrete Testing Service:  The Contractor shall employ a testing agency to perform material evaluation tests and to design concrete mixes.

C.
Materials and installed work may require testing and retesting at any time during 

progress of 
Work.  Retesting of rejected materials for installed Work shall be done at 

  Contractor's expense.

PART 2 - PRODUCTS
2.1 
FORM MATERIALS

A.
Forms for Exposed Finish Concrete:  Plywood, metal, metal-framed plywood faced, 

or other acceptable panel-type materials to provide continuous, straight, smooth, exposed surfaces.  Furnish in largest practicable sizes to minimize number of joints and to conform to joint system shown on drawings.

B.
Forms for Unexposed Finish Concrete:  Plywood, lumber, metal, or another acceptable material.  Provide lumber dressed on at least two edges and one side for tight fit.

C.
Forms for Creating Void Areas:   Fiberboard carton  forms completely wax impregnated  throughout with water resistant paraffin and polyethylene and designed to carry a uniformly distributed top load up to 1000 p.s.f.

D.
Form Release Agent:  Provide commercial formulation form release agent with a maximum of 350 mg/l volatile organic compounds (VOCs) that will not bond with, stain, or adversely affect concrete surfaces and will not impair subsequent treatments of concrete surfaces.

E.
Form Ties:  Factory-fabricated, adjustable-length, removable or snap-off metal form ties designed to prevent form deflection and to prevent spalling of concrete upon removal.  Provide units that will leave no metal closer than 1-1/2 inches to the plane of the exposed concrete surface.

2.2 
REINFORCING MATERIALS

A.
Reinforcing Bars:  ASTM A 615, Grade 60 deformed.

B.
Steel Wire:  ASTM A 82, plain, cold-drawn steel.

C.
Welded Wire Fabric:  ASTM A 185, welded steel wire fabric.

D.
Deformed-Steel Welded Wire Fabric:  ASTM A 497.

E.
Supports for Reinforcement:  Bolsters, chairs, spacers, and other devices for spacing, supporting, and fastening reinforcing bars and welded wire fabric in place.  Use wire bar-type supports complying with CRSI specifications.
1.
For slabs-on-grade, use supports with sand plates or horizontal runners where base material ill not support chair legs.

2.
For exposed-to-view concrete surfaces where legs of supports are in contact with forms, provide supports with legs that are protected by plastic (CRSI, Class 1). 

2.3 
CONCRETE MATERIALS

A.
Portland Cement:  ASTM C 150, Type I or Type II.  

       

1.

Use one brand of cement throughout Project unless otherwise acceptable to Architect.

     B.

Fly Ash:  ASTM C 618, Type C or F.

     C.
Normal-Weight Aggregates:  ASTM C 33 and as specified.  Provide aggregates from a single source for exposed concrete.
1.

For exposed exterior surfaces, do not use fine or coarse aggregates that contain 


substances that cause spalling.



2.
Local aggregates not complying with ASTM C 33 that have been shown to produce concrete of adequate strength and durability by special tests or actual service may be used when acceptable to Architect.

D.

Lightweight Aggregates:  ASTM C 330.

E.

Water:  Potable.

     F.
Admixtures, General:  Provide concrete admixtures that contain not more than 0.1 percent chloride ions.


 G.
Air-Entraining Admixture:  ASTM C 260, certified by manufacturer to be compatible with other required admixtures.

H.
Water-Reducing Admixture:  ASTM C 494, Type A.

I.
High-Range Water-Reducing Admixture:  ASTM C 494, Type approved by Architect.
    J. 

Water-Reducing, Accelerating Admixture:  ASTM C 494, Type C or E.  
    K.

Water-Reducing, Retarding Admixture:  ASTM C 494, Type D.
2.4 
RELATED MATERIALS

A.
Vapor Retarder:  Provide vapor retarder that is resistant to deterioration when tested

according to ASTM E 154, as follows:
1.
Clear polyethylene sheet not less than 6 mils thick conforming to ASTM D2103. 

B.
Absorptive Cover:  Burlap cloth made from jute or kenaf, weighing approximately 9 oz. per sq. yd., complying with AASHTO M 182, Class 2.

C.
Moisture-Retaining Cover:  One of the following, complying with ASTM C 171.
1.
Waterproof paper.



2.
Polyethylene film.



3.
Polyethylene-coated burlap.

D.
Liquid Membrane-Forming Curing Compound:  Liquid-type membrane-forming curing compound complying with ASTM C 309, Type I, Class A.  Moisture loss not more than 0.55 kg/sq. meter when applied at 200 sq. ft./gal.
1.
Provide material that has a maximum volatile organic compound (VOC) rating of 350 mg per liter.

E.
Water-Based Acrylic Membrane Curing Compound:  ASTM C 309, Type I, Class B.


F.
Evaporation Control:  Monomolecular film-forming compound applied to exposed concrete slab surfaces for temporary protection from rapid moisture loss.

G.
Underlayment Compound:  Free-flowing, self-leveling, pumpable, cement-based compound for applications from 1 inch thick to feathered edges.

H.
Bonding Agent:  Polyvinyl acetate or acrylic base.

I.
Epoxy Adhesive:  ASTM C 881, two-component material suitable for use on dry or damp surfaces. Provide material type, grade, and class to suit Project requirements.

J.
Waterstops:  Dumbbell or centerbulb polyvinyl chloride type conforming to CRD-C572.  Size and configuration shall be as indicated on the Drawings.
K.
Curing, Sealing and Hardening Compound:  Water based chemically-reactive penetrating sealer and hardener, seals by densifying concrete so that water molecules cannot pass through but air and water vapor  can.  Products offered  by manufacturers to comply with the requirements include the following:

1.
Ashford Formula Curecrete Distribution, Inc.

L.
Dry Shake Surface Hardner:  Product composed of a pre-mixed, ready-to-use mineral aggregate surface hardener that is proportioned, mixed and packaged at the factory.  Products offered by manufacturers to comply with the requirements include the following: 


1.    MASTERCRON FF ; Master Builders, Inc.

2.5 

PROPORTIONING AND DESIGNING MIXES

    A. 

Prepare design mixes for each type and strength of concrete by either laboratory trial batch or




field  experience methods as specified in ACI 301.  For the trial batch method, use an independent testing agency acceptable to Architect for preparing and reporting proposed mix designs.

 B.
          Submit written reports to Architect of each proposed mix for each class of concrete at least 15 days prior to start of Work.  Do not begin concrete production until proposed mix designs have been submitted to Architect.

C.
          Design mixes to provide normal weight concrete or light weight concrete with the 28-day compressive strength as indicated on drawings.

D.

Slump Limits:  Proportion and design mixes to result in concrete slump at point of placement as follows:   

   

1.
Not more than 4 inches.

E.
Adjustment to Concrete Mixes:  Mix design adjustments may be requested by Contractor when characteristics of materials, job conditions, weather, test results, or other circumstances warrant, as accepted by Architect.  Laboratory test data for revised mix design and strength results must be submitted to and accepted by Architect before using in Work.

2.6
ADMIXTURES

A.

Use water-reducing admixture or high-range water-reducing admixture (superplasticizer) in concrete, as required, for placement and workability.

B.

Use accelerating admixture in concrete slabs placed at ambient temperatures below 40 deg F (10 deg C) and falling.
2.7 

CONCRETE MIXING

A.

Ready-Mixed Concrete:  Comply with requirements of ASTM C 94, and as specified.

1.
When air temperature is between 85 deg F (30 deg C) and 90 deg F (32 deg C), reduce mixing and delivery time from 1-1/2 hours to 75 minutes, and when air temperature is above 90 deg F (32 deg C), reduce mixing and delivery time to 60 minutes.  Ice can be added to concrete so that delivery time can remain at 1-1/2 hours.

PART 3 - EXECUTION

3.1 
GENERAL


A.
Coordinate the installation of joint materials, vapor retarder/barrier, and other related materials with placement of forms and reinforcing steel.


3.2
 FORMS

A.
General:  Design, erect, support, brace, and maintain formwork to support vertical, lateral, static, and dynamic loads that might be applied until concrete structure can support such loads.  Construct formwork so concrete members and structures are of correct size, shape, alignment, elevation, and position.  Maintain formwork construction tolerances and surface irregularities complying with the following ACI 347 limits:


1.
Provide Class A tolerances for concrete surfaces exposed to view.


2.
Provide Class C tolerances for other concrete surfaces.

   B.
Construct forms to sizes, shapes, lines, and dimensions shown and to obtain accurate alignment, location, grades, level, and plumb work in finished structures.  Provide for openings, offsets, sinkages, keyways, recesses, moldings, rustications, reglets, chamfers, blocking, screeds, bulkheads, anchorages and inserts, and other features required in the Work.  Use selected materials to obtain required finishes.  Solidly butt joints and provide backup at joints to prevent cement paste from leaking.

   C.
Fabricate forms for easy removal without hammering or prying against concrete surfaces.  Provide crush plates or wrecking plates where stripping may damage cast concrete surfaces.  Provide top forms for inclined surfaces where slope is too steep to place concrete with bottom forms only.  Kerf wood inserts for forming keyways, reglets, recesses, and the like for easy removal.


D.
Provide temporary openings for clean-outs and inspections where interior area of formwork is inaccessible before and during concrete placement.  Securely brace temporary openings and set tightly to forms to prevent losing concrete mortar.  Locate temporary openings in forms at inconspicuous locations.


E.
Chamfer exposed corners and edges as indicated, using wood, metal, PVC, or rubber chamfer strips fabricated to produce uniform smooth lines and tight edge joints.


F.
Provisions for Other Trades:  Provide openings in concrete formwork to accommodate work of other trades.  Determine size and location of openings, recesses, and chases from trades providing such items.  Accurately place and securely support items built into forms.


G.
Cleaning and Tightening:  Thoroughly clean forms and adjacent surfaces to receive concrete.  Remove chips, wood, sawdust, dirt, or other debris just before placing concrete.  Retighten forms and bracing before placing concrete, as required, to prevent mortar leaks and maintain proper alignment.
3.3 
VAPOR RETARDER/BARRIER INSTALLATION

A.
General:   Under all slabs on grade, place vapor retarder/barrier sheeting in position with longest dimension parallel with direction of pour.


B.
Lap joints 6 inches and seal with manufacturer's recommended mastic or pressure-sensitive tape.

3.4 
PLACING REINFORCEMENT


A.
General:  Comply with Concrete Reinforcing Steel Institute's recommended practice for "Placing Reinforcing Bars," for details and methods of reinforcement placement and supports and as specified.

1.
Avoiding cutting or puncturing vapor retarder/barrier during reinforcement placement and concreting operations.  Repair damages before placing concrete.


B.
Clean reinforcement of loose rust and mill scale, earth, ice, and other materials that reduce or destroy bond with concrete.

   C.
Accurately position, support, and secure reinforcement against displacement.   Locate and support reinforcing by metal chairs, runners, bolsters, spacers, and hangers, as approved by Architect.


D.
Place reinforcement to maintain minimum coverages as indicated for concrete protection.  Arrange, space, and securely tie bars and bar supports to hold reinforcement in position during concrete placement operations.  Set wire ties so ends are directed into concrete, not toward exposed concrete surfaces.


E.
Install welded wire fabric in lengths as long as practicable.  Lap adjoining pieces at least one full mesh and lace splices with wire.  Offset laps of adjoining widths to prevent continuous laps in either direction.
3.5
JOINTS


A.
Construction Joints:  Locate and install construction joints so they do not impair strength or appearance of the structure, as acceptable to Architect.


B.
Provide keyways as indicated on drawings or at least 1-1/2 inches deep in construction joints in walls and slabs and between walls and footings.  Bulkheads designed and accepted for this purpose may be used for slabs.


C.
Provide dumbbell or centerbulb type waterstops at all construction joints in areas indicated on the drawings.



D.
Place construction joints perpendicular to main reinforcement.  Continue reinforcement across construction joints except as indicated otherwise.  Do not continue reinforcement through sides of strip placements.


E.
Use bonding agent on existing concrete surfaces that will be joined with fresh concrete.


F.
Isolation Joints in Slabs-on-Grade:  Construct isolation joints in slabs-on-grade at points of contact between slabs-on-grade and vertical surfaces, such as column pedestals, foundation walls, grade beams, and other locations, as indicated. 

1.
Joint fillers and sealants are specified in Division 7 Section "Joint Sealants."

3.6 
INSTALLING EMBEDDED ITEMS

A.
General:  Set and build into formwork anchorage devices and other embedded items required for other work that is attached to or supported by cast-in-place concrete.  Use setting drawings, diagrams, instructions, and directions provided by suppliers of items to be attached.

B.
Forms for Slabs:  Set edge forms, bulkheads, and intermediate screed strips for slabs to achieve required elevations and contours in finished surfaces.  Provide and secure units to support screed strips using strike-off templates or compacting-type screeds.

3.7 
PREPARING FORM SURFACES

A.
General:  Coat contact surfaces of forms with an approved, nonresidual, low-VOC, form-coating compound before placing reinforcement.

1.
Do not allow excess form-coating material to accumulate in forms or come into contact with in-place concrete surfaces against which fresh concrete will be placed.  Apply according to manufacturer's instructions.


2.
Coat steel forms with a nonstaining, rust-preventative material.  Rust-stained steel formwork is not acceptable.

3.8
CONCRETE PLACEMENT

A.
Inspection:  Before placing concrete, inspect and complete formwork installation, reinforcing steel, and items to be embedded or cast in.  Notify other trades to permit installation of their work.

B.
General:  Comply with ACI 304, "Guide for Measuring, Mixing, Transporting, and Placing Concrete," and as specified.

1.
Deposit concrete continuously or in layers of such thickness that no new concrete will be placed on concrete that has hardened sufficiently to cause seams or planes of weakness.  If a section cannot be placed continuously, provide construction joints as specified.  Deposit concrete to avoid segregation at its final location.
C.
Placing Concrete in Forms:  Deposit concrete in forms in horizontal layers no deeper than 24 inches and in a manner to avoid inclined construction joints.  Where placement consists of several layers, place each layer while preceding layer is still plastic to avoid cold joints.


1.
Consolidate placed concrete by mechanical vibrating equipment supplemented by hand-spading, rodding, or tamping.  Use equipment and procedures for consolidation of concrete complying with ACI 309.



2.
Do not use vibrators to transport concrete inside forms.  Insert and withdraw vibrators vertically at uniformly spaced locations no farther than the visible effectiveness of  the machine.  Place vibrators to rapidly penetrate placed layer and at least 6 inches into preceding layer.  Do not insert vibrators into lower layers of concrete that have begun to set.  At each insertion, limit duration of vibration to time necessary to consolidate concrete and complete embedment of reinforcement and other embedded items without causing mix to segregate.

D.
Placing Concrete Slabs:  Deposit and consolidate concrete slabs in a continuous operation, within limits of construction joints, until completing placement of a panel or section.


1.
Consolidate concrete during placement operations so that concrete is thoroughly worked around reinforcement, other embedded items and into corners.

      
 2.
Bring slab surfaces to correct level with a straightedge and strike off.  Use bull floats or darbies to smooth surface free of humps or hollows.  Do not disturb slab surfaces prior to beginning finishing operations.



3.
Maintain reinforcing in proper position on chairs during concrete placement.

E.
Cold-Weather Placement:  Comply with provisions of ACI 306 and as follows.  Protect concrete work from physical damage or reduced strength that could be caused by frost, freezing actions, or low temperatures.

F.
Hot-Weather Placement:  When hot weather conditions exist that would impair quality and strength of concrete, place concrete complying with ACI 305 and as specified.


1.
Use water-reducing retarding admixture when required by high temperatures, low humidity, or other adverse placing conditions, as acceptable to Architect.

3.9 
FINISHING FORMED SURFACES

A.
Rough-Formed Finish:  Provide a rough-formed finish on formed concrete surfaces not exposed to view in the finished Work or concealed by other construction.  This is the concrete surface having texture imparted by form-facing material used, with tie holes and defective areas repaired and patched, and fins and other projections exceeding 1/4 inch in height rubbed down or chipped off.

B.
Smooth-Formed Finish:  Provide a smooth-formed finish on formed concrete surfaces exposed to view or to be covered with a coating material applied directly to concrete, or a covering material applied directly to concrete, such as waterproofing, dampproofing, veneer plaster, painting, or another similar system.  This is an as-cast concrete surface obtained with selected form-facing material, arranged in an orderly and symmetrical manner with a minimum of seams.  Repair and patch defective areas with fins and other projections completely removed and smoothed.

C.
Grout Cleaned Finish:  Provide where indicated on Drawings in accordance with ACI 301-89, paragraph 10.3.2.

D.
Related Unformed Surfaces:  At tops of walls, horizontal offsets, and similar unformed surfaces adjacent to formed surfaces, strike-off smooth and finish with a texture matching adjacent formed surfaces. 

3.10 
MONOLITHIC SLAB FINISHES
A.
Scratch Finish:  Apply scratch finish to monolithic slab surfaces to receive concrete floor topping or mortar setting beds for tile, portland cement terrazzo, and other bonded applied cementitious finish flooring material, and where indicated.

B.
Float Finish:  Apply float finish to monolithic slab surfaces to receive trowel finish and other finishes as specified; slab surfaces to be covered with membrane or elastic waterproofing, membrane or elastic roofing, or sand-bed terrazzo; and where indicated.


1.
After screeding, consolidating, and leveling concrete slabs, do not work surface until ready for floating.  Begin floating, using float blades or float shoes only, when surface water has disappeared, or when concrete has stiffened sufficiently to permit operation of power-driven floats, or both.  Consolidate surface with power-driven floats or by hand-floating if area is small or inaccessible to power units.    Uniformly slope surfaces to drains.  Immediately after leveling, refloat surface to a uniform, smooth, granular texture.

C.
Trowel Finish:  Apply a trowel finish to monolithic slab surfaces exposed to view and slab surfaces to be covered with resilient flooring, carpet, ceramic or quarry tile, paint, or another thin film-finish coating system.
1.
After floating, begin first trowel-finish operation using a power-driven trowel.  Begin final troweling when surface produces a ringing sound as trowel is moved over surface.  Consolidate concrete surface by final hand-troweling operation, free of trowel marks, uniform in texture and appearance.

 D.
Trowel and Fine Broom Finish:  Where ceramic or quarry tile is to be installed with thin-set mortar, apply a trowel finish as specified, then immediately follow by slightly scarifying the surface with a fine broom.

 E.
Nonslip Broom Finish:  Apply a nonslip broom finish to exterior concrete platforms, steps, and ramps, and elsewhere as indicated.


1.
Immediately after float finishing, slightly roughen concrete surface by brooming with fiber-bristle broom perpendicular to main traffic route.  Coordinate required final finish with Architect before application.


 F.
Finishing Tolerances – All slabs other than those designated as Random Traffic Slabs 


shall be finished with Class A tolerances in accordance with ACI 301, paragraph 11.9.   


For Random Traffic Slab tolerances refer to paragraph 3.16 of this section.
3.11 
MISCELLANEOUS CONCRETE ITEMS

A.
Filling In:  Fill in holes and openings left in concrete structures for passage of work by other trades, unless otherwise shown or directed, after work of other trades is in place.  Mix, place, and cure concrete as specified to blend with in-place construction.  Provide other miscellaneous concrete filling shown or required to complete Work.

B.
Curbs:  Provide monolithic finish to interior curbs by stripping forms while concrete is still green and by steel-troweling surfaces to a hard, dense finish with corners, intersections, and terminations slightly rounded.

C.
Equipment Bases and Foundations:  Provide machine and equipment bases and foundations as shown on drawings.  Set anchor bolts for machines and equipment to template at correct elevations, complying with diagrams or templates of manufacturer furnishing machines and equipment.

3.12 

CONCRETE CURING AND PROTECTION

A.

General:  Protect freshly placed concrete from premature drying and excessive old or hot temperatures. In hot, dry, and windy weather protect concrete from rapid moisture loss before and during finishing operations with an evaporation-control material.  Apply according to manufacturer's instructions after screeding and bull floating, but before power floating and troweling.

1.
Start initial curing as soon as free water has disappeared from concrete surface after placing and finishing.  Weather permitting, keep continuously moist for not less than 7 days.

B.

Curing Methods:  Cure concrete by curing compound, by moist curing, by moisture-retaining  cover curing, or by combining these methods, as specified.

1.  
Provide moisture curing by the following methods:
 



a.
Keep concrete surface continuously wet by covering with water.

 



b.  
Use continuous water-fog spray.

   
c.
Cover concrete surface with specified absorptive cover, thoroughly saturate cover with water, and keep continuously wet.  Place absorptive cover to provide coverage of concrete surfaces and edges, with a 4-inch lap over adjacent absorptive covers.


2. 
   Provide moisture-retaining cover curing as follows:

a.
Cover concrete surfaces with moisture-retaining cover for curing concrete, placed in widest practicable width with sides and ends lapped at least 3 inches and sealed by waterproof tape or adhesive.  Immediately repair any holes or tears during curing period using cover material and waterproof tape.
 
3.
Apply curing compound on exposed interior slabs and on exterior slabs, walks, and curbs as follows:



a.
Apply curing compound to concrete slabs as soon as final finishing operations are complete (within 2 hours and after surface water sheen has disappeared).  Apply uniformly in continuous operation by power spray or roller according to manufacturer's directions.  Recoat areas subjected to heavy rainfall within 3 hours after initial application.  Maintain continuity of coating and repair damage during curing period.

b.
Use membrane curing compounds that will not affect surfaces to be covered with finish materials applied directly to concrete.
C.
  Curing Formed Surfaces:  Cure formed concrete surfaces, including underside of beams, supported slabs, and other similar surfaces, by moist curing with forms in place for the full curing period or until forms are removed.  If forms are removed, continue curing by methods specified above, as applicable.

D.
Curing Unformed Surfaces:  Cure unformed surfaces, including slabs, floor topping, and 

other flat surfaces, by applying the appropriate curing method.


 1.
Final cure concrete surfaces to receive finish flooring with a moisture-retaining cover, unless otherwise directed.
3.13 
REMOVING FORMS


A.
General:  Formwork not supporting weight of concrete, such as sides of beams,walls, 



columns, and similar parts of the work, may be removed after cumulatively curing at not 


less than 50 deg F (10 deg C) for 12 hours after placing concrete, provided concrete is 


sufficiently hard to not be damaged by form-removal operations, and provided curing and 


protection operations are maintained.


B.
Formwork supporting weight of concrete, such as beam soffits, joists, slabs, and other 


structural elements until concrete has attained at least 75 percent of design minimum 


compressive strength at 28 days.  Determine potential compressive strength of in-place 


concrete by testing field-cured specimens representative of concrete location or members.

    C. 
Comply with ACI 301-89, Chapter 4, Article 4.6 - Reshoring.
3.14 
REUSING FORMS

 
A.
Clean and repair surfaces of forms to be reused in the Work.  Split, frayed, delaminated, or 


otherwise damaged form-facing material will not be accceptable for exposed surfaces.  


Apply new form-coating compound as specified for new formwork.



B.
When forms are extended for successive concrete placement, thoroughly clean surfaces, remove fins and laitance, and tighten forms to close joints.  Align and secure joint to avoid offsets.  Do not use patched forms for exposed concrete surfaces except as acceptable to Architect.

3.15
CONCRETE SURFACE REPAIRS


A.
  Patching Defective Areas:  Repair and patch defective areas with cement mortar



  immediately after removing forms, when acceptable to Architect.


B.
Mix dry-pack mortar, consisting of one part portland cement to 2-1/2 parts fine aggregate 


passing a No. 16 mesh sieve, using only enough water as required for handling and



  placing.


1.
Cut out honeycombs, rock pockets, voids, and holes left by tie rods and bolts down to solid concrete but in no case to a depth less than 1 inch.  Make edges of cuts perpendicular to the concrete surface. Thoroughly clean, dampen with water, and brush-coat the area to be patched with bonding agent.  Place patching mortar before bonding agent has dried.

2.
For surfaces exposed to view, blend white portland cement and standard portland cement so that, when dry, patching mortar will match surrounding color.  Provide test areas at inconspicuous locations to verify mixture and color match before proceeding with patching. Compact mortar in place and strike-off slightly higher than surrounding surface.


C.

Repairing Formed Surfaces:  Remove and replace concrete having defective surfaces if defects cannot be repaired to satisfaction of Architect.  Surface defects include color and texture irregularities, cracks, spalls, air bubbles, honeycomb, rock pockets, fins and other projections on the surface, and stains and other discolorations that cannot be removed by cleaning.  Flush out form tie holes and fill with dry-pack mortar or precast cement cone plugs secured in place with bonding agent.
1.
Repair concealed formed surfaces, where possible, containing defects that affect the concrete's durability.  If defects cannot be repaired, remove and replace the concrete.


D.
Repairing Unformed Surfaces:  Test unformed surfaces, such as monolithic slabs, for smoothness and verify surface tolerances specified for each surface and finish.  Correct low and high areas as specified.  Test unformed surfaces sloped to drain for trueness of slope and smoothness by using a template having the required slope.
1.
Repair finished unformed surfaces containing defects that affect the concrete's durability.  Surface defects include crazing and cracks in excess of 0.01 inch wide or that penetrate to the reinforcement or completely through nonreinforced sections regardless of width, spalling, popouts, honeycombs, rock pockets, and other objectionable conditions.

2.
Correct high areas in unformed surfaces by grinding after concrete has cured at least 14 days.

3.
Correct low areas in unformed surfaces during or immediately after completing surface finishing operations by cutting out low areas and replacing with patching mortar.  Finish repaired areas to blend into adjacent concrete.  Proprietary underlayment compounds may be used when acceptable to Architect.

4.
Repair defective areas, except random cracks and single holes not exceeding 1 inch in diameter, by cutting out and replacing with fresh concrete.  Remove defective areas with clean, square cuts and expose reinforcing steel with at least 3/4-inch clearance all around.  Dampen concrete surfaces in contact with patching concrete and apply bonding agent.  Mix patching concrete of same materials to provide concrete of same type or class as original concrete.  Place, compact, and finish to blend with adjacent finished concrete.  Cure in same manner as adjacent concrete.

3.16
QUALITY CONTROL TESTING DURING CONSTRUCTION 


A.
General:  The Contractor  shall employ a testing agency to perform tests and to submit test reports.


B.
Sampling and testing for quality control during concrete placement shall include the following, as directed by Architect.

1.
Sampling Fresh Concrete:  ASTM C 172, except modified for slump to comply with ASTM C 94.

2.
Slump:  ASTM C 143; one test at point of discharge for each day's pour of each type of concrete; additional tests when concrete consistency seems to have changed.

3.
Air Content:  ASTM C 173, volumetric method for lightweight or normal weight concrete; ASTM C 231, pressure method for normal weight concrete; one for each day's pour of each type of air-entrained concrete.

4.
Concrete Temperature:  ASTM C 1064; one test hourly when air temperature is 40 deg F (4 deg C) and below, when 80 deg F (27 deg C) and above, and one test for each set of compressive-strength specimens.
5.
Compression Test Specimen:  ASTM C 31; one set of four standard cylinders for each compressive-strength test, unless otherwise directed.  Mold and store cylinders for laboratory-cured test specimens except when field-cured test specimens are required.
6.
Compressive-Strength Tests:  ASTM C 39; one set for each day's pour exceeding 5 cu. yd. plus additional sets for each 50 cu. yd. more than the first 25 cu. yd. of each concrete class placed in any one day; one specimen tested at 7 days, two specimens tested at 28 days, and one specimen retained in reserve for later testing if required.


 SEQ CHAPTER \h \r 1C.

Random Traffic Floor:



1.
Designation: The ground floor slab for the facility is designated the Random Traffic Floor.  Any floor slab comprising part of the Random Traffic Floor shall be designated a Random Traffic Slab.



2.
Local Flatness/Levelness Tolerance:   All Random Traffic Slabs shall conform to the following ACI F-Number requirements:

Specified Overall Value:
FF  35/FL25

Minimum Local Value:
FF24/FL17




 3.
General Conformity to Design Grade: The entire Random Traffic Floor shall fall within +or - 1/2" of the as-built floor elevations shown on the plans.



 4.
Expectations and Modifications: All floor tolerance measurements shall be referenced to the as-built design grades shown on the plans, even when (as with sloped-to-drain and predeflection cambers) such grades are not horizontal. 




 5.
Floor Tolerance Measurements:  Floor flatness and levelness tests on the Random Traffic Floor 
shall be conducted in accordance with the provisions set forth in ASTM E1155-87 





using a Dipstick © Floor Profiler manufactured by Face Construction Technologies, Norfolk, VA or approved equal.  Floor tolerance measurements shall be made by the Owner within 16 hours after completion of the final troweling operation - and in all cases before forms and/or shores have been removed - using a suitable flatness measuring device.  Results of all floor tolerance tests - including a formal notice of acceptance or rejection of the work - shall be provided to the Contractor within 24 hours after data collection (not excluding weekends or holidays.)




 6.
Remedy for out-of-tolerance work:   All Random Traffic Floor sections measuring at or above both of the specified Minimum Local F-Numbers shall be accepted for tolerance compliance as constructed.  All Random Traffic Floor sections measuring below either  (or both) of the specified Minimum Local F-Numbers shall be removed and replaced.  For the purposes of this paragraph, a floor section shall be any rectangular area bound by column and/ or half-column lines, as determined by  the A/E.                                        

 
 7.
   Defective Concrete Finishing:  Concrete finishing which is not true to line and plane, which is not thoroughly troweled and properly surfaced as required, which fails to achieve the specified tolerance requirements or has a rough top surface, except where required, or which does not connect properly to adjoining work, or does not slope to drains, or is not properly cured, will be deemed defective.  Remove and replace with proper work and material conforming to the requirements, when so directed by the A/E.

  8.
   Floors judged by the A/E to be unfit to receive floor covering material shall be brought to required finish by the Contractor at no additional cost to the Owner.  An underlayment material must be used.

D.
Test results will be reported in writing to Owner,  Architect, Structural Engineer, Ready-Mix


Producer, and  Contractor within 24 hours after tests.  Reports of compressive strength 

tests shall contain the Project  identification  name  and number, date of concrete 

placement, name of concrete testing  service,  concrete type and class, location of concrete 

batch in structure, design compressive strength at 28 days, concrete mix proportions and 

materials, compressive breaking strength, and type of break for both 7-day tests and 28-day 

tests.

E.
 Nondestructive Testing:  Impact hammer, sonoscope, or other nondestructive device may  
 be  permitted  but shall not be used as the sole basis for acceptance or rejection.

F.
 Additional Tests:  The testing agency will make additional tests of in-place concrete when 
 test results indicate specified concrete strengths and other characteristics have not been 
 attained in the structure, as directed by Architect.  Testing agency may conduct tests to        

 determine adequacy of concrete by cored cylinders complying with ASTM C 42, or by other                 methods as directed.
END OF SECTION 03300

CAST-IN-PLACE CONCRETE
03300 - 13

