Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
08/03 (R 05/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 054000 - COLD-FORMED METAL FRAMING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Exterior load-bearing wall framing.

2. Interior load-bearing wall framing.

3. Exterior non-load-bearing wall framing.

4. Floor joist framing.

5. Roof trusses.

6. Roof rafter framing.

7. Ceiling joist framing.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 05 Section "Metal Fabrications" for masonry shelf angles and connections.

2. Division 09 Section "Non-Structural Metal Framing" for interior non-load-bearing, metal-stud framing and ceiling-suspension assemblies.

3. Division 09 Section "Gypsum Board Shaft Wall Assemblies" for interior non-load-bearing, metal-stud-framed, shaft-wall assemblies.

1.3 PERFORMANCE REQUIREMENTS

Retain this Article if delegating any part of design responsibility for cold-formed metal framing to fabricator.  Coordinate with Part 2, deleting prescriptive requirements such as steel thickness and minimum yield strength unless imposing minimum design restrictions.  Insert other performance and design criteria below to suit Project or add to Drawings.  AIA Document A201 requires Owner or Architect to specify performance and design criteria to be satisfied.

A. Structural Performance:  Provide cold-formed metal framing capable of withstanding design loads within limits and under conditions indicated.

1. Design Loads:  [As indicated.] [As follows:]

Delete first seven subparagraphs below if design loads and load combinations are indicated on Drawings.

a. Dead Loads:  [Weights of materials and construction] <Insert applicable dead loads>.

b. Live Loads:  <Insert applicable live loads.>

c. Roof Loads:  <Insert applicable roof loads.>

d. Snow Loads:  <Insert applicable snow loads.>

e. Wind Loads:  <Insert applicable wind loads.>

f. Seismic Loads:  <Insert applicable seismic loads.>

g. <Insert loads.>

2. Deflection Limits:  Design framing systems to withstand[ design loads] without deflections greater than the following:

Component deflection limits in first eight subparagraphs below are examples only.  Select deflection limits from applicable subparagraphs or insert other limits as appropriate for wall, floor, and ceiling finish materials.

a. Exterior Load-Bearing Wall Framing:  Horizontal deflection of [1/240] [1/360] [1/600] [1/720] of the wall height.

b. Interior Load-Bearing Wall Framing:  Horizontal deflection of [1/240] [1/360] of the wall height under a horizontal load of 5 lbf/sq. ft. (239 Pa).

c. Exterior Non-Load-Bearing Framing:  Horizontal deflection of [1/240] [1/360] [1/600] [1/720] <Insert ratio> of the wall height.

d. Floor Joist Framing:  Vertical deflection of 1/480 for live loads and l/360 for total loads of the span.

e. Roof Trusses:  Vertical deflection of [1/240] [1/360] of the span.

f. Scissor Roof Trusses:  Horizontal deflection of 1-1/4 inches (32 mm) <Insert dimension> at reactions.

g. Roof Rafter Framing:  Horizontal deflection of [1/240] [1/360] of the horizontally projected span.

h. Ceiling Joist Framing:  Vertical deflection of [1/240] [1/360] of the span.

i. <Insert deflection limits.>

3. Design framing systems to provide for movement of framing members without damage or overstressing, sheathing failure, connection failure, undue strain on fasteners and anchors, or other detrimental effects when subject to a maximum ambient temperature change of 120 deg F (67 deg C).

Retain subparagraph and associated subparagraph below for non-load-bearing and load-bearing walls if design responsibility for cold-formed framing is assigned to Contractor.  Indicate locations on Drawings if different movement is anticipated for different building elements.  If preferred, change deflection limits to ratios such as L/300 for floors and L/200 for roofs.

4. Design framing system to maintain clearances at openings, to allow for construction tolerances, and to accommodate live load deflection of primary building structure as follows:

a. Upward and downward movement of [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] [1-1/2 inches (38 mm)].

B. Cold-Formed Steel Framing, General:  Design according to AISI's "Standard for Cold-Formed Steel Framing - General Provisions."

Delete three subparagraphs below if not applicable.

1. Headers:  Design according to AISI's "Standard for Cold-Formed Steel Framing - Header Design."

Usually retain first subparagraph below, particularly for brick-veneer backup framing.

2. Design exterior non-load-bearing wall framing to accommodate horizontal deflection without regard for contribution of sheathing materials.

3. Roof Trusses:  Design according to AISI's "Standard for Cold-Formed Steel Framing - Truss Design."

1.4 SUBMITTALS

A. Product Data:  For each type of cold-formed metal framing product and accessory indicated.

B. LEED Submittal:

Retain subparagraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  An alternative method of complying with Credit MR 4.1 and MR 4.2 requirements is to retain requirement in Division 01 Section "Sustainable Design Requirements" that gives Contractor the option and responsibility for determining how Credit MR 4.1 and MR 4.2 requirements will be met.

1. Product Data for Credit MR 4.1[ and Credit MR 4.2]:  For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content.

a. Include statement indicating costs for each product having recycled content.

C. Shop Drawings:  Show layout, spacings, sizes, thicknesses, and types of cold-formed metal framing; fabrication; and fastening and anchorage details, including mechanical fasteners.  Show reinforcing channels, opening framing, supplemental framing, strapping, bracing, bridging, splices, accessories, connection details, and attachment to adjoining work.

Retain subparagraph below if cold-formed metal framing is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

1. For cold-formed metal framing indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements." and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For [professional engineer] [testing agency].

F. Product Test Reports:  From a qualified testing agency, unless otherwise stated, indicating that each of the following complies with requirements, based on evaluation of comprehensive tests for current products:

Edit list below and add other test reports if required.  Delete paragraph above and list below if not required.

1. Steel sheet.

2. Expansion anchors.

3. Power-actuated anchors.

4. Mechanical fasteners.

5. Vertical deflection clips.

6. Horizontal drift deflection clips

7. Miscellaneous structural clips and accessories.

Insert specific model code organization in paragraph below or revise if report must be from another source.

G. Research/Evaluation Reports:  For cold-formed metal framing.

1.5 QUALITY ASSURANCE

Retain paragraph below if retaining "Performance Requirements" Article.

A. Engineering Responsibility:  Preparation of Shop Drawings, design calculations, and other structural data by a qualified professional engineer.

Delete paragraph below if Contractor is not required to engage the services of a qualified professional engineer in "Submittals" Article.

B. Professional Engineer Qualifications:  A professional engineer who is legally qualified to practice in jurisdiction where Project is located and who is experienced in providing engineering services of the kind indicated.  Engineering services are defined as those performed for installations of cold-formed metal framing that are similar to those indicated for this Project in material, design, and extent.

Delete paragraph below if test reports from qualified independent testing agencies are not required; retain if Contractor selects testing agency.

C. Testing Agency Qualifications:  An independent testing agency, acceptable to authorities having jurisdiction, qualified according to ASTM E 329 to conduct the testing indicated.

Usually retain mill certifications or test reports from a qualified testing agency below.  Add option of test reports from in-house testing with calibrated test equipment, if permitted.  Add option for testing ductility if required.  See "Mill Certification" Paragraph in "Materials" Article in the Evaluations for more information.

D. Product Tests:  Mill certificates or data from a qualified independent testing agency[, or in-house testing with calibrated test equipment] indicating steel sheet complies with requirements, including base-metal thickness, yield strength, tensile strength, total elongation, chemical requirements,[ ductility,] and metallic-coating thickness.

Delete paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

E. Welding:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code--Steel," and AWS D1.3, "Structural Welding Code--Sheet Steel."

Delete paragraph below if no fire-resistance-rated units are required.

F. Fire-Test-Response Characteristics:  Where indicated, provide cold-formed metal framing identical to that of assemblies tested for fire resistance per ASTM E 119 by a testing and inspecting agency acceptable to authorities having jurisdiction.

Always retain paragraph below.

G. AISI Specifications and Standards:  Comply with AISI's "North American Specification for the Design of Cold-Formed Steel Structural Members" and its "Standard for Cold-Formed Steel Framing - General Provisions."

Retain two subparagraphs below, as applicable, if Project includes trusses or headers for load-bearing walls.

1. Comply with AISI's "Standard for Cold-Formed Steel Framing - Truss Design."

2. Comply with AISI's "Standard for Cold-Formed Steel Framing - Header Design."

Consider retaining paragraph below if Project is limited to one- and two-family residential construction, framing is fully detailed, and this AISI document is acceptable to authorities having jurisdiction.

H. Comply with AISI's "Standard for Cold-Formed Steel Framing - Prescriptive Method for One and Two Family Dwellings."

Delete paragraph below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 01.

I. Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 01 Section "Project Management and Coordination."

1.6 DELIVERY, STORAGE, AND HANDLING

A. Protect cold-formed metal framing from corrosion, deformation, and other damage during delivery, storage, and handling.

B. Store cold-formed metal framing, protect with a waterproof covering, and ventilate to avoid condensation.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering cold-formed metal framing that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide cold-formed metal framing by one of the following:

List below includes members of Steel Stud Manufacturers Association.

1. Allied Studco.

2. AllSteel Products, Inc.

3. California Expanded Metal Products Company.

4. Clark Steel Framing.

5. Consolidated Fabricators Corp.; Building Products Division.

6. Craco Metals Manufacturing, LLC.

7. Custom Stud, Inc.

8. Dale/Incor.

9. Design Shapes in Steel.

10. Dietrich Metal Framing; a Worthington Industries Company.

11. Formetal Co. Inc. (The).

12. Innovative Steel Systems.

13. MarinoWare; a division of Ware Industries.

14. Quail Run Building Materials, Inc.

15. SCAFCO Corporation.

16. Southeastern Stud & Components, Inc.

17. Steel Construction Systems.

18. Steeler, Inc.

19. Super Stud Building Products, Inc.

20. United Metal Products, Inc.

21. <Insert manufacturer's name.>

2.2 MATERIALS

Retain first paragraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation.  The Steel Recycling Institute indicates that steel sheet is made by the basic oxygen furnace method, which typically has 23 percent postconsumer recycled content and 1.5 percent preconsumer recycled content.

A. Recycled Content of Steel Products:  Provide products with an average recycled content of steel products so postconsumer recycled content plus one-half of preconsumer recycled content is not less than [25] <Insert number> percent.

B. Steel Sheet:  ASTM A 1003/A 1003M, Structural Grade, Type H, metallic coated, of grade and coating weight as follows:

Select minimum grade requirements from options in subparagraph below.  If more than one selection is required, indicate location of each on Drawings.

1. Grade:  [ST33H (ST230H)] [ST50H (ST340H)] [As required by structural performance] <Insert grade>.

Minimum coating requirement for Structural Grade, Type H steel is G60 or equivalent.  Retain first option in subparagraph below if ASTM A 1003/A 1003M's listing of minimum coating thicknesses is required.  This minimum coating designation assumes normal exposure conditions and construction practices.  When more severe exposure conditions are probable, for example, in coastal areas, consider specifying a heavier coating.  BIA recommends G90 (Z275) for stud backup applications.  Verify availability of heavier-coated steel.  If more than one selection is required, indicate location of each on Drawings.

2. Coating:  [G60 (Z180), A60 (ZF180), AZ50 (AZ150), or GF30 (ZGF90)] [G90 (Z275) or equivalent] <Insert coating weight>.

Retain paragraph below if specifying vertical deflection clips and drift clips.

C. Steel Sheet for [Vertical Deflection] [Drift] Clips:  ASTM A 653/A 653M, structural steel, zinc coated, of grade and coating as follows:

Select grade requirements from options in first subparagraph below.

1. Grade:  [50 (340), Class 1 or 2] [As required by structural performance].

2. Coating:  G90 (Z275).

2.3 LOAD-BEARING WALL FRAMING

Retain this Article if load-bearing steel studs are required.  Distinguish axial load-bearing framing from exterior non-load-bearing wall framing here or on Drawings.  Indicate stud and track web depth on Drawings or insert here.

A. Steel Studs:  Manufacturer's standard C-shaped steel studs, of web depths indicated, punched, with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.  If retaining different thicknesses for different components, indicate locations here or in framing articles below.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Flange widths vary with application.  If sheathing or masonry ties are required, consider minimum flange width of 1-5/8 inches (41 mm).  Sequence corresponds to new common flange width designators 137, 162, 200, and 250.

2. Flange Width:  [1-3/8 inches (35 mm)] [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)].

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

B. Steel Track:  Manufacturer's standard U-shaped steel track, of web depths indicated, unpunched, with straight flanges, and as follows:

Select one steel thickness from first subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)] [Matching steel studs].

2. Flange Width:  [1-1/4 inches (32 mm)] <Insert dimension if manufacturer's standard width is insufficient>.

C. Steel Box or Back-to-Back Headers:  Manufacturer's standard C-shapes used to form header beams, of web depths indicated, punched, with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.  If retaining different thicknesses for different locations, indicate locations here or in the framing articles below.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Flange widths vary with application; coordinate with wall width.

2. Flange Width:  [1-3/8 inches (35 mm)] [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)].

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

D. Steel Double-L Headers:  Manufacturer's standard L-shapes used to form header beams, of web depths indicated, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.  If retaining different thicknesses for different locations, indicate locations here or in framing articles below.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

First option in subparagraph below is minimum top flange width recognized by AISI's "Standard for Cold-Formed Steel Framing - Header Design." Coordinate with wall width.

2. Top Flange Width:  [1-1/2 inches (38 mm)] [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)].

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

2.4 EXTERIOR NON-LOAD-BEARING WALL FRAMING

Retain this Article if exterior non-load-bearing wall framing, sometimes called "curtain-wall" framing by manufacturers, is required.  Indicate stud and track web depth on Drawings or insert here.

A. Steel Studs:  Manufacturer's standard C-shaped steel studs, of web depths indicated, punched, with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Flange widths vary with application.  If sheathing or masonry ties are required, consider minimum flange width of 1-5/8 inches (41 mm).  Sequence corresponds to new common flange width designators 137, 162, 200, and 250.

2. Flange Width:  [1-3/8 inches (35 mm)] [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)].

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

B. Steel Track:  Manufacturer's standard U-shaped steel track, of web depths indicated, unpunched, with unstiffened flanges, and as follows:

Select one steel thickness from first subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)] [Matching steel studs].

2. Flange Width:  [1-1/4 inches (32 mm)] <Insert dimension if manufacturer's standard width is insufficient>.

Select one of three paragraphs and associated subparagraphs below for components to cope with vertical deflection of the primary structure.

Retain first paragraph and subparagraphs below if vertical deflection clips are required; revise to add displacement if deflection of primary structure is not indicated or Part 1 "Performance Requirements" Article is deleted.

C. Vertical Deflection Clips:  Manufacturer's standard [bypass] [head] clips, capable of accommodating upward and downward vertical displacement of primary structure through positive mechanical attachment to stud web.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Dietrich Metal Framing; a Worthington Industries Company.

b. MarinoWare, a division of Ware Industries.

c. SCAFCO Corporation

d. The Steel Network, Inc.

e. <Insert, in separate subparagraphs, manufacturer's name.>

Retain first paragraph and subparagraphs below if a proprietary single-leg deflection track is required.  Revise description, as applicable, if limiting types of single-leg track.

D. Single Deflection Track:  Manufacturer's single, deep-leg, U-shaped steel track; unpunched, with unstiffened flanges, of web depth to contain studs while allowing free vertical movement, with flanges designed to support horizontal and lateral loads and transfer them to the primary structure, and as follows:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. <Insert, in separate subparagraphs, manufacturer's name.>

Select one steel thickness from first subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 43, 54, 68, and 97 and obsolete 18-, 16-, 14-, and 12-gage designations.  Deflection track flange is usually designed to be thicker than corresponding studs to resist transverse loading.  Coordinate flange width with deflection of primary structure to ensure that structure does not bear on framing.

3. Minimum Base-Metal Thickness:  [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

4. Flange Width:  [1 inch (25 mm) plus the design gap for 1-story structures] [and] [1 inch (25 mm) plus twice the design gap for other applications] <Insert dimension>.

E. Double Deflection Tracks:  Manufacturer's double, deep-leg, U-shaped steel tracks, consisting of nested inner and outer tracks; unpunched, with unstiffened flanges.

Select one steel thickness from first subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 43, 54, 68, and 97 and obsolete 18-, 16-, 14-, and 12-gage designations.  Deflection track flange is usually designed to be thicker than corresponding studs to resist transverse loading.  Coordinate flange width with deflection of primary structure to ensure that structure does not bear on framing.

1. Outer Track:  Of web depth to allow free vertical movement of inner track, with flanges designed to support horizontal and lateral loads and transfer them to the primary structure, and as follows:

a. Minimum Base-Metal Thickness:  [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

b. Flange Width:  [1 inch (25 mm) plus the design gap for 1-story structures] [and] [1 inch (25 mm) plus twice the design gap for other applications] <Insert dimension>.

2. Inner Track:  Of web depth indicated, and as follows:

a. Minimum Base-Metal Thickness:  [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

b. Flange Width:  <Insert dimension equal to sum of outer deflection track flange width plus 1 inch (25 mm).>

Retain paragraph below if drift clips are required to accommodate horizontal and vertical deflection of the primary structure.

F. Drift Clips:  Manufacturer's standard bypass or head clips, capable of isolating wall stud from upward and downward vertical displacement and lateral drift of primary structure.

2.5 FLOOR JOIST FRAMING

Retain this Article if steel joists are required.  If joist and joist-track depth are not indicated, revise paragraphs below and add depth required.

A. Steel Joists:  Manufacturer's standard C-shaped steel joists, of web depths indicated, [unpunched,] [punched,] [punched, with enlarged service holes,] with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

Revise paragraph below to include descriptions of other related components, such as headers or other built-up members, at openings or other terminations.

B. Steel Joist Track:  Manufacturer's standard U-shaped steel joist track, of web depths indicated, unpunched, with unstiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)] [Matching steel joists].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

2.6 ROOF TRUSSES

Retain first option in paragraph below for predominant method of fabricating trusses from proprietary shapes for manufacturer's proprietary trusses.  Retain second option, now the exception, if C-shapes are proposed.  Besides several of the listed framing manufacturers, Aegis Metal Framing, Alpine Engineered Products, Mitek Industries, Nucon Steel,Tri- Chord, and others produce trusses.

A. Roof Truss Members:  Manufacturer's standard[-shape steel sections] [C-shaped steel sections, of web depths indicated, unpunched, with stiffened flanges].

Delete remainder of this Article if retaining first option in paragraph above and manufacturer designs roof trusses.

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

Insert calculated section properties for top and bottom chords and each web member.  Indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

2.7 ROOF-RAFTER FRAMING

Retain this Article if steel rafters are required.  If rafter web depth is not indicated, revise paragraph below and add depth required.

A. Steel Rafters:  Manufacturer's standard C-shaped steel sections, of web depths indicated, unpunched, with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

Revise paragraph below to include descriptions of built-up members, such as ridges, collar ties, rafter braces, if general description will not suffice.

B. Built-up Members:  Built-up members of manufacturer's standard C-shaped steel section, with stiffened flanges, nested into a U-shaped steel section joist track, with unstiffened flanges; unpunched; of web depths indicated; and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)] [Matching steel rafters].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

2.8 CEILING JOIST FRAMING

Retain this Article if steel joists are required.  If joist and joist-track depth is not indicated, revise paragraph below and add depth required.

A. Steel Ceiling Joists:  Manufacturer's standard C-shaped steel sections, of web depths indicated, [unpunched,] [punched with enlarged service holes,] with stiffened flanges, and as follows:

Select one steel thickness from subparagraph below or revise to suit Project.  Sequence corresponds to new common thickness designators 33, 43, 54, 68, and 97 and obsolete 20-, 18-, 16-, 14-, and 12-gage designations.

1. Minimum Base-Metal Thickness:  [0.0329 inch (0.84 mm)] [0.0428 inch (1.09 mm)] [0.0538 inch (1.37 mm)] [0.0677 inch (1.72 mm)] [0.0966 inch (2.45 mm)].

Select one flange width from subparagraph below.  Flange widths may vary with application.  Sequence corresponds to new common flange width designators 162, 200, and 250.

2. Flange Width:  [1-5/8 inches (41 mm)] [2 inches (51 mm)] [2-1/2 inches (63 mm)], minimum.

Delete subparagraph below if assigning design responsibility to Contractor in Part 1 "Performance Requirements" Article.  If retaining, indicate whether design is based on gross or effective section properties.

3. Section Properties:  <Insert minimum allowable calculated section modulus, moment of inertia, and allowable moment.>

2.9 FRAMING ACCESSORIES

Revise minimum yield strength of accessories as required.

A. Fabricate steel-framing accessories from steel sheet, ASTM A 1003/A 1003M, Structural Grade, Type H, metallic coated, of same grade and coating weight used for framing members.

B. Provide accessories of manufacturer's standard thickness and configuration, unless otherwise indicated, as follows:

Revise list below to suit Project.

1. Supplementary framing.

2. Bracing, bridging, and solid blocking.

3. Web stiffeners.

4. Anchor clips.

5. End clips.

6. Foundation clips.

7. Gusset plates.

8. Stud kickers, knee braces, and girts.

9. Joist hangers and end closures.

10. Hole reinforcing plates.

11. Backer plates.

2.10 ANCHORS, CLIPS, AND FASTENERS

Delete paragraph below if rolled steel shapes and clips are not required or are specified in another Section.

A. Steel Shapes and Clips:  ASTM A 36/A 36M, zinc coated by hot-dip process according to ASTM A 123/A 123M.

Select grade of anchor bolt, head type, and type of protective coating from paragraph below.  Revise if using high-strength, low-alloy anchor bolts.

B. Anchor Bolts:  ASTM F 1554, Grade [36] [55], threaded carbon-steel [hex-headed bolts] [headless, hooked bolts] [headless bolts, with encased end threaded,] and carbon-steel nuts; and flat, hardened-steel washers; zinc coated by [hot-dip process according to ASTM A 153/A 153M, Class C] [mechanically deposition according to ASTM B 695, Class 50].

Retain paragraph below if expansion anchors are acceptable.  Verify safety factor with Project's structural engineer.  Revise as required or insert specific load requirements and names of acceptable products.

C. Expansion Anchors:  Fabricated from corrosion-resistant materials, with capability to sustain, without failure, a load equal to 5 times design load, as determined by testing per ASTM E 488 conducted by a qualified independent testing agency.

Retain first paragraph below if power-actuated fasteners are acceptable.  Verify safety factor with Project's structural engineer.

D. Power-Actuated Anchors:  Fastener system of type suitable for application indicated, fabricated from corrosion-resistant materials, with capability to sustain, without failure, a load equal to 10 times design load, as determined by testing per ASTM E 1190 conducted by a qualified independent testing agency.

E. Mechanical Fasteners:  ASTM C 1513, corrosion-resistant-coated, self-drilling, self-tapping steel drill screws.

1. Head Type:  Low-profile head beneath sheathing, manufacturer's standard elsewhere.

F. Welding Electrodes:  Comply with AWS standards.

2.11 MISCELLANEOUS MATERIALS

A. Galvanizing Repair Paint:  [SSPC-Paint 20 or DOD-P-21035] [ASTM A 780].

Select appropriate grout from first two paragraphs below if concrete or masonry substrates require leveling before setting track or prefabricated assemblies.

B. Cement Grout:  Portland cement, ASTM C 150, Type I; and clean, natural sand, ASTM C 404.  Mix at ratio of 1 part cement to 2-1/2 parts sand, by volume, with minimum water required for placement and hydration.

C. Nonmetallic, Nonshrink Grout:  Premixed, nonmetallic, noncorrosive, nonstaining grout containing selected silica sands, portland cement, shrinkage-compensating agents, and plasticizing and water-reducing agents, complying with ASTM C 1107, with fluid consistency and 30-minute working time.

D. Shims:  Load bearing, high-density multimonomer plastic, nonleaching.

E. Sealer Gaskets:  Closed-cell neoprene foam, 1/4 inch (6.4 mm) thick, selected from manufacturer's standard widths to match width of bottom track or rim track members.

2.12 FABRICATION

Retain this Article for examples of shop or field fabrication including panelized load and non-load-bearing walls and roof trusses.

A. Fabricate cold-formed metal framing and accessories plumb, square, and true to line, and with connections securely fastened, according to referenced AISI's specifications and standards, manufacturer's written instructions, and requirements in this Section.

1. Fabricate framing assemblies using jigs or templates.

2. Cut framing members by sawing or shearing; do not torch cut.

3. Fasten cold-formed metal framing members by welding, screw fastening, clinch fastening, or riveting as standard with fabricator.  Wire tying of framing members is not permitted.

a. Comply with AWS D1.3 requirements and procedures for welding, appearance and quality of welds, and methods used in correcting welding work.

Retain subparagraph above and subparagraph below if using mechanical fasteners.

b. Locate mechanical fasteners and install according to Shop Drawings, with screw penetrating joined members by not less than three exposed screw threads.

Retain subparagraph below if fabricated assemblies include other materials or revise to suit Project.

4. Fasten other materials to cold-formed metal framing by welding, bolting, or screw fastening, according to Shop Drawings.

B. Reinforce, stiffen, and brace framing assemblies to withstand handling, delivery, and erection stresses.  Lift fabricated assemblies to prevent damage or permanent distortion.

Revise paragraph and subparagraphs below to suit Project.

C. Fabrication Tolerances:  Fabricate assemblies level, plumb, and true to line to a maximum allowable tolerance variation of 1/8 inch in 10 feet (1:960) and as follows:

1. Spacing:  Space individual framing members no more than plus or minus 1/8 inch (3 mm) from plan location.  Cumulative error shall not exceed minimum fastening requirements of sheathing or other finishing materials.

2. Squareness:  Fabricate each cold-formed metal framing assembly to a maximum out-of-square tolerance of 1/8 inch (3 mm).

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine supporting substrates and abutting structural framing for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

Delete two paragraphs below if sprayed fire-resistive materials are not required or applicable.

A. Before sprayed fire-resistive materials are applied, attach continuous angles, supplementary framing, or tracks to structural members indicated to receive sprayed fire-resistive materials.

B. After applying sprayed fire-resistive materials, remove only as much of these materials as needed to complete installation of cold-formed framing without reducing thickness of fire-resistive materials below that are required to obtain fire-resistance rating indicated.  Protect remaining fire-resistive materials from damage.

Retain paragraph below if joists, rafters, trusses, or bottom track of load-bearing walls requires a uniform-bearing surface on concrete or masonry construction.

C. Install load bearing shims or grout between the underside of wall bottom track or rim track and the top of foundation wall or slab at stud or joist locations to ensure a uniform bearing surface on supporting concrete or masonry construction.

Retain paragraph below if isolating framing from contact with concrete or masonry construction.

D. Install sealer gaskets to isolate the underside of wall bottom track or rim track and the top of foundation wall or slab at stud or joist locations.

3.3 INSTALLATION, GENERAL

Retain this Article with each specific framing classification in articles farther below.

A. Cold-formed metal framing may be shop or field fabricated for installation, or it may be field assembled.

B. Install cold-formed metal framing according to AISI's "Standard for Cold-Formed Steel Framing - General Provisions" and to manufacturer's written instructions unless more stringent requirements are indicated.

Retain first paragraph and subparagraph below if shop or field fabricating wall panels.

C. Install shop- or field-fabricated, cold-formed framing and securely anchor to supporting structure.

1. Screw, bolt, or weld wall panels at horizontal and vertical junctures to produce flush, even, true-to-line joints with maximum variation in plane and true position between fabricated panels not exceeding 1/16 inch (1.6 mm).

D. Install cold-formed metal framing and accessories plumb, square, and true to line, and with connections securely fastened.

1. Cut framing members by sawing or shearing; do not torch cut.

2. Fasten cold-formed metal framing members by welding, screw fastening, clinch fastening, or riveting.  Wire tying of framing members is not permitted.

a. Comply with AWS D1.3 requirements and procedures for welding, appearance and quality of welds, and methods used in correcting welding work.

Retain subparagraph above and subparagraph below if using mechanical fasteners.

b. Locate mechanical fasteners and install according to Shop Drawings, and complying with requirements for spacing, edge distances, and screw penetration.

E. Install framing members in one-piece lengths unless splice connections are indicated for track or tension members.

F. Install temporary bracing and supports to secure framing and support loads comparable in intensity to those for which structure was designed.  Maintain braces and supports in place, undisturbed, until entire integrated supporting structure has been completed and permanent connections to framing are secured.

Include details on Drawings showing expansion- and control-joint construction and locations.

G. Do not bridge building expansion and control joints with cold-formed metal framing.  Independently frame both sides of joints.

Retain first paragraph below if insulation for exterior framing is required.

H. Install insulation, specified in Division 07 Section "Thermal Insulation," in built-up exterior framing members, such as headers, sills, boxed joists, and multiple studs at openings, that are inaccessible on completion of framing work.

I. Fasten hole reinforcing plate over web penetrations that exceed size of manufacturer's standard punched openings.

Revise paragraph and subparagraph below to suit Project.  Coordinate with limitations of subsequent finish materials.

J. Erection Tolerances:  Install cold-formed metal framing level, plumb, and true to line to a maximum allowable tolerance variation of 1/8 inch in 10 feet (1:960) and as follows:

1. Space individual framing members no more than plus or minus 1/8 inch (3 mm) from plan location.  Cumulative error shall not exceed minimum fastening requirements of sheathing or other finishing materials.

3.4 LOAD-BEARING WALL INSTALLATION

If this Article is required, retain with "Installation, General" Article.

A. Install continuous top and bottom tracks sized to match studs.  Align tracks accurately and securely anchor at corners and ends, and at spacings as follows:

Select anchor spacing in subparagraph below to suit requirements and type of anchor.

1. Anchor Spacing:  [24 inches (610 mm)] [32 inches (813 mm)] [To match stud spacing] [As shown on Shop Drawings].

B. Squarely seat studs against top and bottom tracks with gap not exceeding of 1/8 inch (3 mm) between the end of wall framing member and the web of track.  Fasten both flanges of studs to top and bottom tracks.  Space studs as follows:

1. Stud Spacing:  [12 inches (305 mm)] [16 inches (406 mm)] [19.2 inches (488 mm)] [24 inches (610 mm)] [As indicated].

Select from options in subparagraph above for IP spacings and equivalent SI (metric) dimensions or from options in subparagraph below if metric spacings are required.

2. Stud Spacing:  [300 mm] [400 mm] [600 mm] [As indicated].

C. Set studs plumb, except as needed for diagonal bracing or required for nonplumb walls or warped surfaces and similar configurations.

D. Align studs vertically where floor framing interrupts wall-framing continuity.  Where studs cannot be aligned, continuously reinforce track to transfer loads.

E. Align floor and roof framing over studs.  Where framing cannot be aligned, continuously reinforce track to transfer loads.

F. Anchor studs abutting structural columns or walls, including masonry walls, to supporting structure as indicated.

G. Install headers over wall openings wider than stud spacing.  Locate headers above openings as indicated.  Fabricate headers of compound shapes indicated or required to transfer load to supporting studs, complete with clip-angle connectors, web stiffeners, or gusset plates.

1. Frame wall openings with not less than a double stud at each jamb of frame as indicated on Shop Drawings.  Fasten jamb members together to uniformly distribute loads.

2. Install runner tracks and jack studs above and below wall openings.  Anchor tracks to jamb studs with clip angles or by welding, and space jack studs same as full-height wall studs.

H. Install supplementary framing, blocking, and bracing in stud framing indicated to support fixtures, equipment, services, casework, heavy trim, furnishings, and similar work requiring attachment to framing.

1. If type of supplementary support is not indicated, comply with stud manufacturer's written recommendations and industry standards in each case, considering weight or load resulting from item supported.

Select spacing of bridging from options in paragraph below or revise to suit Project.

I. Install horizontal bridging in stud system, spaced [48 inches (1220 mm)] [as indicated] [as indicated on Shop Drawings].  Fasten at each stud intersection.

Select type of bridging required from three subparagraphs below or revise to suit Project.  Add locations if more than one type of bridging is required.  Add minimum size of flat steel strap, such as 1-1/2 by 0.0329 inch (38 by 0.84 mm), if default size is required.

1. Bridging:  Cold-rolled steel channel, welded or mechanically fastened to webs of punched studs with a minimum of 2 screws into each flange of the clip angle for framing members up to 6 inches (150 mm) deep.

2. Bridging:  Combination of flat, taut, steel sheet straps of width and thickness indicated and stud-track solid blocking of width and thickness to match studs.  Fasten flat straps to stud flanges and secure solid blocking to stud webs or flanges.

3. Bridging:  Proprietary bridging bars installed according to manufacturer's written instructions.

Delete first paragraph below if not required.  Revise bracing type and reinforcement at terminations to suit Project.  Description below usually applies to shear walls.  Add track reinforcing or gusset plate requirements to Drawings if applicable, particularly for shear walls.  If sheathing provides bracing to one or both stud flanges, revise to suit Project.

J. Install steel sheet diagonal bracing straps to both stud flanges, terminate at and fasten to reinforced top and bottom tracks.  Fasten clip-angle connectors to multiple studs at ends of bracing and anchor to structure.

K. Install miscellaneous framing and connections, including supplementary framing, web stiffeners, clip angles, continuous angles, anchors, and fasteners, to provide a complete and stable wall-framing system.

3.5 EXTERIOR NON-LOAD-BEARING WALL INSTALLATION

If this Article is required, retain with "Installation, General" Article.

A. Install continuous tracks sized to match studs.  Align tracks accurately and securely anchor to supporting structure as indicated.

Select fastening of studs to top track only if required.  Do not fasten studs to deflection track, such as in infill wall framing.

B. Fasten both flanges of studs to[ top and] bottom track, unless otherwise indicated.  Space studs as follows:

1. Stud Spacing:  [12 inches (305 mm)] [16 inches (406 mm)] [19.2 inches (488 mm)] [24 inches (610 mm)] [As indicated].

Select from options in subparagraph above for IP spacings and equivalent SI (metric) dimensions or from options in subparagraph below if metric spacings are required.

2. Stud Spacing:  [300 mm] [400 mm] [480 mm] [600 mm] [As indicated].

C. Set studs plumb, except as needed for diagonal bracing or required for nonplumb walls or warped surfaces and similar requirements.

Indicate isolation details on Drawings or insert detailed description here.

D. Isolate non-load-bearing steel framing from building structure to prevent transfer of vertical loads while providing lateral support.

Retain one of first two subparagraphs below if using deflection track with infill wall framing.  Delete both subparagraphs and retain third if deflection clips are required for bypassing or infill wall framing.  Vertical deflection clips are used if wall is stick built or panelized.  Single deflection track is used if stud wall is stick built; double deflection track is used with wall panels.  Drift clips may be used in seismic areas.

1. Install single-leg deflection tracks and anchor to building structure.

2. Install double deep-leg deflection tracks and anchor outer track to building structure.

3. Connect vertical deflection clips to [bypassing] [infill] studs and anchor to building structure.

4. Connect drift clips to cold formed metal framing and anchor to building structure.

E. Install horizontal bridging in wall studs, spaced in rows indicated on Shop Drawings but not more than 48 inches (1220 mm) apart.  Fasten at each stud intersection.

Retain subparagraph and associated subparagraph below if single deflection track is required.

1. Top Bridging for Single Deflection Track:  Install row of horizontal bridging within [12 inches (305 mm)] [18 inches (450 mm)] of single deflection track.  Install a combination of flat, taut, steel sheet straps of width and thickness indicated and stud or stud-track solid blocking of width and thickness matching studs.  Fasten flat straps to stud flanges and secure solid blocking to stud webs or flanges.

a. Install solid blocking at [96-inch (2440-mm) centers] [centers indicated] [centers indicated on Shop Drawings].

Select type of bridging required from three subparagraphs below or revise to suit Project.  Add locations if more than one type of bridging is required.  Add minimum size of flat steel strap, such as 1-1/2 by 0.0329 inch (38 by 0.84 mm), if default size is required.

2. Bridging:  Cold-rolled steel channel, welded or mechanically fastened to webs of punched studs.

3. Bridging:  Combination of flat, taut, steel sheet straps of width and thickness indicated and stud-track solid blocking of width and thickness to match studs.  Fasten flat straps to stud flanges and secure solid blocking to stud webs or flanges.

4. Bridging:  Proprietary bridging bars installed according to manufacturer's written instructions.

F. Install miscellaneous framing and connections, including stud kickers, web stiffeners, clip angles, continuous angles, anchors, fasteners, and stud girts, to provide a complete and stable wall-framing system.

3.6 JOIST INSTALLATION

If this Article is required, retain with "Installation, General" Article.

A. Install perimeter joist track sized to match joists.  Align and securely anchor or fasten track to supporting structure at corners, ends, and spacings indicated on Shop Drawings.

B. Install joists bearing on supporting frame, level, straight, and plumb; adjust to final position, brace, and reinforce.  Fasten joists to both flanges of joist track.

Revise minimum end bearing in first subparagraph below if joists bearing on flange of joist track are acceptable.  Web stiffeners will usually be required to reinforce joist web.

1. Install joists over supporting frame with a minimum end bearing of 1-1/2 inches (38 mm).

2. Reinforce ends and bearing points of joists with web stiffeners, end clips, joist hangers, steel clip angles, or steel-stud sections as indicated on Shop Drawings.

C. Space joists not more than 2 inches (51 mm) from abutting walls, and as follows:

1. Joist Spacing:  [12 inches (305 mm)] [16 inches (406 mm)] [19.2 inches (488 mm)] [24 inches (610 mm)] [As indicated].

Select from options in subparagraph above for IP spacings and equivalent SI (metric) dimensions or from options in subparagraph below if metric spacings are required.

2. Joist Spacing:  [300 mm] [400 mm] [480 mm] [600 mm] [As indicated].

D. Frame openings with built-up joist headers consisting of joist and joist track, nesting joists, or another combination of connected joists if indicated.

E. Install joist reinforcement at interior supports with single, short length of joist section located directly over interior support, with lapped joists of equal length to joist reinforcement, or as indicated[ on Shop Drawings].

1. Install web stiffeners to transfer axial loads of walls above.

F. Install bridging at intervals indicated[ on Shop Drawings].  Fasten bridging at each joist intersection as follows:

Select type of bridging required from two subparagraphs below or revise to suit Project.  Add locations if more than one type of bridging is required.  Add minimum size of flat steel strap, such as 1-1/2 by 0.0329 inch (38 by 0.84 mm), if default size is required.  Revise if also fastening flat steel strap bridging to top flange of joists.

1. Bridging:  Joist-track solid blocking of width and thickness indicated, secured to joist webs.

2. Bridging:  Combination of flat, taut, steel sheet straps of width and thickness indicated and joist-track solid blocking of width and thickness indicated.  Fasten flat straps to bottom flange of joists and secure solid blocking to joist webs.

G. Secure joists to load-bearing interior walls to prevent lateral movement of bottom flange.

H. Install miscellaneous joist framing and connections, including web stiffeners, closure pieces, clip angles, continuous angles, hold-down angles, anchors, and fasteners, to provide a complete and stable joist-framing assembly.

3.7 TRUSS INSTALLATION

If this Article is required, retain with "Installation, General" Article.

A. Install, bridge, and brace trusses according to Shop Drawings and requirements in this Section.

B. Truss Spacing:  [16 inches (406 mm)] [19.2 inches (488 mm)] [24 inches (610 mm)] [32 inches (813 mm)] [48 inches (1220 mm)] [As indicated].

Select from options in paragraph above for IP spacings and equivalent SI (metric) dimensions or from options in first paragraph below if metric spacings are required.

C. Truss Spacing:  [400 mm] [480 mm] [600 mm] [800 mm] [1200 mm].

D. Do not alter, cut, or remove framing members or connections of trusses.

E. Erect trusses with plane of truss webs plumb and parallel to each other, align, and accurately position at spacings indicated.

F. Erect trusses without damaging framing members or connections.

Retain first paragraph below if trusses bear on load-bearing, cold-formed wall framing.

G. Align webs of bottom chords and load-bearing studs or continuously reinforce track to transfer loads to structure.  Anchor trusses securely at all bearing points.

H. Install continuous bridging and permanently brace trusses as indicated[ on Shop Drawings and designed according to LGSEA's Technical Note 551e, "Design Guide for Permanent Bracing of Cold-Formed Steel Trusses."][.]

Insert additional article titles here if other framing classifications warrant more detailed installation requirements than those in "Installation, General" Article.

3.8 FIELD QUALITY CONTROL

Retain this Article if field testing and inspecting are required.  Provisions below include shop and field testing and inspecting.  Revise and add a "Source Quality Control" Article to end of Part 2 if separate shop and field testing and inspecting are required.  Revise first paragraph below to include code-mandated special inspections or revise if Contractor engages testing agency.

A. Testing:  Owner will engage a qualified independent testing and inspecting agency to perform field tests and inspections and prepare test reports.

B. Field and shop welds will be subject to testing and inspecting.

C. Testing agency will report test results promptly and in writing to Contractor and Architect.

D. Remove and replace work where test results indicate that it does not comply with specified requirements.

E. Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

3.9 REPAIRS AND PROTECTION

Retain first paragraph below if galvanized framing is in this Section.

A. Galvanizing Repairs:  Prepare and repair damaged galvanized coatings on fabricated and installed cold-formed metal framing with galvanized repair paint according to ASTM A 780 and manufacturer's written instructions.

B. Provide final protection and maintain conditions, in a manner acceptable to manufacturer and Installer, that ensure that cold-formed metal framing is without damage or deterioration at time of Substantial Completion.

END OF SECTION 054000

COLD-FORMED METAL FRAMING
054000 - 1

