Copyright 2005 AIA
MASTERSPEC Full Length
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 210533 - HEAT TRACING FOR FIRE-SUPPRESSION PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes heat tracing with the following electric heating cables:

1. Plastic insulated, series resistance.

2. Self-regulating, parallel resistance.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Heat Tracing for Plumbing Piping."

2. Division 23 Section "Heat Tracing for HVAC Piping."

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.

1. Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required.

B. Shop Drawings:  For electric heating cable.  Include plans, sections, details, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and Maintenance Data:  For electric heating cables to include in operation and maintenance manuals.

E. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties for electric heating cable and insert number in subparagraph below.

1. Warranty Period:  [10] [15] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this Article for pipe-mounting freeze protection.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Delta-Therm Corporation.

2. Easy Heat Inc.

3. NUHEAT.

4. Orbit Manufacturing.

5. Pyrotenax; a division of Tyco Thermal Controls.

6. Raychem; a division of Tyco Thermal Controls.

7. WarmlyYours.com Inc.

8. Watts Radiant Inc.

9. <Insert manufacturer's name.>

D. Comply with IEEE 515.1.

E. Heating Element:  Single- or dual-stranded resistor wire.  Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

F. Electrical Insulating Jacket:  Minimum 4.0-mil (0.10-mm) Kapton with silicone jacket or Tefzel.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

G. Cable Cover:  Aluminum braid[ and silicone or Hylar outer jacket].

H. Maximum Operating Temperature:  [300 deg F (150 deg C)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

I. Capacities and Characteristics:

1. Maximum Heat Output:  [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert heat output>.

2. Piping Diameter:  <Insert NPS (DN).>

3. Number of Parallel Cables:  <Insert number.>

4. Spiral Wrap Pitch:  <Insert inches (mm).>

Verify available voltages and heat-output ratings with specified manufacturer.

5. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

6. Phase:  <Insert value.>

7. Hertz:  <Insert value.>

8. Full-Load Amperes:  <Insert value.>

9. Minimum Circuit Ampacity:  <Insert value.>

10. Maximum Overcurrent Protection:  <Insert value.>

2.2 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain this Article for pipe-mounting freeze protection.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. BH Thermal Corporation.

2. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

3. Delta-Therm Corporation.

4. Easy Heat Inc.

5. Nelson Heat Trace.

6. Pyrotenax; a division of Tyco Thermal Controls.

7. Raychem; a division of Tyco Thermal Controls.

8. Thermon Manufacturing Co.

9. Trasor Corp.

10. <Insert manufacturer's name.>

D. Heating Element:  Pair of parallel No. [16] [18] AWG, [tinned] [nickel-coated] stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length.  Terminate with waterproof, factory-assembled nonheating leads with connectors at one end, and seal the opposite end watertight.  Cable shall be capable of crossing over itself once without overheating.

E. Electrical Insulating Jacket:  Flame-retardant polyolefin.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover:  [Tinned-copper] [Stainless-steel] braid[, and polyolefin outer jacket with UV inhibitor].

G. Maximum Operating Temperature (Power On):  [150 deg F (65 deg C)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping in first paragraph below.

H. Maximum Exposure Temperature (Power Off):  [185 deg F (85 deg C)] <Insert temperature>.

I. Maximum Operating Temperature:  [300 deg F (150 deg C)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

J. Capacities and Characteristics:

1. Maximum Heat Output:  [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert heat output>.

2. Piping Diameter:  <Insert NPS (DN).>

3. Number of Parallel Cables:  <Insert number.>

4. Spiral Wrap Pitch:  <Insert inches (mm).>

Verify available voltages and heat-output ratings with specified manufacturer.

5. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

6. Phase:  <Insert value.>

7. Hertz:  <Insert value.>

8. Full-Load Amperes:  <Insert value.>

9. Minimum Circuit Ampacity:  <Insert value.>

10. Maximum Overcurrent Protection:  <Insert value.>

2.3 CONTROLS

A. Remote bulb unit with adjustable temperature range from [30 to 50 deg F (minus 1 to plus 10 deg C)] <Insert range>.

B. Snap action; open-on-rise, single-pole switch with minimum current rating adequate for connected cable.

C. Remote bulb on capillary, resistance temperature device, or thermistor for directly sensing pipe-wall temperature.

D. Corrosion-resistant, waterproof control enclosure.

2.4 ACCESSORIES

A. Cable Installation Accessories:  Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

B. Warning Tape:  Continuously printed "Electrical Tracing"; vinyl, at least 3 mils (0.08 mm) thick, and with pressure-sensitive, permanent, waterproof, self-adhesive back.

1. Width for Markers on Pipes with OD, Including Insulation, Less Than 6 Inches (150 mm):  3/4 inch (19 mm) minimum.

2. Width for Markers on Pipes with OD, Including Insulation, 6 Inches (150 mm) or Larger:  1-1/2 inches (38 mm) minimum.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine surfaces and substrates to receive electric heating cables for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Ensure surfaces and pipes in contact with electric heating cables are free of burrs and sharp protrusions.

2. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install electric heating cable across expansion joints according to manufacturer's written recommendations using slack cable to allow movement without damage to cable.

B. Install electric heating cables after piping has been tested and before insulation is installed.

C. Install electric heating cables according to IEEE 515.1.

D. Install insulation over piping with electric cables according to Division 21 Section "Fire-Suppression Systems Insulation."

E. Install warning tape on piping insulation where piping is equipped with electric heating cables.

F. Set field-adjustable switches and circuit-breaker trip ranges.

G. Protect installed heating cables, including nonheating leads, from damage.

3.3 CONNECTIONS

A. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

B. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Testing:  Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

1. Test cables for electrical continuity and insulation integrity before energizing.

2. Test cables to verify rating and power input.  Energize and measure voltage and current simultaneously.

B. Repeat tests for continuity, insulation resistance, and input power after applying thermal insulation on pipe-mounting cables.

C. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 210533

	HEAT TRACING FOR FIRE-SUPPRESSION PIPING
	210533 - 1



