Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211100 - FACILITY FIRE-SUPPRESSION WATER-SERVICE PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes fire-suppression water-service piping and related components outside the building [and service entrance piping through floor into the building] [and service entrance piping through wall into the building].

Utility companies usually provide water meters and bill charges directly or through Contractor to Owner.  Contact utility company serving the site for information.  Delete first paragraph below if water meters are provided by utility company or Contractor.  If utility company furnishes water meters, identify the company here, specify what it will do,  and revise text to suit Project.

B. Utility-furnished products include water meters that will be furnished to the site, ready for installation.

C. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 21 Section "Fire-Suppression Standpipes" for fire-suppression standpipes inside the building.

2. Division 21 Section "Wet-Pipe Sprinkler Systems" for wet-pipe fire-suppression sprinkler systems inside the building.

3. Division 21 Section "Dry-Pipe Sprinkler Systems" for dry-pipe fire-suppression sprinkler systems inside the building.

4. Division 21 Section "Foam-Water Systems" for AFFF piping.

5. Division 21 Section "[Electric-Drive, Centrifugal Fire Pumps] [Diesel-Drive, Centrifugal Fire Pumps] [Electric-Drive, Vertical-Turbine Fire Pumps] [Diesel-Drive, Vertical-Turbine Fire Pumps]" for fire pumps, pressure-maintenance pumps, and controllers.

1.3 SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.

B. Shop Drawings:

1. Detail precast concrete vault assemblies and indicate dimensions, method of field assembly, and components.

Retain subparagraph below if equipment includes wiring.

2. Wiring Diagrams:  For power, signal, and control wiring.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  For piping and specialties including relation to other services in same area, drawn to scale.  Show piping and specialty sizes and valves, meter and specialty locations, and elevations.

D. Field quality-control reports.

1.4 QUALITY ASSURANCE

Retain and revise first paragraph below to suit Project, or delete if not applicable.

A. Regulatory Requirements:

1. Comply with requirements of utility company supplying water.  Include tapping of water mains and backflow prevention.

2. Comply with standards of authorities having jurisdiction for fire-suppression water-service piping, including materials, hose threads, installation, and testing.

B. Piping materials shall bear label, stamp, or other markings of specified testing agency.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Comply with the "Approval Guide," published by FM Global, or UL's "Fire Protection Equipment Directory" for fire-service-main products.

E. NFPA Compliance:  Comply with NFPA 24 for materials, installations, tests, flushing, and valve and hydrant supervision for fire-suppression water-service piping.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Preparation for Transport:  Prepare valves, including fire hydrants, according to the following:

1. Ensure that valves are dry and internally protected against rust and corrosion.

2. Protect valves against damage to threaded ends and flange faces.

3. Set valves in best position for handling.  Set valves closed to prevent rattling.

B. During Storage:  Use precautions for valves, including fire hydrants, according to the following:

1. Do not remove end protectors unless necessary for inspection; then reinstall for storage.

2. Protect from weather.  Store indoors and maintain temperature higher than ambient dew point temperature.  Support off the ground or pavement in watertight enclosures when outdoor storage is necessary.

C. Handling:  Use sling to handle valves and fire hydrants if size requires handling by crane or lift.  Rig valves to avoid damage to exposed parts.  Do not use handwheels or stems as lifting or rigging points.

D. Deliver piping with factory-applied end caps.  Maintain end caps through shipping, storage, and handling to prevent pipe-end damage and to prevent entrance of dirt, debris, and moisture.

E. Protect stored piping from moisture and dirt.  Elevate above grade.  Do not exceed structural capacity of floor when storing inside.

F. Protect flanges, fittings, and specialties from moisture and dirt.

G. Store plastic piping protected from direct sunlight.  Support to prevent sagging and bending.

1.6 PROJECT CONDITIONS

Retain this article if interruption of existing water-distribution service is required.

A. Interruption of Existing Fire-Suppression Water-Service Piping:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water-distribution service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of service.

2. Do not proceed with interruption of service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.7 COORDINATION

Revise this article to suit Project if new fire-suppression water-service piping will connect to other on-site water-distribution piping.

A. Coordinate connection to water main with utility company.

PART 2 -  PRODUCTS

First five articles below include examples of materials used for water-distribution piping.  See "Writing Guide" Article in the Evaluations.

2.1 COPPER TUBE AND FITTINGS

Tube in first paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

A. Soft Copper Tube:  [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, annealed temper.

Tube in first paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

B. Hard Copper Tube:  [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, drawn temper.

C. Copper, Solder-Joint Fittings:  ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint pressure type.  Furnish only wrought-copper fittings if indicated.

D. Copper, Pressure-Seal Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Viega; Plumbing & Heating Systems.

b. <Insert manufacturer's name>.

2. Standard:  UL 213.

3. NPS 2 (DN 50) and Smaller:  Wrought-copper fitting with EPDM O-ring seal in each end.

4. NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Bronze fitting with stainless-steel grip ring and EPDM O-ring seal in each end.

Flanges in first paragraph below are available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

E. Bronze Flanges:  ASME B16.24, Class 150, with solder-joint end.  Furnish Class 300 flanges if required to match piping.

Unions in paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).  NFPA 13 limits unions to NPS 2 (DN 50) and smaller.

F. Copper Unions:  MSS SP-123, cast-copper-alloy, hexagonal-stock body with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

2.2 DUCTILE-IRON PIPE AND FITTINGS

Ductile-iron pipe is intended for fire-suppression water-service-piping outside the building and underslab within the building.

Pipe in first paragraph below is available in NPS 3 to NPS 24 (DN 80 to DN 600).

A. Grooved-Joint, Ductile-Iron Pipe:  AWWA C151, with cut, rounded-grooved ends.

Pipe in first paragraph below is available in NPS 3 to NPS 24 (DN 80 to DN 600).

B. Mechanical-Joint, Ductile-Iron Pipe:  AWWA C151, with mechanical-joint bell and plain spigot end.

Pipe in first paragraph below is available in NPS 3 to NPS 48 (DN 80 to DN 1200).

C. Push-on-Joint, Ductile-Iron Pipe:  AWWA C151, with push-on-joint bell and plain spigot end.

D. Grooved-End, Ductile-Iron Pipe Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Shurjoint Piping Products.

c. Star Pipe Products.

d. Victaulic Company.

e. <Insert manufacturer's name>.

Fittings and couplings in subparagraphs below are available in NPS 3 to NPS 24 (DN 80 to DN 600).

2. Grooved-End, Ductile-Iron Fittings:  ASTM A 47/A 47M, malleable-iron castings or ASTM A 536, ductile-iron castings with dimensions matching pipe.

3. Grooved-End, Ductile-Iron-Piping Couplings:  AWWA C606, for ductile-iron-pipe dimensions.  Include ferrous housing sections, gasket suitable for water, and bolts and nuts.

E. Mechanical-Joint, Ductile-Iron Fittings:  AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

1. Glands, Gaskets, and Bolts:  AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Fittings in first paragraph below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

F. Push-on-Joint, Ductile-Iron Fittings:  AWWA C153, ductile-iron compact pattern.

1. Gaskets:  AWWA C111, rubber.

Flanges in paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

G. Flanges:  ASME B16.1, Class 125, cast iron.

2.3 PE PIPE AND FITTINGS

Pipe in first paragraph below is FM Global approved in NPS 2 to NPS 12 (DN 50 to DN 300).

A. PE, Fire-Service Pipe:  FM Global approved, with minimum thickness equivalent to [Class 150] [and] [Class 200].

B. Molded PE Fittings:  FM Global approved; PE butt-fusion type, made to match PE pipe dimensions and class.

2.4 PVC PIPE AND FITTINGS

Pipe in first paragraph below is UL listed in NPS 4 to NPS 12 (DN 100 to DN 300).

A. PVC Pipe:  [AWWA C900] [or] [UL 1285], [Class 150] [and] [Class 200], with bell end with gasket, and with spigot end.

B. PVC Fittings:  [AWWA C900] [or] [UL 1285], [Class 150] [and] [Class 200], with bell-and-spigot or double-bell ends.  Include elastomeric gasket in each bell.

2.5 FIBERGLASS PIPE AND FITTINGS

"RTRP" is ASTM and AWWA abbreviation for fiberglass pipe; "RTRF" is ASTM abbreviation for fiberglass fittings.

Pipe in first paragraph below is UL listed in NPS 4 to NPS 12 (DN 100 to DN 300).

A. RTRP:  UL 1713, [Class 150] [and] [Class 200], with bell-and-spigot ends for bonded joints.  Liner is optional unless otherwise indicated.

B. RTRF:  UL 1713, similar to pipe in material, pressure class, and joining method.

2.6 SPECIAL PIPE FITTINGS

A. Ductile-Iron Flexible Expansion Joints:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. EBAA Iron, Inc.

b. ROMAC Industries Inc.

c. Star Pipe Products.

d. <Insert manufacturer's name>.

2. Description:  Compound, ductile-iron fitting with combination of flanged and mechanical-joint ends complying with AWWA C110 or AWWA C153.  Include two gasketed ball-joint sections and one or more gasketed sleeve sections.  Assemble components for offset and expansion indicated.  Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

3. Pressure Rating:  250 psig (1725 kPa) minimum.

B. Ductile-Iron Deflection Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. EBAA Iron, Inc.

b. <Insert manufacturer's name>.

2. Description:  Compound, ductile-iron coupling fitting with sleeve and one or two flexing sections for up to 15-degree deflection, gaskets, and restrained-joint ends complying with AWWA C110 or AWWA C153.  Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

3. Pressure Rating:  250 psig (1725 kPa) minimum.

2.7 ENCASEMENT FOR PIPING

Many authorities having jurisdiction will not permit direct burial of fire-suppression water-service piping.  If allowed by authorities having jurisdiction, consider installing underground piping in a PVC conduit.

A. Standard:  ASTM A 674 or AWWA C105.

B. Material:  [Linear low-density PE film of 0.008-inch (0.20-mm)] [or] [High-density, cross-laminated PE film of 0.004-inch (0.10-mm)] minimum thickness.

C. Form:  [Sheet] [or] [tube].

D. Color:  [Black] [or] [natural] <Insert color>.

2.8 JOINING MATERIALS

A. Gaskets for Ferrous Piping and Copper-Alloy Tubing:  ASME B16.21, asbestos free.

B. Brazing Filler Metals:  AWS A5.8/A5.8M, BCuP Series.

C. Bonding Adhesive for Fiberglass Piping:  As recommended by fiberglass piping manufacturer.

2.9 PIPING SPECIALTIES

A. Transition Fittings:  Manufactured fitting or coupling same size as, with pressure rating at least equal to and ends compatible with, piping to be joined.

B. Tubular-Sleeve Pipe Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cascade Waterworks Manufacturing.

b. Dresser, Inc.; Dresser Piping Specialties.

c. Ford Meter Box Company, Inc. (The); Pipe Products Division.

d. JCM Industries.

e. ROMAC Industries Inc.

f. Smith-Blair, Inc.; a Sensus company.

g. Viking Johnson.

h. <Insert manufacturer's name>.

2. Description:  Metal, bolted, sleeve-type, reducing or transition coupling, with center sleeve, gaskets, end rings, and bolt fasteners, and with ends of same sizes as piping to be joined.

3. Standard:  AWWA C219.

4. Center-Sleeve Material:  [Manufacturer's standard] [Carbon steel] [Stainless steel] [Ductile iron] [Malleable iron].

5. Gasket Material:  Natural or synthetic rubber.

6. Pressure Rating:  [150 psig (1035 kPa)] [200 psig (1380 kPa)] <Insert value> minimum.

7. Metal Component Finish:  Corrosion-resistant coating or material.

2.10 [CORPORATION VALVES] [AND] [CURB VALVES]

Caution:  High-pressure valves in this article are rated for 150 psig (1035 kPa), but most manufacturers' valves have a higher pressure rating.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Amcast Industrial Corporation.

2. Ford Meter Box Company, Inc. (The); Pipe Products Division.

3. Jones, James Company.

4. Master Meter, Inc.

5. McDonald, A. Y. Mfg. Co.

6. Mueller Co.; Water Products Division.

7. Red Hed Manufacturing & Supply.

8. <Insert manufacturer's name>.

Retain first paragraph below for tapping connections NPS 2 (DN 50) and smaller.

B. Corporation Valves:  Comply with AWWA C800.  Include saddle and valve compatible with tapping machine[ and manifold].

1. Service Saddle:  Copper alloy with seal and AWWA C800, threaded outlet for corporation valve.

2. Corporation Valve:  Bronze body and ground-key plug, with AWWA C800, threaded inlet and outlet matching service piping material.

Retain subparagraph below if utility company requires multiple connections.

3. Manifold:  Copper fitting with two to four inlets as required, with ends matching corporation valves and outlet matching service piping material.

C. Curb Valves:  Comply with AWWA C800 for high-pressure service-line valves.  Valve has bronze body, ground-key plug or ball, wide tee head, and inlet and outlet matching service piping material.

D. Service Boxes for Curb Valves:  Similar to AWWA M44 requirements for cast-iron valve boxes.  Include cast-iron telescoping top section of length required for depth of burial of valve, plug with lettering "WATER," and bottom section with base that fits over curb valve and with a barrel approximately 3 inches (75 mm) in diameter.

1. Shutoff Rods:  Steel; with tee-handle with one pointed end, stem of length to operate deepest buried valve, and slotted end matching curb valve.

E. Meter Valves:  Comply with AWWA C800 for high-pressure service-line valves.  Include angle- or straight-through-pattern bronze body, ground-key plug or ball, and wide tee head, with inlet and outlet matching service piping material.

2.11 GATE VALVES

Verify with authorities having jurisdiction whether AWWA (including small MSS) or UL-listed/FM-approved valves are required.

A. AWWA Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American AVK Company; Valves & Fittings Division.

b. American Cast Iron Pipe Company; American Flow Control Division.

c. American Cast Iron Pipe Company; Waterous Company Subsidiary.

d. American R/D.

e. Clow Valve Company; a division of McWane, Inc.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. East Jordan Iron Works, Inc.

h. Kennedy Valve; a division of McWane, Inc.

i. M&H Valve Company; a division of McWane, Inc.

j. Mueller Co.; Water Products Division.

k. NIBCO INC.

l. Tyler Pipe; a division of McWane, Inc.; Utilities Division.

m. U.S. Pipe.

n. <Insert manufacturer's name>.

Retain any of seven subparagraphs below for valve types and pressure ratings required.  If more than one pressure zone is required, show pressure ratings of valves on Drawings.

2. 200-psig (1380-kPa), AWWA, Iron, Nonrising-Stem, Metal-Seated Gate Valves:

a. Description:  Gray- or ductile-iron body and bonnet; with cast-iron or bronze double-disc gate, bronze gate rings, bronze stem, and stem nut.

b. Standard:  AWWA C500.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Mechanical joint.

e. Interior Coating:  Complying with AWWA C550.

3. 200-psig (1380-kPa), AWWA, Iron, Nonrising-Stem, Resilient-Seated Gate Valves:

a. Description:  Gray- or ductile-iron body and bonnet; with bronze or gray- or ductile-iron gate, resilient seats, bronze stem, and stem nut.

b. Standard:  AWWA C509.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Mechanical or push-on joint.

e. Interior Coating:  Complying with AWWA C550.

4. 250-psig (1725-kPa), AWWA, Iron, Nonrising-Stem, Resilient-Seated Gate Valves:

a. Description:  Ductile-iron body and bonnet; with bronze or ductile-iron gate, resilient seats, bronze stem, and stem nut.

b. Standard:  AWWA C509.

c. Pressure Rating:  250 psig (1725 kPa).

d. End Connections:  Mechanical or push-on joint.

e. Interior Coating:  Complying with AWWA C550.

5. 200-psig (1380-kPa), AWWA, Iron, OS&Y, Metal-Seated Gate Valves:

a. Description:  Cast- or ductile-iron body and bonnet; with cast-iron double disc, bronze disc and seat rings, and bronze stem.

b. Standard:  AWWA C500.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Flanged or grooved.

6. 200-psig (1380-kPa), AWWA, Iron, OS&Y, Resilient-Seated Gate Valves:

a. Description:  Cast- or ductile-iron body and bonnet; with bronze, gray-iron, or ductile-iron gate; resilient seats; and bronze stem.

b. Standard:  AWWA C509.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Flanged or grooved.

7. 250-psig (1725-kPa), AWWA, Iron, OS&Y, Resilient-Seated Gate Valves:

a. Description:  Cast- or ductile-iron body and bonnet; with bronze, gray-iron, or ductile-iron gate; resilient seats; and bronze stem.

b. Standard:  AWWA C509.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Flanged or grooved.

8. Class 125, Bronze, Nonrising-Stem Gate Valves:

a. Description:  Class 125, Type 1; bronze with solid wedge and malleable-iron handwheel.

b. Standard:  MSS SP-80.

c. Pressure Rating:  200 psig (1380 kPa).

d. End Connections:  Solder joint or threaded.

Retain UL-listed or FM-approved, cast-iron gate valves for use with indicator posts and OS&Y gate valves for fire-service piping in vaults if required by authorities having jurisdiction.

B. UL-Listed or FM-Approved Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American AVK Company; Valve & Fittings Division.

b. American Cast Iron Pipe Company; American Flow Control Division.

c. American Cast Iron Pipe Company; Waterous Company Subsidiary.

d. Clow Valve Company; a division of McWane, Inc.

e. Crane Co.; Crane Valve Group; Jenkins Valves.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. East Jordan Iron Works, Inc.

h. Hammond Valve.

i. Kennedy Valve; a division of McWane, Inc.

j. M&H Valve Company; a division of McWane, Inc.

k. Milwaukee Valve Company.

l. Mueller Co.; Water Products Division.

m. NIBCO INC.

n. Shurjoint Piping Products.

o. Troy Valve; a division of Penn-Troy Manufacturing, Inc.

p. Tyco Fire & Building Products LP.

q. United Brass Works, Inc.

r. U.S. Pipe.

s. Watts Water Technologies, Inc.

t. <Insert manufacturer's name>.

2. 175-psig (1200-kPa), UL-Listed or FM-Approved, Iron, Nonrising-Stem Gate Valves:

a. Description:  Iron body and bonnet, bronze seating material, and inside screw.

b. Standards:  UL 262 and "Approval Guide," published by FM Global, listing.

c. Pressure Rating:  175 psig (1200) minimum.

d. End Connections:  Mechanical or push-on joint.

e. Indicator-Post Flange:  Include on valves used with indicator posts.

3. 250-psig (1725-kPa), UL-Listed or FM-Approved, Iron, Nonrising-Stem Gate Valves:

a. Description:  Iron body and bonnet, bronze seating material, and inside screw.

b. Standards:  UL 262 and "Approval Guide," published by FM Global, listing.

c. Pressure Rating:  250 psig (1725 kPa) minimum.

d. End Connections:  Mechanical or push-on joint.

e. Indicator-Post Flange:  Include on valves used with indicator posts.

Use supervisory switches with valves in first subparagraph below.

4. 175-psig (1200-kPa), UL-Listed or FM-Approved, Iron, OS&Y, Gate Valves:

a. Description:  Iron body and bonnet and bronze seating material.

b. Standards:  UL 262 and "Approval Guide," published by FM Global, listing.

c. Pressure Rating:  175 psig (1200 kPa) minimum.

d. End Connections:  Flanged or grooved.

Use supervisory switches with valves in first subparagraph below.

5. 250-psig (1725-kPa), UL-Listed or FM-Approved, Iron, OS&Y Gate Valves:

a. Description:  Iron body and bonnet and bronze seating material.

b. Standards:  UL 262 and "Approval Guide," published by FM Global, listing.

c. Pressure Rating:  250 psig (1725 kPa) minimum.

d. End Connections:  Flanged or grooved.

Use supervisory switches with valves in subparagraph below.

6. UL-Listed or FM-Approved, OS&Y Bronze, Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Crane Co.; Crane Valve Group; Crane Valves.

2) Crane Co.; Crane Valve Group; Stockham Division.

3) Milwaukee Valve Company.

4) NIBCO INC.

5) United Brass Works, Inc.

6) <Insert manufacturer's name>.

b. Description:  Bronze body and bonnet and bronze stem.

c. Standards:  UL 262 and "Approval Guide," published by FM Global, listing.

d. Pressure Rating:  175 psig (1200 kPa) minimum.

e. End Connections:  Threaded.

2.12 GATE VALVE ACCESSORIES AND SPECIALTIES

Retain first paragraph below for tapping connections larger than NPS 2 (DN 50).

A. Tapping-Sleeve Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Cast Iron Pipe Company; Waterous Company Subsidiary.

b. Clow Valve Company; a division of McWane, Inc.

c. East Jordan Iron Works, Inc.

d. Flowserve.

e. Kennedy Valve; a division of McWane, Inc.

f. M&H Valve Company; a division of McWane, Inc.

g. Mueller Co.; Water Products Division.

h. U.S. Pipe.

i. <Insert manufacturer's name>.

3. Description:  Sleeve and valve compatible with drilling machine.

4. Standard:  MSS SP-60.

5. Tapping Sleeve:  Cast-iron, ductile-iron, or stainless-steel, two-piece bolted sleeve with flanged outlet for new branch connection.  Sleeve shall match size and type of pipe material being tapped and have recessed flange for branch valve.

6. Valve:  AWWA, cast-iron, nonrising-stem, [metal] [resilient]-seated gate valve with one raised-face flange mating tapping-sleeve flange.

B. Valve Boxes:  Comply with AWWA M44 for cast-iron valve boxes.  Include top section, adjustable extension of length required for depth of burial of valve, plug with lettering "WATER," and bottom section with base that fits over valve and with a barrel approximately 5 inches (125 mm) in diameter.

1. Operating Wrenches:  Steel; with tee-handle with one pointed end, stem of length to operate deepest buried valve, and socket matching valve operating nut.

C. Indicator Posts:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American AVK Company; Valves & Fittings Division.

b. American Cast Iron Pipe Company; American Flow Control Division.

c. American Cast Iron Pipe Company; Waterous Company Subsidiary.

d. Clow Valve Company; a division of McWane, Inc.

e. Crane Co.; Crane Valve Group; Stockham Division.

f. Kennedy Valve; a division of McWane, Inc.

g. Mueller Co.; Water Products Division.

h. NIBCO INC.

i. Tyco Fire & Building Products LP.

j. <Insert manufacturer's name>.

2. Description:  Vertical-type, cast-iron body with operating wrench, extension rod, and adjustable cast-iron barrel of length required for depth of burial of valve.

3. Standards:  UL 789 and "Approval Guide," published by FM Global, listing.

2.13 BUTTERFLY VALVES

Verify with authorities having jurisdiction whether AWWA, UL-listed, or FM-approved valves are required.

A. AWWA Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. DeZurik/Copes-Vulcan; a unit of SPX Corporation.

b. Milliken Valve Company.

c. Mosser Valve; a division of Olson Technologies, Inc.

d. Mueller Co.; Water Products Division.

e. Pratt, Henry Company.

f. Val-Matic Valve & Manufacturing Corp.

g. <Insert manufacturer's name>.

2. Description:  Rubber seated.

3. Standard:  AWWA C504.

4. Body Material:  Cast or ductile iron.

5. Body Type:  [Wafer] [or] [flanged].

6. Pressure Rating:  150 psig (1035 kPa).

B. UL Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Kennedy Valve; a division of McWane, Inc.

b. Milwaukee Valve Company.

c. Mueller Co.; Water Products Division.

d. NIBCO INC.

e. Pratt, Henry Company.

f. <Insert manufacturer's name>.

3. Description:  Metal on resilient material seating.

4. Standards:  UL 1091 and "Approval Guide," published by FM Global, listing.

5. Body Material:  Cast or ductile iron.

6. Body Type:  [Wafer] [or] [flanged].

7. Pressure Rating:  175 psig (1200 kPa).

2.14 CHECK VALVES

Verify with authorities having jurisdiction whether AWWA, UL-listed, or FM-approved valves are required.

Check valves in first paragraph below are available in NPS 2 (DN 50) and larger.

A. AWWA Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American AVK Company; Valves & Fittings Division.

b. American Cast Iron Pipe Company; American Flow Control Division.

c. APCO Willamette Valve and Primer Corporation.

d. Clow Valve Company; a division of McWane, Inc.

e. Crane Co.; Crane Valve Group; Crane Valves.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. Kennedy Valve; a division of McWane, Inc.

h. M&H Valve Company; a division of McWane, Inc.

i. Mueller Co.; Water Products Division.

j. NIBCO INC.

k. Watts Water Technologies, Inc.

l. <Insert manufacturer's name>.

2. Description:  Swing-check type with resilient seat; with interior coating according to AWWA C550 and ends to match piping.

3. Standard:  AWWA C508.

4. Pressure Rating:  175 psig (1200 kPa).

Check valves in paragraph below are available in NPS 2-1/2 (DN 65) and larger.

B. UL-Listed or FM-Approved Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Cast Iron Pipe Company; Waterous Company Subsidiary.

b. Clow Valve Company; a division of McWane, Inc.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Globe Fire Sprinkler Corporation.

e. Kennedy Valve; a division of McWane, Inc.

f. Kidde Fire Fighting.

g. Matco-Norca.

h. Mueller Co.; Water Products Division.

i. NIBCO INC.

j. Reliable Automatic Sprinkler Co., Inc.

k. Tyco Fire & Building Products LP.

l. United Brass Works, Inc.

m. Victaulic Company.

n. Viking Corporation.

o. Watts Water Technologies, Inc.

p. <Insert manufacturer's name>.

2. Description:  Swing-check type with pressure rating, rubber-face checks unless otherwise indicated, and ends matching piping.

3. Standards:  UL 312 and "Approval Guide," published by FM Global, listing.

4. Pressure Rating:  [175 psig (1200 kPa)] [250 psig (1725 kPa)].

2.15 DETECTOR CHECK VALVES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

2. Badger Meter, Inc.

3. FEBCO; SPX Valves & Controls.

4. Globe Fire Sprinkler Corporation.

5. Kennedy Valve; a division of McWane, Inc.

6. Mueller Co.; Hersey Meters Division.

7. Victaulic Company.

8. Viking Corporation.

9. Watts Water Technologies, Inc.

10. <Insert manufacturer's name>.

C. Description:  Galvanized cast-iron body, bolted cover with air-bleed device for access to internal parts, and flanged ends.  Include one-piece bronze disc with bronze bushings, pivot, and replaceable seat.  Include threaded bypass taps in inlet and outlet for bypass meter connection.  Set valve to allow minimal water flow through bypass meter when major water flow is required.

D. Standards:  UL 312 and "Approval Guide," published by FM Global, listing.

E. Pressure Rating:  175 psig (1200 kPa).

F. Water Meter:  AWWA C700, disc type, at least one-fourth size of detector check valve.  Include meter, bypass piping, gate valves, check valve, and connections to detector check valve.

2.16 WATER METERS

A. Water meters will be furnished by utility company.

If utility company furnishes water meters, identify utility company in "Summary" Article and delete remaining paragraphs in this article.  If water meters are specified in this Section, delete paragraph above, retain remaining paragraphs, and revise to suit Project.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. AMCO Water Metering Systems.

2. Badger Meter, Inc.

3. Carlon Meter.

4. Hays Fluid Controls.

5. McCrometer.

6. Mueller Co.; Hersey Meters Division.

7. Neptune Technology Group Inc.

8. Sensus Metering Systems.

9. <Insert manufacturer's name>.

Retain one of first three paragraphs below.  Verify type of meter required with utility company and authorities having jurisdiction.

C. Displacement-Type Water Meters:

1. Description:  With bronze main case.

2. Standard:  AWWA C700.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

D. Turbine-Type Water Meters:

1. Standard:  AWWA C701.

2. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

E. Compound-Type Water Meters:

1. Standard:  AWWA C702.

2. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

Retain one of two "Remote Registration System" paragraphs below if required; revise to suit Project.

F. Remote Registration System:

1. Description:  Utility company's standard; direct-reading type.  Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard:  AWWA C706.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

G. Remote Registration System:

1. Description:  Utility company's standard; encoder type.  Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard:  AWWA C707.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

Retain one of two subparagraphs below; revise to suit Project.

4. Data-Acquisition Units:  Comply with utility company's requirements for type and quantity.

5. Visible Display Units:  Comply with utility company's requirements for type and quantity.

2.17 DETECTOR-TYPE WATER METERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Badger Meter, Inc.

2. Mueller Co.; Hersey Meters Division.

3. Neptune Technology Group Inc.

4. Sensus Metering Systems.

5. <Insert manufacturer's name>.

Retain one of first two paragraphs below.  Verify type of meter required with utility company and authorities having jurisdiction.

B. AWWA, Detector Check Water Meters:

1. Description:  Main line, turbine meter with second meter on bypass.

2. Standard:  AWWA C703.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

4. Pressure Rating:  150 psig (1035 kPa).

5. Bypass Meter:  [AWWA C701, turbine] [AWWA C702, compound]-type, bronze case.

a. Size:  At least one-half nominal size of main-line meter.

C. Fire-Protection, Detector Check Water Meters:

1. Description:  Main-line turbine meter with strainer and second meter on bypass.

2. Standards:  UL's "Fire Protection Equipment Directory" listing and "Approval Guide," published by FM Global, listing.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

4. Pressure Rating:  175 psig (1200 kPa) minimum.

5. Bypass Meter:  AWWA C701, turbine-type, bronze case.

a. Size:  At least NPS 2 (DN 50).

Retain one of two "Remote Registration System" paragraphs below if required, and revise to suit Project.

D. Remote Registration System:

1. Description:  Utility company's standard; direct-reading type.  Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard:  AWWA C706.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

E. Remote Registration System:

1. Description:  Utility company's standard; encoder type.  Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard:  AWWA C707.

3. Registration:  Flow in [gallons (liters)] [cubic feet (cubic meters)].

Retain one of two subparagraphs below and revise to suit Project.

4. Data-Acquisition Units:  Comply with utility company's requirements for type and quantity.

5. Visible Display Units:  Comply with utility company's requirements for type and quantity.

2.18 PRESSURE-REDUCING VALVES

Copy first paragraph below and re-edit for each type of water regulator required.

Water regulators in first paragraph below are available in NPS 1/2 to NPS 3 (DN 15 to DN 80).

A. Water Regulators:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Cash Acme; a division of The Reliance Worldwide Corporation.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Honeywell Water Controls.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

f. <Insert manufacturer's name>.

3. Standard:  ASSE 1003.

4. Pressure Rating:  Initial pressure of 150 psig (1035 kPa).

5. Size:  <Insert NPS (DN)>.

6. Design Flow Rate:  <Insert gpm (L/s)>.

7. Design Inlet Pressure:  <Insert psig (kPa)>.

8. Design Outlet Pressure Setting:  <Insert psig (kPa)>.

9. Body Material:  Bronze[ with chrome-plated finish] for NPS 2 (DN 50) and smaller; cast iron[ with interior lining complying with AWWA C550 or that is FDA approved] for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

10. End Connections:  Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

Copy paragraph below and re-edit for each type of water control valve required.

Water control valves in paragraph below are available in NPS 1-1/4 (DN 32) and larger.

B. Water Control Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. CLA-VAL Automatic Control Valves.

b. Flomatic Corporation.

c. OCV Control Valves.

d. Watts Regulator Company; Ames Fluid Control Systems.

e. Watts Regulator Company; Watts ACV Division.

f. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

g. <Insert manufacturer's name>.

3. Description:  Pilot-operation, diaphragm-type, single-seated main water control valve with AWWA C550 or FDA-approved, interior epoxy coating.  Include small pilot control valve, restrictor device, specialty fittings, and sensor piping.

4. Pressure Rating:  Initial pressure of 150 psig (1035 kPa) minimum.

5. Main Valve Body:  Cast or ductile iron with AWWA C550 or FDA-approved, interior epoxy coating; or stainless-steel body.

a. Size:  <Insert NPS (DN)>.

b. Pattern:  [Angle] [Globe]-valve design.

c. Trim:  Stainless steel.

6. Design Flow Rate:  <Insert gpm (L/s)>.

7. Design Inlet Pressure:  <Insert psig (kPa)>.

8. Design Outlet Pressure Setting:  <Insert psig (kPa)>.

9. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

2.19 BACKFLOW PREVENTERS

Verify with authorities having jurisdiction whether AWWA, or UL-listed, or FM-approved backflow preventers are required.

Copy first paragraph below and re-edit for each type of reduced-pressure-principle backflow preventer required.

Reduced-pressure-principle backflow preventers in first paragraph below are for high hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

A. Reduced-Pressure-Principle Backflow Preventers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Water Technologies, Inc.

f. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

g. <Insert manufacturer's name>.

3. Standard:  [ASSE 1013] [or] [AWWA C511].

4. Operation:  Continuous-pressure applications.

5. Pressure Loss:  [12 psig (83 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size:  <Insert NPS (DN)>.

7. Design Flow Rate:  <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits:  <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)> for NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

10. Body Material:  Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

11. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

12. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

13. Accessories:

a. Valves:  Ball type with threaded ends on inlet and outlet of NPS 2 (DN 50) and smaller; OS&Y gate type with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

b. Air-Gap Fitting:  ASME A112.1.2, matching backflow preventer connection.

Copy first paragraph below and re-edit for each type of double-check, backflow-prevention assembly required.

Double-check, backflow-prevention assemblies in first paragraph below are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

B. Double-Check, Backflow-Prevention Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Water Technologies, Inc.

f. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

g. <Insert manufacturer's name>.

3. Standard:  [ASSE 1015] [or] [AWWA C510].

4. Operation:  Continuous-pressure applications unless otherwise indicated.

5. Pressure Loss:  [5 psig (35 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size:  <Insert NPS (DN)>.

7. Design Flow Rate:  <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits:  <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)> for NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

10. Body Material:  Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

11. End Connections:  Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

12. Configuration:  Designed for [horizontal, straight through] <Insert configuration> flow.

13. Accessories:  Ball valves with threaded ends on inlet and outlet of NPS 2 (DN 50) and smaller; OS&Y gate valves with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

Copy first paragraph below and re-edit for each type of reduced-pressure-detector, fire-protection backflow preventer assembly required.

Reduced-pressure-detector, fire-protection backflow preventer assemblies in first paragraph below are for high hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

C. Reduced-Pressure-Detector, Fire-Protection Backflow Preventer Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

f. <Insert manufacturer's name>.

3. Standards:  ASSE 1047 and UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

4. Operation:  Continuous-pressure applications.

5. Pressure Loss:  [12 psig (83 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size:  <Insert NPS (DN)>.

7. Design Flow Rate:  <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits:  <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)>.

10. Body Material:  [Cast iron with interior lining complying with AWWA C550 or that is FDA approved] [Steel with interior lining complying with AWWA C550 or that is FDA approved] [Stainless steel].

11. End Connections:  Flanged.

12. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

13. Accessories:

a. Valves:  UL 262, "Approval Guide," published by FM Global, listing; OS&Y gate type with flanged ends on inlet and outlet.

b. Air-Gap Fitting:  ASME A112.1.2, matching backflow preventer connection.

c. Bypass:  With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy first paragraph below and re-edit for each type of double-check, detector-assembly backflow preventer required.

Double-check, detector-assembly backflow preventers in first paragraph below are for low hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

D. Double-Check, Detector-Assembly Backflow Preventers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

f. <Insert manufacturer's name>.

3. Standards:  ASSE 1048 and UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

4. Operation:  Continuous-pressure applications.

5. Pressure Loss:  [5 psig (35 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size:  <Insert NPS (DN)>.

7. Design Flow Rate:  <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits:  <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate:  <Insert psig (kPa)>.

10. Body Material:  [Cast iron with interior lining complying with AWWA C550 or that is FDA approved] [Steel with interior lining complying with AWWA C550 or that is FDA approved] [Stainless steel].

11. End Connections:  Flanged.

12. Configuration:  Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

13. Accessories:

a. Valves:  UL 262, "Approval Guide," published by FM Global, listing, approved; OS&Y gate type with flanged ends on inlet and outlet.

b. Bypass:  With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy paragraph below and re-edit for each type of backflow preventer test kit required.

E. Backflow Preventer Test Kits:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. FEBCO; SPX Valves & Controls.

c. Flomatic Corporation.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

f. <Insert manufacturer's name>.

2. Description:  Factory calibrated, with gages, fittings, hoses, and carrying case with test-procedure instructions.

2.20 WATER METER BOXES

Retain one of three paragraphs in this article.

A. Description:  Cast-iron body and cover for disc-type water meter, with lettering "WATER METER" on cover; and with slotted, open-bottom base section of length to fit over service piping.

Delete subparagraph below if not permitted.

1. Option:  Base section may be cast-iron, PVC, clay, or other pipe.

B. Description:  Cast-iron body and double cover for disc-type water meter, with lettering "WATER METER" on top cover; and with separate inner cover; air space between covers; and slotted, open-bottom base section of length to fit over service piping.

Use meter box in paragraph below in walks or unpaved areas away from traffic; do not use in roadways.

C. Description:  Polymer-concrete body and cover for disc-type water meter, with lettering "WATER" on cover; and with slotted, open-bottom base section of length to fit over service piping.  Include vertical and lateral design loadings of 15,000 lb minimum over 10 by 10 inches (6 800 kg minimum over 254 by 254 mm) square.

2.21 CONCRETE VAULTS

Retain this article if vaults are required and are not specified in Division 03 Section "Cast-in-Place Concrete" or "Miscellaneous Cast-in-Place Concrete."

A. Description:  Precast, reinforced-concrete vault, designed for A-16 load designation according to ASTM C 857, and made according to ASTM C 858.

B. Ladder:  ASTM A 36/A 36M, steel ladder; or PE-encased steel steps.

Retain one of two "Manhole" paragraphs below.

C. Manhole:  ASTM A 48/A 48M, Class No. 35A minimum tensile strength, gray-iron traffic frame and cover.

1. Dimension:  24-inch (610-mm) minimum diameter unless otherwise indicated.

D. Manhole:  ASTM A 536, Grade 60-40-18, ductile-iron traffic frame and cover.

1. Dimension:  24-inch (610-mm) minimum diameter unless otherwise indicated.

E. Drain:  ASME A112.6.3, cast-iron floor drain with outlet of size indicated.  Include body anchor flange, light-duty cast-iron grate, bottom outlet, and integral or field-installed bronze ball or clapper-type backwater valve.

2.22 PROTECTIVE ENCLOSURES

A. Freeze-Protection Enclosures:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AquaShield.

b. BF Products.

c. DekoRRa Products LLC.

d. Dunco Manufacturing, Inc.

e. G&C Enclosures.

f. Hot Box, Inc.

g. HydroCowl, Inc.

h. Piedmont Well Covers, Inc.

i. Watts Water Technologies, Inc.

j. <Insert manufacturer's name>.

3. Description:  Insulated enclosure designed to protect aboveground water piping, equipment, or specialties from freezing and damage, with heat source to maintain minimum internal temperature of 40 deg F (4 deg C) when external temperatures reach as low as minus 34 deg F (minus 36 deg C).

4. Standard:  ASSE 1060.

Retain one of two subparagraphs below.

5. Class I:  For equipment or devices other than pressure or atmospheric vacuum breakers.

6. Class I-V:  For pressure or atmospheric vacuum breaker equipment or devices.  Include drain opening in housing.

Retain subparagraphs below with either subparagraph retained above for enclosure class.  Revise below to suit Project.

a. Housing:  Reinforced[-aluminum] [or] [-fiberglass] <Insert housing> construction.

1) Size:  Of dimensions indicated but not less than those required for access and service of protected unit.

2) Drain opening for units with drain connection.

3) Access doors with locking devices.

4) Insulation inside housing.

5) Anchoring devices for attaching housing to concrete base.

Features in subparagraph below require additional temperature data; insert here or detail on Drawings.

b. Electric heating cable or heater with self-limiting temperature control.

Class II and Class II-V freeze-retardant enclosures are also available but are not included in this Section.  ASSE 1060 is not clear on requirements for these enclosures.

B. Weather-Resistant Enclosures:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AquaShield.

b. BF Products.

c. DekoRRa Products LLC.

d. Dunco Manufacturing, Inc.

e. G&C Enclosures.

f. Hot Box, Inc.

g. HydroCowl, Inc.

h. Piedmont Well Covers, Inc.

i. Watts Water Technologies, Inc.

j. <Insert manufacturer's name>.

3. Description:  Uninsulated enclosure designed to protect aboveground water piping, equipment, or specialties from weather and damage.

4. Standard:  ASSE 1060.

Retain one of first two subparagraphs below.

5. Class III:  For equipment or devices other than pressure or atmospheric vacuum breakers.

6. Class III-V:  For pressure or atmospheric vacuum breaker equipment or devices.  Include drain opening in housing.

Retain subparagraphs below with either subparagraph retained above for enclosure class.  Revise below to suit Project.

a. Housing:  Reinforced[-aluminum] [or] [-fiberglass] <Insert housing> construction.

1) Size:  Of dimensions indicated, but not less than those required for access and service of protected unit.

2) Drain opening for units with drain connection.

3) Access doors with locking devices.

4) Anchoring devices for attaching housing to concrete base.

C. Expanded-Metal Enclosures:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Backflow Prevention Device InnClosures, Inc.

b. BF Products.

c. Cross Brothers Inc.

d. Le Meur Welding & Manufacturing Co.

e. V.I.T. Products, Inc.

f. <Insert manufacturer's name>.

3. Description:  Enclosure designed to protect aboveground water piping, equipment, or specialties from damage.

4. Material:  ASTM F 1267, expanded metal side and top panels, of weight and with reinforcement of same metal at edges as required for rigidity.

5. Type:  [I, expanded] [II, expanded and flattened].

6. Class:  [Class 1, uncoated carbon steel] [Class 2, hot-dip, zinc-coated carbon steel] [Class 3, corrosion-resistant steel].

Retain first subparagraph below if retaining Class 1 in subparagraph above.

7. Finish:  Manufacturer's enamel paint.

8. Size:  Of dimensions indicated but not less than those required for access and service of protected unit.

9. Locking device.

10. Lugs or devices for securing enclosure to base.

11. Enclosure Bases:  [4-inch- (100-mm-)] [6-inch- (150-mm-)] minimum thickness precast concrete, of dimensions required to extend at least 6 inches (150 mm) beyond edges of enclosure housings.  Include openings for piping.

2.23 FIRE HYDRANTS

A. AWWA Dry-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American AVK Company; Valves & Fittings Division.

b. American Cast Iron Pipe Company; American Flow Control Division.

c. American Cast Iron Pipe Company; Waterous Company Subsidiary.

d. American Foundry Group, Inc.

e. Clow Valve Company; a division of McWane, Inc.

f. East Jordan Iron Works, Inc.

g. Kennedy Valve; a division of McWane, Inc.

h. M&H Valve Company; a division of McWane, Inc.

i. Mueller Co.; Water Products Division.

j. Troy Valve; a division of Penn-Troy Manufacturing, Inc.

k. U.S. Pipe.

l. <Insert manufacturer's name>.

Retain first subparagraph below for AWWA dry-barrel fire hydrants.

3. Description:  Post type, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets; and with 5-1/4-inch (133-mm) main valve, drain valve, and NPS 6 (DN 150) mechanical-joint inlet.  Include interior coating according to AWWA C550.  Hydrant shall have cast-iron body and compression-type valve opening against pressure and closing with pressure.

4. Standard:  AWWA C502.

Verify availability of model with selected manufacturer if 200- or 250-psig (1380- or 1725-kPa) pressure rating is required.

5. Pressure Rating:  [150 psig (1035 kPa) minimum] [200 psig (1380 kPa) minimum] [250 psig (1725 kPa)].

B. UL-Listed, Dry-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Cast Iron Pipe Company; American Flow Control Division.

b. American Cast Iron Pipe Company; Waterous Company Subsidiary.

c. American Foundry Group, Inc.

d. Clow Valve Company; a division of McWane, Inc.

e. East Jordan Iron Works, Inc.

f. Kennedy Valve; a division of McWane, Inc.

g. M&H Valve Company; a division of McWane, Inc.

h. Mueller Co.; Water Products Division.

i. Troy Valve; a division of Penn-Troy Manufacturing, Inc.

j. U.S. Pipe.

k. <Insert manufacturer's name>.

Retain first subparagraph below for UL-listed or FM-approved dry-barrel fire hydrants.

3. Description:  Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets; and with 5-1/4-inch (133-mm) main valve, drain valve, and NPS 6 (DN 150) mechanical-joint inlet.  Hydrant shall have cast-iron body and compression-type valve opening against pressure and closing with pressure.

4. Standards:  UL 246 and "Approval Guide," published by FM Global, listing.

5. Design:  Base valve.

Verify availability of model with selected manufacturer if 175-, 200-, or 250-psig (1200-, 1380-, or 1725-kPa) pressure rating is required.

6. Pressure Rating:  [150 psig (1035 kPa) minimum] [175 psig (1200 kPa) minimum] [200 psig (1380 kPa) minimum] [250 psig (1725 kPa)].

7. Outlet Threads:  NFPA 1963, with external hose thread used by local fire department.  Include cast-iron caps with steel chains.

Revise first two subparagraphs below if required by authorities having jurisdiction.

8. Operating and Cap Nuts:  Pentagon, 1-1/2 inches (38 mm) point to flat.

9. Direction of Opening:  Hydrant valve opens by turning operating nut to left or counterclockwise.

10. Exterior Finish:  Red alkyd-gloss enamel paint unless otherwise indicated.

C. AWWA Wet-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American AVK Company; Valves & Fittings Division.

b. Clow Valve Company; a division of McWane, Inc.

c. Jones, James Company.

d. Mueller Co.; Water Products Division.

e. <Insert manufacturer's name>.

Retain first subparagraph below for AWWA wet-barrel fire hydrants.

3. Description:  Post type, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets and with NPS 6 (DN 150) threaded or flanged inlet, and base section with NPS 6 (DN 150) mechanical-joint inlet.  Include interior coating according to AWWA C550.

4. Standard:  AWWA C503.

Verify availability of model with selected manufacturer if 200- or 250-psig (1380- or 1725-kPa) pressure rating is required.

5. Pressure Rating:  [150 psig (1035 kPa) minimum] [200 psig (1380 kPa) minimum] [250 psig (1725 kPa)].

D. UL-Listed, Wet-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American AVK Company; Valves & Fittings Division.

b. Clow Valve Company; a division of McWane, Inc.

c. Jones, James Company.

d. Mueller Co.; Water Products Division.

e. <Insert manufacturer's name>.

Retain first subparagraph below for UL-listed or FM-approved wet-barrel fire hydrants.

3. Description:  Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets and with NPS 6 (DN 150) threaded or flanged inlet, and base section with NPS 6 (DN 150) mechanical-joint inlet.

4. Standards:  UL 246 and "Approval Guide," published by FM Global, listing.

5. Design:  Wet barrel.

Verify availability of model with selected manufacturer if 175- or 200-psig (1200- or 1380-kPa) pressure rating is required.

6. Pressure Rating:  [150 psig (1035 kPa) minimum] [175 psig (1200 kPa) minimum] [200 psig (1380 kPa)].

7. Outlet Threads:  NFPA 1963, with external hose thread used by local fire department.  Include cast-iron caps with steel chains.

Revise first two subparagraphs below if required by authorities having jurisdiction.

8. Operating and Cap Nuts:  Pentagon, 1-1/2 inches (38 mm) point to flat.

9. Direction of Opening:  Hydrant valves open by turning operating nut to left or counterclockwise.

10. Exterior Finish:  Red alkyd-gloss enamel paint unless otherwise indicated.

2.24 FIRE-DEPARTMENT CONNECTIONS

Copy this article and re-edit for each type of fire-department connection required.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Elkhart Brass Mfg. Company, Inc.

2. Fire-End & Croker Corporation.

3. Guardian Fire Equipment, Inc.

4. Kidde Fire Fighting.

5. Potter Roemer.

6. Reliable Automatic Sprinkler Co., Inc.

7. <Insert manufacturer's name>.

C. Description:  Freestanding, with cast-bronze body, thread inlets according to NFPA 1963 and matching local fire-department hose threads, and threaded bottom outlet.  Include lugged caps, gaskets, and chains; lugged swivel connection and drop clapper for each hose-connection inlet; 18-inch- (460-mm-) high brass sleeve; and round escutcheon plate.

D. Standard:  UL 405.

Retain one of first three paragraphs below.

E. Connections:  Two NPS 2-1/2 (DN 65) inlets and one [NPS 4 (DN 100)] [NPS 6 (DN 150)] outlet.

F. Connections:  [Three] [Four] NPS 2-1/2 (DN 65) inlets and one NPS 6 (DN 150) outlet.

G. Connections:  Six NPS 2-1/2 (DN 65) inlets and one [NPS 6 (DN 150)] [NPS 8 (DN 200)] outlet.

H. Inlet Alignment:  [Inline, horizontal] [Square].

I. Finish Including Sleeve:  [Polished chrome plated] [Rough chrome plated] [Polished bronze].

J. Escutcheon Plate Marking:  "[AUTO SPKR] [&] [STANDPIPE]."

2.25 ALARM DEVICES

A. General:  UL 753 and "Approval Guide," published by FM Global, listing, of types and sizes to mate and match piping and equipment.

Devices in three paragraphs below are usually located inside the building and are specified in other Division 21 Sections.  Verify requirements with authorities having jurisdiction.  Indicators in first paragraph mount on pipe with vane in water and can be used with wet-barrel fire hydrants.

B. Water-Flow Indicators:  Vane-type water-flow detector, rated for 250-psig (1725-kPa) working pressure; designed for horizontal or vertical installation; with two single-pole, double-throw circuit switches to provide isolated alarm and auxiliary contacts, 7 A, 125-V ac and 0.25 A, 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal when cover is removed.

Switches in first paragraph below mount on stem of OS&Y gate valves and on indicator posts.

C. Supervisory Switches:  Single pole, double throw; designed to signal valve in other than fully open position.

Switches in paragraph below mount on barrel of dry-barrel fire hydrants.

D. Pressure Switches:  Single pole, double throw; designed to signal increase in pressure.

2.26 SLEEVES

Sleeves for exterior walls and slabs-on-grade are also specified in Division 21 Sections "Fire-Suppression Standpipes," "Wet-Pipe Sprinkler Systems," and "Dry-Pipe Sprinkler Systems."Division 13 Do not specify these sleeves in both this Section and another fire-suppression piping Section.

Wall-pipe sleeves in first paragraph below are available with many end variations.

A. Cast-Iron Wall-Pipe Sleeves:  Cast or fabricated of cast iron and equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop unless otherwise indicated.

B. Galvanized-Steel-Sheet Sleeves:  0.0239-inch (0.6-mm) minimum thickness; round tube closed with welded longitudinal joint.

C. Galvanized-Steel-Pipe Sleeves:  ASTM A 53/A 53M, Type E, standard-weight, zinc-coated, plain ends.

2.27 SLEEVE SEALS

Sleeve seals for exterior walls and slabs-on-grade are also specified in Division 21 Sections "Fire-Suppression Standpipes," "Wet-Pipe Sprinkler Systems," and "Dry-Pipe Sprinkler Systems." Do not specify these sleeve seals in both this Section and another fire-suppression piping Section.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Advance Products & Systems, Inc.

2. Calpico, Inc.

3. Metraflex, Inc.

4. Pipeline Seal and Insulator, Inc.

5. <Insert manufacturer's name>.

B. Description:  Modular sealing element unit, designed for field assembly, to fill annular space between pipe and sleeve.

Retain "EPDM-rubber" option in first paragraph below unless NBR gasket material is required because hydrocarbons are present in the soil.

C. Sealing Elements:  [EPDM-rubber] [or] [NBR] interlocking links shaped to fit surface of pipe.  Include type and number required for pipe material and size of pipe.

D. Pressure Plates:  [Carbon steel] [Plastic] [Stainless steel].

E. Connecting Bolts and Nuts:  [Carbon steel with corrosion-resistant coating] [Stainless steel] of length required to secure pressure plates to sealing elements.

2.28 GROUT

A. Standard:  ASTM C 1107, Grade B, posthardening and volume adjusting, dry, hydraulic-cement grout.

B. Characteristics:  Nonshrink; recommended for interior and exterior applications.

C. Design Mix:  5000-psi (34-MPa), 28-day compressive strength.

D. Packaging:  Premixed and factory packaged.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Comply with excavating, trenching, and backfilling requirements in Division 31 Section "Earth Moving."

3.2 PIPING INSTALLATION

Retain one of first two paragraphs below.  Retain first paragraph if tap is made by utility company; retain second if tap is made by Contractor.

A. Water-Main Connection:  Arrange with water utility company for tap of size and in location indicated in water main.

B. Water-Main Connection:  Tap water main according to requirements of water utility company and of size and in location indicated.

Retain first paragraph below for tapping of pipe with connections larger than NPS 2 (DN 50).

C. Make connections larger than NPS 2 (DN 50) with tapping machine according to the following:

1. Install tapping sleeve and tapping valve according to MSS SP-60.

2. Install tapping sleeve on pipe to be tapped.  Position flanged outlet for gate valve.

3. Use tapping machine compatible with valve and tapping sleeve; cut hole in main.  Remove tapping machine and connect water-service piping.

4. Install gate valve onto tapping sleeve.  Comply with MSS SP-60.  Install valve with stem pointing up and with valve box.

Retain first paragraph below for tapping of pipe with connections NPS 2 (DN 50) and smaller.

D. Make connections NPS 2 (DN 50) and smaller with drilling machine according to the following:

1. Install service-saddle assemblies and corporation valves in size, quantity, and arrangement required by utility company's standards.

2. Install service-saddle assemblies on water-service pipe to be tapped.  Position outlets for corporation valves.

3. Use drilling machine compatible with service-saddle assemblies and corporation valves.  Drill hole in main.  Remove drilling machine and connect water-service piping.

4. Install corporation valves into service-saddle assemblies.

5. Install manifold for multiple taps in water main.

6. Install curb valve in water-service piping with head pointing up and with service box.

E. Comply with NFPA 24 for fire-service-main piping materials and installation.

F. Install copper tube and fittings according to CDA's "Copper Tube Handbook."

Retain subparagraph below if required.

1. Install encasement for tubing according to ASTM A 674 or AWWA C105.

G. Install ductile-iron, water-service piping according to AWWA C600 and AWWA M41.

Retain subparagraph below if required.

1. Install encasement for piping according to ASTM A 674 or AWWA C105.

H. Install PE pipe according to ASTM D 2774 and ASTM F 645.

I. Install PVC, AWWA pipe according to ASTM F 645 and AWWA M23.

J. Install fiberglass AWWA pipe according to AWWA M45.

Revise first paragraph below for required minimum depth if known.

K. Bury piping with depth of cover over top at least [30 inches (750 mm)] <Insert dimension>, with top at least [12 inches (300 mm)] <Insert dimension> below level of maximum frost penetration, and according to the following:

1. Under Driveways:  With at least [36 inches (910 mm)] <Insert dimension> of cover over top.

2. Under Railroad Tracks:  With at least [48 inches (1220 mm)] <Insert dimension> of cover over top.

3. In Loose Gravelly Soil and Rock:  With at least [12 inches (300 mm)] <Insert dimension> of additional cover.

L. Install piping by tunneling or jacking, or combination of both, under streets and other obstructions that cannot be disturbed.

M. Extend fire-suppression water-service piping and connect to water-supply source and building fire-suppression water-service piping systems at locations and pipe sizes indicated.

1. Terminate fire-suppression water-service piping at building [floor slab] [wall] until building-water-piping systems are installed.  Terminate piping with caps, plugs, or flanges as required for piping material.  Make connections to building's fire-suppression water-service piping systems when those systems are installed.

Retain first paragraph below for piping with gasketed joints and revise to suit Project; delete if not required.

N. Install underground piping with restrained joints at horizontal and vertical changes in direction.  Use restrained-joint piping, thrust blocks, anchors, tie-rods and clamps, and other supports.

O. Comply with requirements in Division 21 Sections for fire-suppression-water piping inside the building.

P. Comply with requirements in Division 22 Section "Domestic Water Piping" for potable-water piping inside the building.

3.3 JOINT CONSTRUCTION

A. Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure rating same as or higher than systems pressure rating for aboveground applications unless otherwise indicated.

B. Install unions adjacent to each valve in tubing NPS 2 (DN 50) and smaller.

C. Install flanges, flange adaptors, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

D. Ream ends of tubes and remove burrs.

E. Remove scale, slag, dirt, and debris from outside and inside of pipes, tubes, and fittings before assembly.

F. Copper-Tubing, Brazed Joints:  Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

G. Copper-Tubing, Pressure-Sealed Joints:  Use proprietary crimping tool and procedure recommended by copper, pressure-seal-fitting manufacturer.

H. Ductile-Iron Piping, Gasketed Joints for Fire-Service-Main Piping:  UL 194.

I. Ductile-Iron Piping, Grooved Joints:  Cut-groove pipe.  Assemble joints with grooved-end, ductile-iron-piping couplings, gaskets, lubricant, and bolts.

J. Flanged Joints:  Select appropriate gasket material in size, type, and thickness suitable for water service.  Join flanges with bolts according to ASME B31.9.

K. PE Piping Heat-Fusion Joints:  Clean and dry joining surfaces by wiping with clean cloth or paper towels.  Join according to ASTM D 2657.

L. PVC Piping Gasketed Joints:  Use joining materials according to AWWA C900.  Construct joints with elastomeric seals and lubricant according to ASTM D 2774 or ASTM D 3139.

M. Fiberglass Piping Bonded Joints:  Use adhesive and procedure recommended by piping manufacturer.

N. Dissimilar Materials Piping Joints:  Use adapters compatible with both piping materials, with OD, and with system working pressure.

O. Do not use flanges or unions for underground piping.

3.4 ANCHORAGE INSTALLATION

Delete this article if anchorages are not required.

A. Anchorage, General:  Install water-distribution piping with restrained joints.  Anchorages and restrained-joint types that may be used include the following:

Retain subparagraphs below for types of anchorages and restrained joints permitted.

1. Concrete thrust blocks.

2. Locking mechanical joints.

3. Set-screw mechanical retainer glands.

4. Bolted flanged joints.

5. Heat-fused joints.

6. Pipe clamps and tie rods.

7. <Insert devices>.

B. Install anchorages for tees, plugs and caps, bends, crosses, valves, and hydrant branches in fire-suppression water-service piping according to NFPA 24 and the following:

1. Gasketed-Joint, Ductile-Iron, Water-Service Piping:  According to AWWA C600.

2. Gasketed-Joint, PVC Water-Service Piping:  According to AWWA M23.

3. Bonded-Joint Fiberglass, Water-Service Piping:  According to AWWA M45.

C. Apply full coat of asphalt or other acceptable corrosion-resistant material to surfaces of installed ferrous anchorage devices.

3.5 VALVE INSTALLATION

A. AWWA Gate Valves:  Comply with AWWA C600 and AWWA M44.  Install each underground valve with stem pointing up and with valve box.

B. AWWA Valves Other Than Gate Valves:  Comply with AWWA C600 and AWWA M44.

C. UL-Listed or FM-Approved Gate Valves:  Comply with NFPA 24.  Install each underground valve and valves in vaults with stem pointing up and with vertical cast-iron indicator post.

D. UL-Listed or FM-Approved Valves Other Than Gate Valves:  Comply with NFPA 24.

E. MSS Valves:  Install as component of connected piping system.

F. Corporation Valves and Curb Valves:  Install each underground curb valve with head pointed up and with service box.

G. Pressure-Reducing Valves:  Install in vault or aboveground between shutoff valves.[  Install full-size valved bypass.]

H. Support valves and piping, not direct buried, on concrete piers.  Comply with requirements for concrete piers in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

3.6 DETECTOR CHECK VALVE INSTALLATION

A. Install in vault or aboveground.

B. Install for proper direction of flow.  Install bypass with water meter, gate valves on each side of meter, and check valve downstream from meter.

C. Support detector check valves and piping on concrete piers.  Comply with requirements for concrete piers in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

3.7 WATER METER INSTALLATION

Delete this article if utility company provides water meters.

A. Install water meters, piping, and specialties according to utility company's written instructions.

Retain one or more of first three paragraphs below.

B. Water Meters:  Install [displacement] [turbine]-type water meters NPS 2 (DN 50) and smaller in meter boxes with shutoff valves on water meter inlets.  Include valves on water meter outlets, and include valved bypass around meters unless prohibited by authorities having jurisdiction.

C. Water Meters:  Install [compound] [turbine]-type water meters NPS 3 (DN 80) and larger in meter vaults.  Include shutoff valves on water meter inlets and outlets, and include valved bypass around meters.  Support meters, valves, and piping on brick or concrete piers.

D. Water Meters:  Install detector-type water meters in meter vault according to AWWA M6.  Include shutoff valves on water meter inlets and outlets, and include full-size valved bypass around meters.  Support meters, valves, and piping on brick or concrete piers.

E. Support water meters and piping NPS 3 (DN 80) and larger on concrete piers.  Comply with requirements for concrete piers in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

3.8 ROUGHING-IN FOR WATER METERS

Retain this article if Contractor is to rough-in for water meters to be installed by utility company.

A. Rough-in piping and specialties for water meter installation according to utility company's written instructions.

3.9 BACKFLOW PREVENTER INSTALLATION

A. Install backflow preventers of type, size, and capacity indicated.  Include valves and test cocks.  Install according to requirements of plumbing and health department and authorities having jurisdiction.

B. Do not install backflow preventers that have relief drain in vault or in other spaces subject to flooding.

C. Do not install bypass piping around backflow preventers.

Revise or delete paragraph below to suit Project.

D. Support NPS 2-1/2 (DN 65) and larger backflow preventers and piping on concrete piers.  Comply with requirements for concrete piers in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

3.10 WATER METER BOX INSTALLATION

A. Install water meter boxes in paved areas flush with surface.

B. Install water meter boxes in grass or earth areas with top [2 inches (50 mm)] <Insert dimension> above surface.

3.11 CONCRETE VAULT INSTALLATION

A. Install precast concrete vaults according to ASTM C 891.

3.12 PROTECTIVE ENCLOSURE INSTALLATION

A. Install concrete base level and with top approximately [2 inches (50 mm)] <Insert dimension> above grade.

B. Install protective enclosure over valves and equipment.

C. Anchor protective enclosure to concrete base.

3.13 FIRE HYDRANT INSTALLATION

A. General:  Install each fire hydrant with separate gate valve in supply pipe, anchor with restrained joints or thrust blocks, and support in upright position.

B. Wet-Barrel Fire Hydrants:  Install with valve below frost line.  Provide for drainage.

C. AWWA Fire Hydrants:  Comply with AWWA M17.

D. UL-Listed or FM-Approved Fire Hydrants:  Comply with NFPA 24.

3.14 FIRE-DEPARTMENT CONNECTION INSTALLATION

A. Install ball drip valves at each check valve for fire-department connection to mains.

B. Install protective pipe bollards [on two sides of] [on three sides of] <Insert arrangement> each fire-department connection.  Pipe bollards are specified in Division 05 Section "Metal Fabrications."

3.15 ALARM DEVICE INSTALLATION

Delete this article if alarm devices are specified in other Division 21 Sections.

A. General:  Comply with NFPA 24 for devices and methods of valve supervision.  Underground valves with valve box do not require supervision.

Retain one of first two paragraphs below to suit requirements of authorities having jurisdiction.

B. Supervisory Switches:  Supervise valves in open position.

1. Valves:  Grind away portion of exposed valve stem.  Bolt switch, with plunger in stem depression, to OS&Y gate-valve yoke.

2. Indicator Posts:  Drill and thread hole in upper-barrel section at target plate.  Install switch, with toggle against target plate, on barrel of indicator post.

C. Locking and Sealing:  Secure unsupervised valves as follows:

1. Valves:  Install chain and padlock on open OS&Y gate valve.

2. Post Indicators:  Install padlock on wrench on indicator post.

D. Pressure Switches:  Drill and thread hole in exposed barrel of fire hydrant.  Install switch.

E. Water-Flow Indicators:  Install in water-service piping in vault.  Select indicator with saddle and vane matching pipe size.  Drill hole in pipe, insert vane, and bolt saddle to pipe.

F. Connect alarm devices to building's fire-alarm system.  Wiring and fire-alarm devices are specified in Division 28 Sections.

3.16 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect fire-suppression water-service piping to [utility water main] [existing water main] <Insert piping system>.  Use [tapping sleeve and tapping valve] [service clamp and corporation valve] <Insert method>.

B. Connect fire-suppression water-service piping to interior fire-suppression piping.

C. Connect waste piping from concrete vault drains to [sanitary sewerage system.  Comply with requirements in Division 22 Section "Facility Sanitary Sewers" for connection to sanitary sewer] [storm-drainage system.  Comply with requirements in Division 33 Section "Storm Utility Drainage Piping" for connection to storm sewer].

3.17 SLEEVE INSTALLATION

A. General Requirements:  Install sleeves for pipes and tubes passing through penetrations in exterior walls.

Retain subparagraph below if sleeves are not required for core-drilled holes.

1. Exception:  Sleeves are not required for core-drilled holes.

B. Cut sleeves to length for mounting flush with both surfaces.

C. Install sleeves in new [floor slabs] [and] [walls] as they are constructed.

D. For exterior wall penetrations above grade, seal annular space between sleeves and piping using [joint sealants appropriate for size, depth, and location of joint.  Comply with requirements for joint sealants in Division 07 Section "Joint Sealants."] [sleeve seals.]

E. For exterior wall penetrations below grade, seal annular space between sleeves and piping using sleeve seals.

F. Seal space outside of sleeves in concrete walls with grout.

G. Install the following sleeve materials:

1. Galvanized- [steel pipe] [or] [steel-sheet] sleeves for pipes smaller than NPS 6 (DN 150).

2. [Cast-iron wall-pipe] [or] [galvanized-steel pipe] sleeves for pipes NPS 6 (DN 150) and larger.

3.18 SLEEVE SEAL INSTALLATION

Sleeve seals in this article are used in exterior concrete and masonry walls and in floors for a watertight seal around water-service piping entries into the building.  These seals typically require installation in a sleeve for proper operation.

A. Install sleeve seals in sleeves in exterior concrete [floor slabs] [and] [walls] at fire-suppression water-service piping entries into the building.

B. Select type and number of sealing elements required for pipe material and size.  Position pipe in center of sleeve.  Assemble sleeve seal components and install in annular space between pipe and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make a watertight seal.

3.19 FIELD QUALITY CONTROL

Revise this article to suit requirements of authorities having jurisdiction.

A. Use test procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described below.

B. Piping Tests:  Conduct piping tests before joints are covered and after concrete thrust blocks have hardened sufficiently.  Fill pipeline 24 hours before testing and apply test pressure to stabilize system.  Use only potable water.

C. Hydrostatic Tests:  Test at not less than one-and-one-half times the working pressure for two hours.

1. Increase pressure in 50-psig (350-kPa) increments and inspect each joint between increments.  Hold at test pressure for one hour; decrease to 0 psig (0 kPa).  Slowly increase again to test pressure and hold for one more hour.  Maximum allowable leakage is 2 quarts (1.89 L) per hour per 100 joints.  Remake leaking joints with new materials and repeat test until leakage is within allowed limits.

D. Prepare test and inspection reports.

3.20 IDENTIFICATION

A. Install continuous underground[ detectable] warning tape during backfilling of trench for underground fire-suppression water-service piping.  Locate below finished grade, directly over piping.  Underground warning tapes are specified in Division 31 Section "Earth Moving."

Retain paragraph below if using nonmetallic fire-suppression water-service piping or fire-suppression water-service piping with electrically insulated fittings.

B. Permanently attach equipment nameplate or marker indicating plastic fire-suppression water-service piping or fire-suppression water-service piping with electrically insulated fittings, on main electrical meter panel.  Comply with requirements for identifying devices in Division 22 Section "Identification for Plumbing Piping and Equipment."

3.21 CLEANING

Revise this article to suit requirements of authorities having jurisdiction.

A. Clean[ and disinfect] fire-suppression water-service piping as follows:

1. Purge new piping systems and parts of existing systems that have been altered, extended, or repaired before use.

Retain first subparagraph below for fire-protection-water piping not connected to potable-water supply.

2. Use purging[ and disinfecting] procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described in NFPA 24 for flushing of piping.  Flush piping system with clean, potable water until dirty water does not appear at points of outlet.

Retain subparagraph below for fire-suppression water-service piping connected to potable-water supply.

3. Use purging and disinfecting procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described in AWWA C651 or do as follows:

Retain one of first two subparagraphs below.

a. Fill system or part of system with water/chlorine solution containing at least 50 ppm of chlorine; isolate and allow to stand for 24 hours.

b. Drain system or part of system of previous solution and refill with water/chlorine solution containing at least 200 ppm of chlorine; isolate and allow to stand for three hours.

c. After standing time, flush system with clean, potable water until no chlorine remains in water coming from system.

d. Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedure if biological examination shows evidence of contamination.

B. Prepare reports of purging[ and disinfecting] activities.

3.22 PIPING SCHEDULE

See Editing Instruction No. 3 in the Evaluations for cautions about selecting products.

Retain one or more piping applications in this article.  Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Underground fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be[ one of] the following:

Retain one or both subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Hard] [Soft] copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

2. NPS 2 (DN 50) PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Underground fire-suppression water-service piping NPS 3 (DN 80) shall be[ one of] the following:

Retain one or more of five subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Hard] [Soft] copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

2. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

3. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

4. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

5. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Underground fire-suppression water-service piping NPS 4 (DN 100) shall be[ one of] the following:

Retain one or more of seven subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Hard] [Soft] copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

2. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

3. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

4. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

5. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

6. PVC, [Class 150] [Class 200] pipe listed for fire-protection service; PVC fittings of same class as pipe; and gasketed joints.

7. Fiberglass, RTRP, [Class 150] [Class 200]; RTRF; and bonded joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

D. Underground fire-suppression water-service piping [NPS 6 to NPS 12 (DN 150 to DN 300)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of six subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

4. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

5. PVC, [Class 150] [Class 200] pipe listed for fire-protection service; PVC fittings of same class as pipe; and gasketed joints.

6. Fiberglass, RTRP, [Class 150] [Class 200]; RTRF; and bonded joints.

E. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be hard copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought- or cast-copper-alloy, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

F. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 3 and NPS 4 (DN 80 and DN 100)] <Insert pipe size range> shall be[ one of] the following:

Retain one or both subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Hard copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

2. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

G. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 5 to NPS 12 (DN 125 to DN 300)] <Insert pipe size range> shall be grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

Piping in three paragraphs below is for fire-suppression water-service piping that will be installed, buried in earth, below the lowest floor, and within the building footprint; retain if required.

H. Underslab fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be [hard] [soft] copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

I. Underslab fire-suppression water-service piping [NPS 3 and NPS 4 (DN 80 and DN 100)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of four subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Hard] [Soft] copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

2. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

3. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and restrained, gasketed joints.

4. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and restrained, gasketed joints.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

J. Underslab fire-suppression water-service piping [NPS 6 to NPS 12 (DN 150 to DN 300)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of three subparagraphs below.  If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and restrained, gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and restrained, gasketed joints.

3.23 VALVE SCHEDULE

See Editing Instruction No. 3 in the Evaluations for cautions about selecting products.

Retain one or more valve applications in this article.  Coordinate with materials specified in Part 2.

A. Drawings indicate valve types to be used.  Where specific valve types are not indicated, the following requirements apply:

B. Underground fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be corporation valves or curb valves with ends compatible with piping.

C. Meter box fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be meter valves.

D. Vault fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be [Class 125, MSS, bronze, nonrising stem] [or] [UL-listed or FM-approved, OS&Y, bronze,] gate valves.

Retain "one of" option in first paragraph below to allow Contractor to select valve materials from those retained.

E. Underground fire-suppression water-service shutoff valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or more of three subparagraphs below.  If using more than one type of valve, identify various valve types on Drawings.

1. 200-psig (1380-kPa), AWWA, iron, nonrising-stem, [metal] [resilient]-seated gate valves.

2. 250-psig (1725-kPa), AWWA, iron, nonrising-stem, resilient-seated gate valves.

3. [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM-approved, iron, nonrising-stem gate valves.

F. Indicator-post underground fire-suppression water-service valves NPS 3 (DN 80) and larger shall be [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM-approved, iron, nonrising-stem gate valves with indicator-post flange.

Retain "one of" option in first paragraph below to allow Contractor to select valve materials from those retained.

G. Standard-pressure, [aboveground] [and] [vault] fire-suppression water-service shutoff valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or more of four subparagraphs below.  If using more than one type of valve, identify various valve types on Drawings.

1. 200-psig (1380-kPa), AWWA, iron, OS&Y, [metal] [resilient]-seated gate valves.

2. 250-psig (1725-kPa), AWWA, iron, OS&Y, resilient-seated gate valves.

3. [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM-approved, iron, OS&Y gate valves.

4. [AWWA] [or] [UL-listed or FM-approved] butterfly valves.

Retain "one of" option in paragraph below to allow Contractor to select valve materials from those retained.

H. Fire-suppression water-service check valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or both subparagraphs below.  If using more than one type of valve, identify various valve types on Drawings.

1. [AWWA] [or] [UL-listed or FM-approved] check valves.

2. UL-listed or FM-approved detector check valves.

END OF SECTION 211100

	FACILITY FIRE-SUPPRESSION WATER-SERVICE PIPING
	211100 - 1



