Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
12/02 (R 06/06)

Copyright 2002 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221316 - SANITARY WASTE AND VENT PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following for soil, waste, and vent piping inside the building:

Adjust list below to suit Project.

1. Pipe, tube, and fittings.

2. Special pipe fittings.

3. Encasement for underground metal piping.

B. Related Sections include the following:

List below products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Sanitary Sewerage Pumps."

2. Division 22 Section "Chemical Waste-Systems for Laboratory and Healthcare Facilities" for chemical-waste and vent piping systems.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. EPDM:  Ethylene-propylene-diene terpolymer rubber.

C. LLDPE:  Linear, low-density polyethylene plastic.

D. NBR:  Acrylonitrile-butadiene rubber.

E. PE:  Polyethylene plastic.

F. PVC:  Polyvinyl chloride plastic.

G. TPE:  Thermoplastic elastomer.

1.4 PERFORMANCE REQUIREMENTS

A. Components and installation shall be capable of withstanding the following minimum working pressure, unless otherwise indicated:

Revise pressure ratings in two subparagraphs below to suit Project.  Coordinate with Division 22 Section "Sanitary Waste Piping Specialties." Soil and waste piping may require higher rating if used in high-rise buildings.

1. Soil, Waste, and Vent Piping:  [10-foot head of water (30 kPa)] <Insert pressure>.

2. Sanitary Sewer, Force-Main Piping:  [50 psig (345 kPa)] [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert pressure>.

Revise paragraph below to indicate specific loads determined by Project's structural engineer or refer to loads indicated on Drawings.  Model building codes and ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

B. Seismic Performance:  Soil, waste, and vent piping and support and installation shall be capable of withstanding the effects of seismic events determined according to [ASCE 7, "Minimum Design Loads for Buildings and Other Structures."] <Insert applicable code requirement.>

1.5 SUBMITTALS

Retain first paragraph below if required.

A. Product Data:  For pipe, tube, fittings, and couplings.

B. LEED Submittal:

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for solvent cements and adhesive primers.

1. Product Data for Credit EQ 4.1:  For solvent cements and adhesive primers, including printed statement of VOC content.

C. Shop Drawings:

Retain subparagraph below if piping is required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

1. Design Calculations:  Signed and sealed by a qualified professional engineer for selecting seismic restraints.

Retain subparagraph below if sovent drainage system is retained.

2. Sovent Drainage System:  Include plans, elevations, sections, and details.

D. Field quality-control inspection and test reports.

1.6 QUALITY ASSURANCE

A. Piping materials shall bear label, stamp, or other markings of specified testing agency.

Retain paragraph below if NSF markings are required.

B. Comply with NSF 14, "Plastics Piping Systems Components and Related Materials," for plastic piping components.  Include marking with "NSF-dwv" for plastic drain, waste, and vent piping; "NSF-drain" for plastic drain piping; "NSF-tubular" for plastic continuous waste piping; and "NSF-sewer" for plastic sewer piping.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to edit this Section.

A. Refer to Part 3 "Piping Applications" Article for applications of pipe, tube, fitting, and joining materials.

2.3 HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS

Pipe and fittings in this Article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

A. Pipe and Fittings:  ASTM A 74, [Service] [and] [Extra-Heavy] class(es).

B. Gaskets:  ASTM C 564, rubber.

C. Calking Materials:  ASTM B 29, pure lead and oakum or hemp fiber.

2.4 HUBLESS CAST-IRON SOIL PIPE AND FITTINGS

Pipe, fittings, and couplings in first two paragraphs below are available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

A. Pipe and Fittings:  ASTM A 888 or CISPI 301.

Sovent stack fittings in first paragraph below are available in NPS 2 to NPS 8 (DN 50 to DN 200).  Use of sovent fittings does not eliminate need for standard hubless cast-iron pipe fittings.

B. Sovent Stack Fittings:  ASME B16.45 or ASSE 1043, hubless, cast-iron aerator and deaerator drainage fittings.

C. Shielded Couplings:  ASTM C 1277 assembly of metal shield or housing, corrosion-resistant fasteners, and rubber sleeve with integral, center pipe stop.

Couplings in subparagraph below are available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375) and are economical, but may not be suitable for installation in corrosive soil.

1. Standard, Shielded, Stainless-Steel Couplings:  CISPI 310, with stainless-steel corrugated shield; stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

a. [Available ]Manufacturers:

1) ANACO.

2) Fernco, Inc.

3) Ideal Div.; Stant Corp.

4) Mission Rubber Co.

5) Tyler Pipe; Soil Pipe Div.

6) <Insert manufacturer's name.>

Couplings in subparagraph below are available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375), and include various configurations of manufacturers' "heavy-duty," shielded, stainless-steel couplings.

2. Heavy-Duty, Shielded, Stainless-Steel Couplings:  With stainless-steel shield, stainless-steel bands and tightening devices, and ASTM C 564, rubber sleeve.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

a. [Available ]Manufacturers:

1) ANACO.

2) Clamp-All Corp.

3) Ideal Div.; Stant Corp.

4) Mission Rubber Co.

5) Tyler Pipe; Soil Pipe Div.

6) <Insert manufacturer's name.>

Couplings in subparagraph below are available in NPS 1-1/2 to NPS 10 (DN 40 to DN 250).

3. Heavy-Duty, Shielded, Cast-Iron Couplings:  ASTM A 48/A 48M, two-piece, cast-iron housing; stainless-steel bolts and nuts; and ASTM C 564, rubber sleeve.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

a. [Available ]Manufacturers:

1) MG Piping Products Co.

2) Insert manufacturer's name.
Couplings in paragraph below are available in NPS 1-1/2 to NPS 4 (DN 40 to DN 100), and should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

D. Rigid, Unshielded Couplings:  ASTM C 1461, sleeve-type, reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. <Insert manufacturer's name.>

2.5 STEEL PIPE AND FITTINGS

Pipe in paragraph below is available in NPS 1/8 to NPS 26 (DN 6 to DN 650).

Edit paragraph for specific type or grade, and wall thickness if required.

A. Steel Pipe:  ASTM A 53/A 53M, Type E or S, Grade A or B, Standard Weight or Schedule 40, galvanized.  Include ends matching joining method.

Fittings in first paragraph below are available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

B. Drainage Fittings:  ASME B16.12[, galvanized], threaded, cast-iron drainage pattern.

C. Pressure Fittings:

Fittings in subparagraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

1. Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106, Schedule 40, galvanized, seamless steel pipe.  Include ends matching joining method.

Fittings in subparagraph below are available in NPS 1/8 to NPS 4 (DN 6 to DN 100).

2. Malleable-Iron Unions:  ASME B16.39; Class 150; hexagonal-stock body with ball-and-socket, metal-to-metal, bronze seating surface; and female threaded ends.

Fittings in subparagraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

3. Gray-Iron, Threaded Fittings:  ASME B16.4, Class 125, [galvanized, ]standard pattern.

Fittings in subparagraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

4. Cast-Iron Flanges:  ASME B16.1, Class 125.

Fittings in subparagraph below are available in NPS 4 to NPS 72 (DN 100 to DN 1800).

5. Cast-Iron, Flanged Fittings:  ASME B16.1, Class 125[, galvanized].

Fittings and couplings in paragraph and subparagraphs below are available in NPS 3/4 to NPS 24 (DN 20 to DN 600).

D. Grooved-Joint Systems:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Anvil International.

b. Star Pipe Products; Star Fittings Div.

c. Victaulic Company.

d. Ward Manufacturing, Inc.

e. <Insert manufacturer's name.>

2. Grooved-End, Steel-Piping Fittings:  ASTM A 47/A 47M, [galvanized, ]malleable-iron casting; ASTM A 106, galvanized-steel pipe; or ASTM A 536, [galvanized, ]ductile-iron casting; with dimensions matching steel pipe.

3. Grooved-End, Steel-Piping Couplings:  AWWA C606, for steel-pipe dimensions.  Include ferrous housing sections, gasket suitable for water, and bolts and nuts.

2.6 STAINLESS-STEEL PIPE AND FITTINGS

Pipe and fittings in this Article are available in NPS 2 to NPS 6 (DN 50 to DN 150).

A. Pipe and Fittings:  ASME A112.3.1, drainage pattern with socket and spigot ends.

B. Gaskets:  Lip seals shaped to fit socket groove, with plastic backup ring.

1. Material:  EPDM, unless NBR is indicated.

2.7 DUCTILE-IRON PIPE AND FITTINGS

Pipe and fittings in paragraph and subparagraphs below are available in NPS 3 to NPS 24 (DN 80 to DN 600).

A. Mechanical-Joint, Ductile-Iron Pipe:  AWWA C151, with mechanical-joint bell and plain spigot end, unless grooved or flanged ends are indicated.

1. Mechanical-Joint, Ductile-Iron Fittings:  AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

2. Glands, Gaskets, and Bolts:  AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Pipe and fittings in paragraph and subparagraphs below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

B. Push-on-Joint, Ductile-Iron Pipe:  AWWA C151, with push-on-joint bell and plain spigot end, unless grooved or flanged ends are indicated.

1. Push-on-Joint, Ductile-Iron Fittings:  AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

2. Gaskets:  AWWA C111, rubber.

Fittings and couplings in paragraph and subparagraphs below are available in NPS 4 to NPS 24 (DN 100 to DN 600).

C. Grooved-Joint Systems:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Victaulic Company.

b. <Insert manufacturer's name.>

2. Grooved-End, Ductile-Iron Fittings:  ASTM A 47/A 47M, malleable-iron castings or ASTM A 536, ductile-iron castings with dimensions matching pipe.

3. Grooved-End, Ductile-Iron-Piping Couplings:  AWWA C606, for ductile-iron-pipe dimensions.  Include ferrous housing sections, gasket suitable for water, and bolts and nuts.

Flanges in paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

D. Flanges:  ASME 16.1, Class 125, cast iron.

2.8 COPPER TUBE AND FITTINGS

Tube and fittings in first paragraph and subparagraph below are available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

A. Copper DWV Tube:  ASTM B 306, drainage tube, drawn temper.

1. Copper Drainage Fittings:  ASME B16.23, cast copper or ASME B16.29, wrought copper, solder-joint fittings.

Tube and fittings in two paragraphs and associated subparagraphs below are available in NPS 1/4 to NPS 12 (DN 6 to DN 300), except flanges are available in NPS 1/4 to at least NPS 6 (DN 8 to at least DN 150) and unions are available in NPS 1/2 to NPS 4 (DN 20 to DN 100).

B. Hard Copper Tube:  ASTM B 88, Types L and M (ASTM B 88M, Types B and C), water tube, drawn temper.

1. Copper Pressure Fittings:  ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint fittings.  Furnish wrought-copper fittings if indicated.

2. Copper Flanges:  ASME B16.24, Class 150, cast copper with solder-joint end.

3. Copper Unions:  MSS SP-123, copper-alloy, hexagonal-stock body with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

C. Soft Copper Tube:  ASTM B 88, Type L (ASTM B 88M, Type B), water tube, annealed temper.

1. Copper Pressure Fittings:  ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint fittings.  Furnish wrought-copper fittings if indicated.

2.9 ABS PIPE AND FITTINGS

Pipe and fittings in this Article are available in NPS 1-1/4 to NPS 6 (DN 32 to DN 150).  Retain one or both of first two paragraphs below and coordinate with Part 3 "Piping Applications" Article.

A. Solid-Wall ABS Pipe:  ASTM D 2661, Schedule 40.

B. Cellular-Core ABS Pipe:  ASTM F 628, Schedule 40.

C. ABS Socket Fittings:  ASTM D 2661, made to ASTM D 3311, drain, waste, and vent patterns.

D. Solvent Cement and Adhesive Primer:

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use ABS solvent cement that has a VOC content of 325 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2.10 PVC PIPE AND FITTINGS

Pipe and fittings in two paragraphs and associated subparagraph below are available in NPS 1-1/4 to NPS 12 (DN 32 to DN 300).  Retain one or both paragraphs and subparagraphs and coordinate with Part 3 "Piping Applications" Article.

A. Solid-Wall PVC Pipe:  ASTM D 2665, drain, waste, and vent.

1. PVC Socket Fittings:  ASTM D 2665, socket type, made to ASTM D 3311, drain, waste, and vent patterns.

B. Cellular-Core PVC Pipe:  ASTM F 891, Schedule 40.

1. PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Schedule 40 pipe.

Pipe and fittings in paragraph and subparagraph below are available in NPS 3 to NPS 12 (DN 80 to DN 300).

C. Cellular-Core, Sewer and Drain Series, PVC Pipe:  ASTM F 891, Series PS 100.

1. PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Series PS 100 sewer and drain pipe.

D. Solvent Cement and Adhesive Primer:

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2.11 SPECIAL PIPE FITTINGS

Retain pipe couplings in first four paragraphs and associated subparagraphs below if dissimilar piping materials or piping with small differences in OD must be joined.

Couplings in paragraph and subparagraphs below are for underground nonpressure piping and should be available in all sizes.

A. Flexible, Nonpressure Pipe Couplings:  Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition pattern.  Include shear ring, ends of same sizes as piping to be joined, and corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Dallas Specialty & Mfg. Co.

b. Fernco, Inc.

c. Logan Clay Products Company (The).

d. Mission Rubber Co.

e. NDS, Inc.

f. Plastic Oddities, Inc.

g. <Insert manufacturer's name.>

2. Sleeve Materials:

a. For Cast-Iron Soil Pipes:  ASTM C 564, rubber.

b. For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

c. For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Couplings in paragraph and subparagraphs below are for aboveground nonpressure piping and should be available in most sizes.

B. Shielded Nonpressure Pipe Couplings:  ASTM C 1460, elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Cascade Waterworks Mfg. Co.

b. Mission Rubber Co.

c. <Insert manufacturer's name.>

Couplings in paragraph and subparagraphs below are for aboveground and underground nonpressure piping, are available in NPS 1-1/2 to NPS 4 (DN 40 to DN 100), and should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

C. Rigid, Unshielded, Nonpressure Pipe Couplings:  ASTM C 1461, sleeve-type reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. <Insert manufacturer's name.>

Couplings in paragraph and subparagraphs below are for underground pressure piping and are available in at least NPS 1-1/2 to NPS 24 (DN 40 to DN 600).

D. Pressure Pipe Couplings:  AWWA C219 metal, sleeve-type same size as, with pressure rating at least equal to, and ends compatible with, pipes to be joined.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Cascade Waterworks Mfg. Co.

b. Dresser, Inc.; DMD Div.

c. EBAA Iron Sales, Inc.

d. Ford Meter Box Company, Inc. (The); Pipe Products Div.

e. JCM Industries, Inc.

f. Romac Industries, Inc.

g. Smith-Blair, Inc.

h. Viking Johnson.

i. <Insert manufacturer's name.>

2. Center-Sleeve Material:  [Manufacturer's standard] [Carbon steel] [Stainless steel] [Ductile iron] [Malleable iron].

3. Gasket Material:  Natural or synthetic rubber.

4. Metal Component Finish:  Corrosion-resistant coating or material.

Ball joints in paragraph and subparagraphs below are for underground piping and are available in NPS 4 to NPS 48 (DN 100 to DN 1200).

E. Flexible Ball Joints:  Ductile-iron fitting with combination of flanged and mechanical-joint ends complying with AWWA C110 or AWWA C153.  Include gasketed ball-joint section and ductile-iron gland, rubber gasket, and steel bolts.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. EBAA Iron Sales, Inc.

b. <Insert manufacturer's name.>

Expansion joints in paragraph and subparagraphs below are for underground piping and are available in NPS 3 to NPS 48 (DN 80 to DN 1200).  Use of this fitting requires offset and expansion-limit dimensions on Drawings.

F. Expansion Joints:  Two or three-piece, ductile-iron assembly consisting of telescoping sleeve(s) with gaskets and restrained-type, ductile-iron, bell-and-spigot end sections complying with AWWA C110 or AWWA C153.  Select and assemble components for expansion indicated.  Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. EBAA Iron Sales, Inc.

b. Romac Industries, Inc.

c. Star Pipe Products; Star Fittings Div.

d. <Insert manufacturer's name.>

Fittings in paragraph and subparagraphs below are for underground piping wall penetrations and are available in NPS 3 to NPS 30 (DN 80 to DN 750).

G. Wall-Penetration Fittings:  Compound, ductile-iron coupling fitting with sleeve and flexing sections for up to 20-degree deflection, gaskets, and restrained-joint ends complying with AWWA C110 or AWWA C153.  Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. SIGMA Corp.

b. <Insert manufacturer's name.>

2.12 ENCASEMENT FOR UNDERGROUND METAL PIPING

Retain this Article if corrosion protection is required for underground metal piping.

A. Description:  ASTM A 674 or AWWA C105, [high-density, crosslaminated PE film of 0.004-inch (0.10-mm)] [or] [LLDPE film of 0.008-inch (0.20-mm)] minimum thickness.

B. Form:  [Sheet] [or] [tube].

C. Color:  [Black] [or] [natural].

PART 3 -  EXECUTION

3.1 EXCAVATION

A. Refer to Division 31 Section "Earth Moving" for excavating, trenching, and backfilling.

3.2 PIPING APPLICATIONS

Select piping applications from this Article.  Coordinate with materials specified in Part 2.  Revise to suit Project.

A. Flanges and unions may be used on aboveground pressure piping, unless otherwise indicated.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

B. Aboveground, soil and waste piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first seven subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless cast-iron soil pipe and fittings[ and sovent stack fittings]; [standard, shielded, stainless-steel] [heavy-duty shielded, stainless-steel] [and] [rigid, unshielded] couplings; and hubless-coupling joints.

3. Steel pipe, drainage fittings, and threaded joints.

4. Stainless-steel pipe and fittings, gaskets, and gasketed joints.

5. Copper DWV tube, copper drainage fittings, and soldered joints.

6. [Solid-wall] [Cellular-core] ABS pipe, ABS socket fittings, and solvent-cemented joints.

7. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

8. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] [Rigid, unshielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

C. Aboveground, soil and waste piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless cast-iron soil pipe and fittings [ and sovent stack fittings]; [standard,] [and] [heavy-duty] shielded, stainless-steel couplings; and hubless-coupling joints.

3. Steel pipe, drainage fittings, and threaded joints.

4. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

D. Aboveground, vent piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first seven subparagraphs and associated subparagraph below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless cast-iron soil pipe and fittings; [standard, shielded, stainless-steel] [heavy-duty shielded, stainless-steel] [and] [rigid, unshielded] couplings; and hubless-coupling joints.

3. Steel pipe, drainage fittings, and threaded joints.

4. Stainless-steel pipe and fittings gaskets, and gasketed joints.

5. Copper DWV tube, copper drainage fittings, and soldered joints.

a. Option for Vent Piping, NPS 2-1/2 and NPS 3-1/2 (DN 65 and DN 90):  Hard copper tube, Type M (Type C); copper pressure fittings; and soldered joints.

6. [Solid-wall] [Cellular-core] ABS pipe, ABS socket fittings, and solvent-cemented joints.

7. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

8. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] [Rigid, unshielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

E. Aboveground, vent piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless cast-iron soil pipe and fittings; [standard,] [and] [heavy-duty] shielded, stainless-steel couplings; and hubless-coupling joints.

3. Steel pipe, drainage fittings, and threaded joints.

4. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

F. Underground, soil, waste, and vent piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first six subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. [Extra-Heavy] [Service] class, cast-iron soil piping; [gaskets; and gasketed] [calking materials; and calked] joints.

2. Hubless cast-iron soil pipe and fittings; [standard, shielded, stainless-steel] [heavy-duty shielded, stainless-steel] [heavy-duty shielded, cast-iron] [and] [rigid, unshielded] couplings; and hubless-coupling joints.

3. Stainless-steel pipe and fittings, gaskets, and gasketed joints.

4. [Cellular-core] [Solid wall] ABS pipe, ABS socket fittings, and solvent-cemented joints.

5. [Cellular-core] [Solid wall] PVC pipe, PVC socket fittings, and solvent-cemented joints.

Pipe and fittings material in first subparagraph below are only available down to NPS 3 (DN 80).  Either delete subparagraph if sizes are smaller than NPS 3 (DN 80) or be prepared to accept pipe sizes larger than indicated on Drawings if these materials are selected by Contractor.

6. Cellular-core, Sewer and Drain Series, PVC pipe; PVC socket fittings; and solvent-cemented joints.

7. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] [Rigid, unshielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

G. Underground, soil and waste piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. [Extra-Heavy] [Service] class, cast-iron soil piping; [gaskets; and gasketed] [calking materials; and calked] joints.

2. Hubless cast-iron soil pipe and fittings; [standard, shielded, stainless-steel] [heavy-duty shielded, stainless-steel] [and] [heavy-duty shielded, cast-iron] couplings; and hubless-coupling joints.

Delete first two subparagraphs below for piping NPS 15 (DN 375) and larger.

3. [Cellular-core] [Solid-wall], Schedule 40, PVC pipe; PVC socket fittings; and solvent-cemented joints.

4. Cellular-core, Sewer and Drain Series, PVC pipe; PVC socket fittings; and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings:  [Flexible,] [Shielded,] nonpressure pipe couplings for joining dissimilar pipe materials with small difference in OD.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

H. Aboveground sanitary-sewage force mains [NPS 1-1/2 and NPS 2 (DN 40 and DN 50)] <Insert pipe size range> shall be[ any of] the following:

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Hard copper tube, [Type L (Type B)] [Type M (Type C)]; copper pressure fittings; and soldered joints.

2. Steel pipe, pressure fittings, and threaded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

I. Aboveground sanitary-sewage force mains [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of three subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Hard copper tube, [Type L (Type B)] [Type M (Type C)]; copper pressure fittings; and soldered joints.

2. Steel pipe, pressure fittings, and threaded joints.

3. Grooved-end steel pipe, grooved-joint system fittings and couplings, and grooved joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

J. Underground sanitary-sewage force mains [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs and associated subparagraph below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. [Hard] [Soft] copper tube, Type L (Type B); [wrought-]copper pressure fittings; and soldered joints.

2. Steel pipe, pressure fittings, and threaded joints.

a. Include grooved-joint system fittings and couplings and grooved joints where indicated.

3. Mechanical-joint, ductile-iron pipe; mechanical-joint, ductile-iron fittings; glands, gaskets, and bolts; and mechanical joints.

a. Include grooved-joint system fittings and couplings and grooved joints where indicated.

4. Push-on-joint, ductile-iron pipe; push-on-joint ductile-iron fittings; gaskets; and gasketed joints.

a. Include grooved-joint system fittings and couplings and grooved joints where indicated.

5. Pressure pipe couplings, if dissimilar pipe materials or piping with small difference in OD must be joined.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

K. Underground sanitary-sewage force mains [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first three subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Steel pipe, pressure fittings, and threaded joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, ductile-iron fittings; glands, gaskets, and bolts; and mechanical-joint joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron fittings; gaskets; and gasketed joints.

4. Pressure pipe couplings, if dissimilar pipe materials or piping with small difference in OD must be joined.

3.3 PIPING INSTALLATION

Sanitary sewer piping outside the building is specified in Division 22 Section "Facility Sanitary Sewers." Edit first paragraph below to suit Project.

A. Sanitary sewer piping outside the building is specified in Division 22 Section "Facility Sanitary Sewers."

B. Basic piping installation requirements are specified in Division 22 Section "Common Work Results for Plumbing."

Retain first paragraph below if piping is required to withstand specific design loads.

C. Install seismic restraints on piping.  Seismic-restraint devices are specified in Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

D. Install cleanouts at grade and extend to where building sanitary drains connect to building sanitary sewers.

E. Install cleanout fitting with closure plug inside the building in sanitary force-main piping.

Retain paragraph below if steel, force-main piping is required.

F. Install underground, steel, force-main piping.[ Install encasement on piping according to ASTM A 674 or AWWA C105.]

Retain paragraph and subparagraph below if ductile-iron, force-main piping is required.

G. Install underground, ductile-iron, force-main piping according to AWWA C600.  Install buried piping inside the building between wall and floor penetrations and connection to sanitary sewer piping outside the building with restrained joints.  Anchor pipe to wall or floor.  Install thrust-block supports at vertical and horizontal offsets.

1. Install encasement on piping according to ASTM A 674 or AWWA C105.

Retain first paragraph and subparagraph below if copper, force-main tubing is required.

H. Install underground, copper, force-main tubing according to CDA's "Copper Tube Handbook."

1. Install encasement on piping according to ASTM A 674 or AWWA C105.

I. Install underground, ductile-iron, special pipe fittings according to AWWA C600.

1. Install encasement on piping according to ASTM A 674 or AWWA C105.

Retain one of first two paragraphs below.

J. Install cast-iron sleeve with water stop and mechanical sleeve seal at each service pipe penetration through foundation wall.  Select number of interlocking rubber links required to make installation watertight.  Sleeves and mechanical sleeve seals are specified in Division 22 Section "Common Work Results for Plumbing."

K. Install wall-penetration fitting at each service pipe penetration through foundation wall.  Make installation watertight.

L. Install cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook," Chapter IV, "Installation of Cast Iron Soil Pipe and Fittings."

1. Install encasement on underground piping according to ASTM A 674 or AWWA C105.

M. Make changes in direction for soil and waste drainage and vent piping using appropriate branches, bends, and long-sweep bends.  Sanitary tees and short-sweep 1/4 bends may be used on vertical stacks if change in direction of flow is from horizontal to vertical.  Use long-turn, double Y-branch and 1/8-bend fittings if 2 fixtures are installed back to back or side by side with common drain pipe.  Straight tees, elbows, and crosses may be used on vent lines.  Do not change direction of flow more than 90 degrees.  Use proper size of standard increasers and reducers if pipes of different sizes are connected.  Reducing size of drainage piping in direction of flow is prohibited.

N. Lay buried building drainage piping beginning at low point of each system.  Install true to grades and alignment indicated, with unbroken continuity of invert.  Place hub ends of piping upstream.  Install required gaskets according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.  Maintain swab in piping and pull past each joint as completed.

O. Install soil and waste drainage and vent piping at the following minimum slopes, unless otherwise indicated:

Edit three subparagraphs below as required by authorities having jurisdiction.

1. Building Sanitary Drain:  2 percent downward in direction of flow for piping NPS 3 (DN 80) and smaller; 1 percent downward in direction of flow for piping NPS 4 (DN 100) and larger.

2. Horizontal Sanitary Drainage Piping:  2 percent downward in direction of flow.

3. Vent Piping:  1 percent down toward vertical fixture vent or toward vent stack.

P. Install engineered soil and waste drainage and vent piping systems as follows:

1. Combination Waste and Vent:  Comply with standards of authorities having jurisdiction.

2. Sovent Drainage System:  Comply with ASSE 1043 and sovent fitting manufacturer's written installation instructions.

3. Reduced-Size Venting:  Comply with standards of authorities having jurisdiction.

Q. Sleeves are not required for cast-iron soil piping passing through concrete slabs-on-grade if slab is without membrane waterproofing.

R. Install ABS soil and waste drainage and vent piping according to ASTM D 2661.

S. Install PVC soil and waste drainage and vent piping according to ASTM D 2665.

T. Install underground [ABS] [and] [PVC] soil and waste drainage piping according to ASTM D 2321.

U. Do not enclose, cover, or put piping into operation until it is inspected and approved by authorities having jurisdiction.

3.4 JOINT CONSTRUCTION

A. Basic piping joint construction requirements are specified in Division 22 Section "Common Work Results for Plumbing."

B. Join hub-and-spigot, cast-iron soil piping with gasket joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

C. Join hub-and-spigot, cast-iron soil piping with calked joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for lead and oakum calked joints.

D. Join hubless cast-iron soil piping according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for hubless-coupling joints.

E. Soldered Joints:  Use ASTM B 813, water-flushable, lead-free flux; ASTM B 32, lead-free-alloy solder; and ASTM B 828 procedure, unless otherwise indicated.

F. Grooved Joints:  Assemble joint with keyed coupling, gasket, lubricant, and bolts according to coupling and fitting manufacturer's written instructions.

G. PVC Nonpressure Piping Joints:  Join piping according to ASTM D 2665.

3.5 VALVE INSTALLATION

Retain this Article if valves are required.

A. General valve installation requirements are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

B. Shutoff Valves:  Install shutoff valve on each sewage pump discharge.

1. Install gate or full-port ball valve for piping NPS 2 (DN 50) and smaller.

2. Install gate valve for piping NPS 2-1/2 (DN 65) and larger.

C. Check Valves:  Install swing check valve, between pump and shutoff valve, on each sewage pump discharge.

D. Backwater Valves:  Install backwater valves in piping subject to sewage backflow.

1. Horizontal Piping:  Horizontal backwater valves.[ Use normally closed type, unless otherwise indicated.]

2. Floor Drains:  Drain outlet backwater valves, unless drain has integral backwater valve.

3. Install backwater valves in accessible locations.

4. Backwater valve are specified in Division 22 Section "Sanitary Waste Piping Specialties."

3.6 HANGER AND SUPPORT INSTALLATION

A. Seismic-restraint devices are specified in Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

B. Pipe hangers and supports are specified in Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment." Install the following:

1. Vertical Piping:  MSS Type 8 or Type 42, clamps.

2. Install individual, straight, horizontal piping runs according to the following:

a. 100 Feet (30 m) and Less:  MSS Type 1, adjustable, steel clevis hangers.

b. Longer Than 100 Feet (30 m):  MSS Type 43, adjustable roller hangers.

c. Longer Than 100 Feet (30 m), if Indicated:  MSS Type 49, spring cushion rolls.

3. Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer:  MSS Type 44, pipe rolls.  Support pipe rolls on trapeze.

4. Base of Vertical Piping:  MSS Type 52, spring hangers.

C. Install supports according to Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment."

D. Support vertical piping and tubing at base and at each floor.

E. Rod diameter may be reduced 1 size for double-rod hangers, with 3/8-inch (10-mm) minimum rods.

Maximum spans below were taken from MSS SP-69 for water service and from model plumbing codes.  Most restrictive piping and spacing dimensions are shown.

F. Install hangers for cast-iron soil piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/2 and NPS 2 (DN 40 and DN 50):  60 inches (1500 mm) with 3/8-inch (10-mm) rod.

2. NPS 3 (DN 80):  60 inches (1500 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 and NPS 5 (DN 100 and DN 125):  60 inches (1500 mm) with 5/8-inch (16-mm) rod.

4. NPS 6 (DN 150):  60 inches (1500 mm) with 3/4-inch (19-mm) rod.

5. NPS 8 to NPS 12 (DN 200 to DN 300):  60 inches (1500 mm) with 7/8-inch (22-mm) rod.

G. Install supports for vertical cast-iron soil piping every 15 feet (4.5 m).

H. Install hangers for steel piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/4 (DN 32):  84 inches (2100 mm) with 3/8-inch (10-mm) rod.

2. NPS 1-1/2 (DN 40):  108 inches (2700 mm) with 3/8-inch (10-mm) rod.

3. NPS 2 (DN 50):  10 feet (3 m) with 3/8-inch (10-mm) rod.

4. NPS 2-1/2 (DN 65):  11 feet (3.4 m) with 1/2-inch (13-mm) rod.

5. NPS 3 (DN 80):  12 feet (3.7 m) with 1/2-inch (13-mm) rod.

6. NPS 4 and NPS 5 (DN 100 and DN 125):  12 feet (3.7 m) with 5/8-inch (16-mm) rod.

7. NPS 6 (DN 150):  12 feet (3.7 m) with 3/4-inch (19-mm) rod.

8. NPS 8 to NPS 12 (DN 200 to DN 300):  12 feet (3.7 m) with 7/8-inch (22-mm) rod.

I. Install supports for vertical steel piping every 15 feet (4.5 m).

J. Install hangers for stainless-steel piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 2 (DN 50):  84 inches (2100 mm) with 3/8-inch (10-mm) rod.

2. NPS 3 (DN 80):  96 inches (2400 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 (DN 100):  108 inches (2700 mm) with 1/2-inch (13-mm) rod.

4. NPS 6 (DN 150):  10 feet (3 m) with 5/8-inch (16-mm) rod.

K. Install supports for vertical stainless-steel piping every 10 feet (3 m).

L. Install hangers for copper tubing with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/4 (DN 32):  72 inches (1800 mm) with 3/8-inch (10-mm) rod.

2. NPS 1-1/2 and NPS 2 (DN 40 and DN 50):  96 inches (2400 mm) with 3/8-inch (10-mm) rod.

3. NPS 2-1/2 (DN 65):  108 inches (2700 mm) with 1/2-inch (13-mm) rod.

4. NPS 3 to NPS 5 (DN 80 to DN 125):  10 feet (3 m) with 1/2-inch (13-mm) rod.

5. NPS 6 (DN 150):  10 feet (3 m) with 5/8-inch (16-mm) rod.

6. NPS 8 (DN 200):  10 feet (3 m) with 3/4-inch (19-mm) rod.

M. Install supports for vertical copper tubing every 10 feet (3 m).

N. Install hangers for [ABS] [and] [PVC] piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/2 and NPS 2 (DN 40 and DN 50):  48 inches (1200 mm) with 3/8-inch (10-mm) rod.

2. NPS 3 (DN 80):  48 inches (1200 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 and 5 (DN 100 and 125):  48 inches (1200 mm) with 5/8-inch (16-mm) rod.

4. NPS 6 (DN 150):  48 inches (1200 mm) with 3/4-inch (19-mm) rod.

5. NPS 8 to NPS 12 (DN 200 to DN 300):  48 inches (1200 mm) with 7/8-inch (22-mm) rod.

O. Install supports for vertical [ABS] [and] [PVC] piping every 48 inches (1200 mm).

P. Support piping and tubing not listed above according to MSS SP-69 and manufacturer's written instructions.

3.7 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect soil and waste piping to exterior sanitary sewerage piping.  Use transition fitting to join dissimilar piping materials.

C. Connect drainage and vent piping to the following:

Edit four subparagraphs below to suit Project.

1. Plumbing Fixtures:  Connect drainage piping in sizes indicated, but not smaller than required by plumbing code.

2. Plumbing Fixtures and Equipment:  Connect atmospheric vent piping in sizes indicated, but not smaller than required by authorities having jurisdiction.

3. Plumbing Specialties:  Connect drainage and vent piping in sizes indicated, but not smaller than required by plumbing code.

4. Equipment:  Connect drainage piping as indicated.  Provide shutoff valve, if indicated, and union for each connection.  Use flanges instead of unions for connections NPS 2-1/2 (DN 65) and larger.

D. Connect force-main piping to the following:

1. Sanitary Sewer:  To exterior force main or sanitary manhole.

2. Sewage Pumps:  To sewage pump discharge.

3.8 FIELD QUALITY CONTROL

Portions of testing and inspection requirements in this Article are taken from model plumbing codes.  Edit if requirements vary.

A. During installation, notify authorities having jurisdiction at least 24 hours before inspection must be made.  Perform tests specified below in presence of authorities having jurisdiction.

1. Roughing-in Inspection:  Arrange for inspection of piping before concealing or closing-in after roughing-in and before setting fixtures.

2. Final Inspection:  Arrange for final inspection by authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

B. Reinspection:  If authorities having jurisdiction find that piping will not pass test or inspection, make required corrections and arrange for reinspection.

C. Reports:  Prepare inspection reports and have them signed by authorities having jurisdiction.

D. Test sanitary drainage and vent piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

1. Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired.  If testing is performed in segments, submit separate report for each test, complete with diagram of portion of piping tested.

2. Leave uncovered and unconcealed new, altered, extended, or replaced drainage and vent piping until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

3. Roughing-in Plumbing Test Procedure:  Test drainage and vent piping, except outside leaders, on completion of roughing-in.  Close openings in piping system and fill with water to point of overflow, but not less than 10-foot head of water (30 kPa).  From 15 minutes before inspection starts to completion of inspection, water level must not drop.  Inspect joints for leaks.

4. Finished Plumbing Test Procedure:  After plumbing fixtures have been set and traps filled with water, test connections and prove they are gastight and watertight.  Plug vent-stack openings on roof and building drains where they leave building.  Introduce air into piping system equal to pressure of 1-inch wg (250 Pa).  Use U-tube or manometer inserted in trap of water closet to measure this pressure.  Air pressure must remain constant without introducing additional air throughout period of inspection.  Inspect plumbing fixture connections for gas and water leaks.

5. Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

6. Prepare reports for tests and required corrective action.

E. Test force-main piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

1. Leave uncovered and unconcealed new, altered, extended, or replaced force-main piping until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

2. Cap and subject piping to static-water pressure of 50 psig (345 kPa) above operating pressure, without exceeding pressure rating of piping system materials.  Isolate test source and allow to stand for four hours.  Leaks and loss in test pressure constitute defects that must be repaired.

3. Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

4. Prepare reports for tests and required corrective action.

3.9 CLEANING

A. Clean interior of piping.  Remove dirt and debris as work progresses.

B. Protect drains during remainder of construction period to avoid clogging with dirt and debris and to prevent damage from traffic and construction work.

C. Place plugs in ends of uncompleted piping at end of day and when work stops.

3.10 PROTECTION

Consider using other piping or specify protection by shielding or lightweight insulation if piping surface temperatures are expected to exceed 140 deg F (60 deg C).

A. Exposed [ABS] [and] [PVC] Piping:  Protect plumbing vents exposed to sunlight with two coats of water-based latex paint.

END OF SECTION 221316

SANITARY WASTE AND VENT PIPING
221316 - 1

