Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
12/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224500 - EMERGENCY PLUMBING FIXTURES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following emergency plumbing fixtures:

Revise list below to suit Project.  First seven categories are defined in ANSI Z358.1.  There is also a category for self-contained emergency showers, but none were identified.  Self-contained emergency shower criteria are in ANSI Z358.1, and such a system could be designed, but that is beyond the scope of this Section.

1. Emergency showers.

2. Eyewash equipment.

3. Self-contained eyewash equipment.

4. Personal eyewash equipment.

5. Eye/face wash equipment.

6. Hand-held drench hoses.

7. Combination units.

8. Water-tempering equipment.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Domestic Water Piping Specialties" for backflow preventers.

2. Division 22 Section "Sanitary Waste Piping Specialties" for floor drains.

3. Division 22 Section "Domestic Water Filtration Equipment" for water filters.

1.3 DEFINITIONS

Definitions in this Article are from standards, references, and model plumbing codes.  See Evaluations for a comprehensive list of definitions.

Retain terms that remain after this Section has been edited.

A. Accessible Fixture:  Emergency plumbing fixture that can be approached, entered, and used by people with disabilities.

B. Plumbed Emergency Plumbing Fixture:  Fixture with fixed, potable-water supply.

C. Self-Contained Emergency Plumbing Fixture:  Fixture with flushing-fluid-solution supply.

D. Tepid:  Moderately warm.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include flow rates and capacities, furnished specialties, and accessories.

Retain paragraph below if fixtures include electrical components and wiring.

B. Shop Drawings:  Diagram power, signal, and control wiring.

Retain first paragraph below only if third-party certification is required.

C. Product Certificates:  Submit certificates of performance testing specified in "Source Quality Control" Article.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For emergency plumbing fixtures to include in maintenance manuals.

1.5 QUALITY ASSURANCE

Retain paragraph below for electrical components.

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by testing agency acceptable to authorities having jurisdiction, and marked for intended use.

See Editing Instruction No. 4 in the Evaluations for discussion about ANSI Z358.1.

B. ANSI Standard:  Comply with ANSI Z358.1, "Emergency Eyewash and Shower Equipment."

Retain first paragraph below if fixtures include accessible emergency plumbing fixtures.  There are similar Federal Government standards for accessibility; verify requirements with authorities having jurisdiction.

C. Regulatory Requirements:  Comply with requirements in ICC A117.1, "Accessible and Usable Buildings and Facilities"[; Public Law 90-480, "Architectural Barriers Act" ; and Public Law 101-336, "Americans with Disabilities Act" ;] for plumbing fixtures for people with disabilities.

D. NSF Standard:  Comply with NSF 61, "Drinking Water System Components--Health Effects," for fixture materials that will be in contact with potable water.

1.6 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Flushing-Fluid Solution:  Separate lot and equal to at least [200] <Insert number> percent of amount of solution installed for each self-contained unit.

PART 2 -  PRODUCTS

Part 2 articles specify typical emergency plumbing fixtures and components.  Retain and edit only those articles applicable to Project.  See Editing Instruction No. 3 in the Evaluations for cautions about combinations of fixture components.

2.1 EMERGENCY SHOWERS

Refer to Emergency Shower Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Emergency Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Murdock, Inc.

h. Sellstrom Manufacturing Co.

i. Speakman Company.

j. WaterSaver Faucet Co.

k. Western Emergency Equipment.

l. <Insert manufacturer's name.>

4. Description:  Plumbed, single-shower-head [horizontal, wall-mounting] [vertical, ceiling-mounting] [freestanding] emergency shower.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 20 gpm (76 L/min.) for at least 15 minutes.

b. Supply Piping:  [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] [galvanized steel] [chrome-plated brass or stainless steel] [PVC] with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Pull [rod] [chain].

d. Shower Head:  8-inch (200-mm) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

Emergency shower in paragraph below may require an expanded description.

B. Emergency Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Encon Safety Products.

b. Guardian Equipment Co.

c. Haws Corporation.

d. Speakman Company.

e. Western Emergency Equipment.

f. <Insert manufacturer's name.>

4. Description:  Plumbed, multiple-spray emergency shower with [eight] [12] [16] small shower heads or nozzles.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 20 gpm (76 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1-1/4 (DN 32) minimum [galvanized] [chrome-plated brass or stainless] steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  [Paddle] [Treadle].

Emergency shower in paragraph below requires data for ambient temperature or heating capacity.

C. Emergency Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. B-L-S Industries, Inc.

b. Encon Safety Products.

c. Haws Corporation.

d. Speakman Company.

e. Western Emergency Equipment.

f. <Insert manufacturer's name.>

4. Description:  Plumbed, freeze-protected, freestanding emergency shower.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 20 gpm (76 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1-1/4 (DN 32) galvanized steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Pull [rod] [chain].

d. Shower Head:  8-inch (200-mm) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

e. Heating System:  [120] [240]-V ac electric; and insulation with protective jacket.

2.2 EYEWASH EQUIPMENT

Refer to the Eyewash Equipment Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Murdock, Inc.

h. Sellstrom Manufacturing Co.

i. Speakman Company.

j. WaterSaver Faucet Co.

k. Western Emergency Equipment.

l. <Insert manufacturer's name.>

4. Description:  Plumbed, freestanding eyewash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  [Paddle] [Push bar] [Treadle].

d. Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

e. Drain Piping:  [NPS 1-1/4 (DN 32) minimum, chrome-plated brass, receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2] [Omit drain piping] [Include galvanized-steel indirect connection to drainage system].

B. Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Sellstrom Manufacturing Co.

h. Speakman Company.

i. WaterSaver Faucet Co.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]wall-mounting eyewash equipment with receptor and wall bracket.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

d. Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

e. Drain Piping:  NPS 1-1/4 (DN 32) minimum, chrome-plated brass, receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2.

C. Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. Lab Safety Supply Inc.

f. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]wall-mounting eyewash equipment with wall bracket.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  [Paddle] [Movement sensor].

D. Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Sellstrom Manufacturing Co.

h. WaterSaver Faucet Co.

i. Western Emergency Equipment.

j. <Insert manufacturer's name.>

4. Description:  Plumbed, adjacent-to-sink, swivel, counter-mounting eyewash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

2.3 SELF-CONTAINED EYEWASH EQUIPMENT

Refer to the Self-Contained Eyewash Equipment Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Self-Contained Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. Lab Safety Supply Inc.

f. Sellstrom Manufacturing Co.

g. Speakman Company.

h. WaterSaver Faucet Co.

i. Western Emergency Equipment.

j. <Insert manufacturer's name.>

4. Description:  Portable, pressurized, self-contained eyewash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver flushing fluid at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Tank:  [10 gal. (3.8 L)] <Insert value>, stainless steel, cylindrical, and suitable for on-floor installation.

c. Flushing Fluid:  Medically acceptable solution manufactured and labeled according to applicable regulations.

d. Piping:  Chrome-plated copper alloy or stainless steel with flow regulator and stay-open control valve.

e. Control-Valve Actuator:  Paddle.

f. Spray Heads:  Twin with covers.

B. Self-Contained Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Fendall.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Sellstrom Manufacturing Co.

h. Speakman Company.

i. WaterSaver Faucet Co.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Static, nonpressurized, self-contained eyewash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver flushing fluid at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Tank:  [14 gal. (53 L) minimum] <Insert value>, plastic, and suitable for shelf mounting.

c. Flushing Fluid:  Medically acceptable solution manufactured and labeled according to applicable regulations.

d. Actuator:  Pull-down front panel.

e. Spray Heads:  Protected, twin.

C. Self-Contained Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. Sellstrom Manufacturing Co.

f. Speakman Company.

g. WaterSaver Faucet Co.

h. <Insert manufacturer's name.>

4. Description:  Freeze-protected, static, nonpressurized, self-contained eyewash equipment with heating system.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver flushing fluid at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

b. Tank:  [14 gal. (53 L) minimum] [20 gal. (76 L) minimum] <Insert value>, plastic, and suitable for shelf mounting.

c. Flushing Fluid:  Medically acceptable solution manufactured and labeled according to applicable regulations.

d. Actuator:  Pull-down front panel.

e. Spray Heads:  Protected, twin.

f. Heating System:  Electric, 120-V ac; and insulation with protective jacket.

2.4 PERSONAL EYEWASH EQUIPMENT

Equipment in this Article does not have capacity requirements.  Typical units have 5-gal. (19-L) tank and eyewash or eyewash and drench hose.

Refer to the Personal Eyewash Equipment Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Personal Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Encon Safety Products.

b. Guardian Equipment Co.

c. <Insert manufacturer's name.>

4. Description:  Portable, pressurized, personal eyewash equipment with spray heads.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver flushing fluid[ at rate not less than 0.4 gpm (1.5 L/min.)].

b. Tank:  5 gal. (19 L), stainless steel, cylindrical, and with base suitable for on-floor installation.

c. Flushing Fluid:  Medically acceptable solution manufactured and labeled according to applicable regulations.

d. Piping:  Chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

e. Control-Valve Actuator:  Paddle.

f. Spray Heads:  Twin with covers.

B. Personal Eyewash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Guardian Equipment Co.

c. WaterSaver Faucet Co.

d. <Insert manufacturer's name.>

4. Description:  Portable, pressurized, personal eyewash equipment with spray heads and drench hose.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver flushing fluid[ at rate not less than 0.4 gpm (1.5 L/min.)].

b. Tank:  5 gal. (19 L), stainless steel, cylindrical, and with base suitable for on-floor installation.

c. Flushing Fluid:  Medically acceptable solution manufactured and labeled according to applicable regulations.

d. Piping:  Chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

e. Spray-Head, Control-Valve Actuator:  Paddle.

f. Spray Heads:  Twin with covers.

g. Drench Hose:  Rubber or plastic.

1) Control-Valve Actuator:  Hand-held squeeze valve.

2) Spray Head:  Single with cover.

2.5 EYE/FACE WASH EQUIPMENT

Refer to the Eye/Face Wash Equipment Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Eye/Face Wash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. Lab Safety Supply Inc.

f. Murdock, Inc.

g. Sellstrom Manufacturing Co.

h. Speakman Company.

i. WaterSaver Faucet Co.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Plumbed, freestanding, pedestal eye/face wash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  [Paddle] [Push bar] [Treadle].

d. Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

e. Drain Piping:  NPS 1-1/4 (DN 32) minimum, chrome-plated brass, receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2.[ Include galvanized-steel indirect connection to drainage system.]

B. Eye/Face Wash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Sellstrom Manufacturing Co.

h. Speakman Company.

i. WaterSaver Faucet Co.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]wall-mounting eye/face wash equipment with receptor and wall bracket.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

d. Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

e. Drain Piping:  NPS 1-1/4 (DN 32) minimum, chrome-plated brass, receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2.

C. Eye/Face Wash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. WaterSaver Faucet Co.

f. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]wall-mounting eye/face wash equipment without receptor and with wall bracket.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

D. Eye/Face Wash Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Encon Safety Products.

b. Guardian Equipment Co.

c. WaterSaver Faucet Co.

d. <Insert manufacturer's name.>

4. Description:  Plumbed, adjacent-to-sink, swivel, counter-mounting eye/face wash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

2.6 HAND-HELD DRENCH HOSES

Refer to the Hand-Held Drench Hose Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Hand-Held Drench Hoses, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Speakman Company.

h. WaterSaver Faucet Co.

i. Western Emergency Equipment.

j. <Insert manufacturer's name.>

4. Description:  Plumbed, wall-mounting, hand-held drench hose with wall bracket.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Piping:  NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

c. Control-Valve Actuator:  Paddle.

d. Hose:  [Coiled] [Plain] [Coiled or plain], rubber or plastic.

e. Spray Heads:  [Single] [Twin].

B. Hand-Held Drench Hoses, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Sellstrom Manufacturing Co.

h. Speakman Company.

i. WaterSaver Faucet Co.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Plumbed, counter-mounting, hand-held drench hose.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Capacity:  Deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

b. Supply Fitting:  NPS 1/2 (DN 15) brass with flow regulator.

c. Hose:  Rubber or plastic.

d. Control-Valve Actuator:  Hand-held squeeze valve.

e. Spray Heads:  [Single] [Twin].

2.7 COMBINATION UNITS

Refer to the Combination Unit Table at the end of the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

A. Combination Units, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Chicago Faucets.

c. Encon Safety Products.

d. Guardian Equipment Co.

e. Haws Corporation.

f. Lab Safety Supply Inc.

g. Murdock, Inc.

h. Sellstrom Manufacturing Co.

i. Speakman Company.

j. WaterSaver Faucet Co.

k. Western Emergency Equipment.

l. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]freestanding, with emergency shower and [eyewash] [eye/face wash] [drench hose] equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Piping:  [Galvanized steel] [Chrome-plated brass or stainless steel] [PVC].

1) Unit Supply:  [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)] from [top] [side].

2) Unit Drain:  Outlet at side near bottom.

3) Shower Supply:  NPS 1 (DN 25) with flow regulator and stay-open control valve.

4) [Eyewash] [Eye/Face Wash] [Drench Hose] Supply:  NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

b. Shower Capacity:  Deliver potable water at rate not less than 20 gpm (76 L/min.) for at least 15 minutes.

1) Control-Valve Actuator:  [Pull rod] [Pull chain] [Treadle].

2) Shower Head:  8-inch (200-mm) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

Select and edit one of three subparagraphs and associated subparagraphs below.

c. Eyewash Equipment:  With capacity to deliver potable water at rate not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

1) Control-Valve Actuator:  [Paddle] [Push bar].

2) Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

d. Eye/Face Wash Equipment:  With capacity to deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

1) Control-Valve Actuator:  [Paddle] [Push bar].

2) Receptor:  [Chrome-plated brass or stainless-steel] [Plastic] bowl.

e. Hand-Held Drench Hose:  With capacity to deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

1) Hose:  Rubber or plastic.

2) Control-Valve Actuator:  Hand-held squeeze valve.

3) Spray Head(s):  [Single] [Twin].

B. Combination Units, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. B-L-S Industries, Inc.

b. Encon Safety Products.

c. Guardian Equipment Co.

d. Haws Corporation.

e. Speakman Company.

f. Western Emergency Equipment.

g. <Insert manufacturer's name.>

4. Description:  Plumbed, [accessible, ]freeze-protected, freestanding, with emergency shower and eye/face wash equipment.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in four subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Piping:  Galvanized steel.

1) Unit Supply:  [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)] from [top] [side] [bottom].

2) Shower Supply:  NPS 1 (DN 25) with flow regulator and stay-open control valve.

3) Eye/Face Wash Supply:  NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

System in first subparagraph below requires data for ambient temperature or heating capacity.

b. Heating System:  Electric, [120] [240]-V ac; and insulation with protective jacket.

c. Shower Capacity:  Deliver potable water at rate not less than 20 gpm (76 L/min.) for at least 15 minutes.

1) Control-Valve Actuator:  [Pull rod] [Pull chain] [Treadle].

2) Shower Head:  8-inch (200-mm) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

d. Eye/Face Wash Equipment:  With capacity to deliver potable water at rate not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

1) Control-Valve Actuator:  [Paddle] [Push bar].

2.8 WATER-TEMPERING EQUIPMENT

Use equipment in this Article only for emergency plumbing fixtures without an integral tempered-water system.  Do not use general-use, thermostatic mixing valves or tempering valves.  Edit temperatures to suit Project.  Indicate capacities on Drawings.

A. Water-Tempering Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Bradley Corporation.

c. Encon Safety Products.

d. Haws Corporation.

e. Lawler Manufacturing Co., Inc.

f. Leonard Valve Company.

g. Powers, a Watts Industries Co.

h. Speakman Company.

i. Therm-Omega-Tech, Inc.

j. Western Emergency Equipment.

k. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, hot- and cold-water-tempering equipment with thermostatic mixing valve.

a. Thermostatic Mixing Valve:  Designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, controls, metal piping, and corrosion-resistant enclosure.

B. Water-Tempering Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Encon Safety Products.

b. Therm-Omega-Tech, Inc.

c. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, steam and cold-water, water-tempering equipment with thermostatic mixing valve.

a. Thermostatic Mixing Valve:  Designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, steam controls, heat exchanger, high-temperature-limit and freeze-protection devices, metal piping, and corrosion-resistant enclosure.

C. Water-Tempering Equipment, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Chronomite Laboratories, Inc.

b. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, water-tempering equipment with electric heating.

a. Heating System:  Electric, designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, controls, heating coils, high-temperature-limit device, metal piping, and corrosion-resistant enclosure.

1) Electrical Characteristics:  [208-V ac, 38] [220-V ac, 40] [277-V ac, 32] A, single phase, 60 Hz.

2.9 SOURCE QUALITY CONTROL

Retain and edit this Article if certification is required for some or all emergency plumbing fixtures.  Some manufacturers do not offer third-party certification of compliance with ANSI Z3358.1 for some or all of their fixtures, although those in this Section do comply with ANSI Z358.1 for type, construction, and operation.

A. Certify performance of [plumbed] [and] [self-contained] emergency plumbing fixtures by independent testing agency acceptable to authorities having jurisdiction.

PART 3 -  EXECUTION

3.1 EXAMINATION

Retain this Article for plumbed emergency plumbing fixtures.  Delete option in paragraph below if no direct-connection drain piping is required.

A. Examine roughing-in for water[ and waste] piping systems to verify actual locations of piping connections before plumbed emergency plumbing fixture installation.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 EMERGENCY PLUMBING FIXTURE INSTALLATION

A. Assemble emergency plumbing fixture piping, fittings, control valves, and other components.

B. Install fixtures level and plumb.

C. Fasten fixtures to substrate.

D. Install shutoff valves in water-supply piping to fixtures.  Use ball, gate, or globe valve if specific type valve is not indicated.  Install valves chained or locked in open position if permitted.  Install valves in locations where they can easily be reached for operation.  Valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

Retain one or both exceptions in subparagraphs below if applicable.

1. Exception:  Omit shutoff valve on supply to group of plumbing fixtures that includes emergency plumbing fixture.

2. Exception:  Omit shutoff valve on supply to emergency equipment if prohibited by authorities having jurisdiction.

E. Install shutoff valve and strainer in steam piping and shutoff valve in condensate return piping.

F. Install dielectric fitting in supply piping to fixture if piping and fixture connections are made of different metals.  Dielectric fittings are specified in Division 22 Section "Common Work Results for Plumbing."

G. Install thermometers in supply and outlet piping connections to water-tempering equipment.  Thermometers are specified in Division 22 Section "Meters and Gages for Plumbing Piping."

Retain paragraph below if fixtures have direct connection drain.

H. Install trap and waste to wall on drain outlet of fixture receptors that are indicated to be directly connected to drainage system.

Retain first paragraph below if fixtures have indirect waste connection.

I. Install indirect waste piping to wall on drain outlet of fixture receptors that are indicated to be indirectly connected to drainage system.  Drainage piping is specified in Division 22 Section "Sanitary Waste and Vent Piping."

J. Install escutcheons on piping wall and ceiling penetrations in exposed, finished locations.  Escutcheons are specified in Division 22 Section "Common Work Results for Plumbing."

K. Fill self-contained fixtures with flushing fluid.

L. Install equipment nameplates or equipment markers on fixtures and equipment signs on water-tempering equipment.  Identification materials are specified in Division 22 Section "Identification for Plumbing Piping and Equipment."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Retain six paragraphs below if required.

B. Connect cold-water-supply piping to plumbed emergency plumbing fixtures not having water-tempering equipment.

C. Connect hot- and cold-water-supply piping to hot- and cold-water-tempering equipment.  Connect output from water-tempering equipment to emergency plumbing fixtures.

D. Connect cold-water and steam supply and condensate return piping to steam and cold-water-tempering equipment.  Connect output from water-tempering equipment to emergency plumbing fixtures.

E. Connect cold water and electrical power to electric heating water-tempering equipment.

F. Directly connect emergency plumbing fixture receptors with trapped drain outlet to sanitary drainage and vent piping.

G. Indirectly connect emergency plumbing fixture receptors without trapped drain outlet to sanitary or storm drainage piping.

Retain both paragraphs below for electrical components.

H. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Mechanical-Component Testing:  After plumbing connections have been made, test for compliance with requirements.  Verify ability to achieve indicated capacities and temperatures.

Retain first paragraph and subparagraph below for electrical components.

B. Electrical-Component Testing:  After electrical circuitry has been energized, test for compliance with requirements.

1. Test and adjust controls and safeties.

C. Repair or replace malfunctioning units.  Retest as specified above after repairs or replacements are made.

D. Report test results in writing.

3.5 ADJUSTING

A. Adjust or replace fixture flow regulators for proper flow.

B. Adjust equipment temperature settings.

END OF SECTION 224500

	EMERGENCY PLUMBING FIXTURES
	224500 - 1



