Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233119 - HVAC CASINGS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. [Factory] [Shop]-fabricated, field-assembled, [single] [double] [single- and double]-wall casings for HVAC equipment.

1.3 PERFORMANCE REQUIREMENTS

Retain first paragraph below if static-pressure classes are not indicated on Drawings.

A. Static-Pressure Classes:

1. Upstream from Fan(s):  [2-inch wg (500 Pa)] <Insert value>.

2. Downstream from Fan(s):  [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] [6-inch wg (1500 Pa)] [10-inch wg (2500 Pa)] <Insert value>.

For critical applications, a table of performance by octave bands should be indicated on Drawings.

B. Acoustical Performance:

1. NRC:  [1.09] [0.94] <Insert number> according to ASTM C 423.

2. STC:  [40] [34] <Insert number> according to ASTM E 90.

C. Structural Performance:

1. Casings shall be fabricated to withstand 133 percent of the indicated static pressure without structural failure.  Wall and roof deflection at the indicated static pressure shall not exceed 1/8 inch per foot (0.97 mm per meter) of width.

a. Fabricate outdoor casings to withstand wind load of 15 lbf/sq. ft. (720 N/sq. m) and snow load of 30 lbf/sq. ft. (1440 N/sq. m).

Retain paragraph below with "Seismic-restraint devices" Subparagraph in "Submittals" Article for projects requiring seismic design.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

D. Seismic Performance:  HVAC casings shall withstand the effects of earthquake motions determined according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" [and] [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of the following products:

1. Factory-fabricated casings.

2. Liners and adhesives.

3. Sealants and gaskets.

4. Seismic-restraint devices.

B. LEED Submittals:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that duct systems comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

2. Product Data for Prerequisite EA 2:  Documentation indicating that duct systems comply with ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

3. Leakage Test Report for Prerequisite EA 2:  Documentation of work performed for compliance with ASHRAE/IESNA 90.1-2004, Section 6.4.4.2.2 - "Duct Leakage Tests."

4. Duct-Cleaning Test Report for Prerequisite EQ 1:  Documentation of work performed for compliance with ASHRAE 62.1-2004, Section 7.2.4 - "Ventilation System Start-Up."

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesives and sealants.

5. Product Data for Credit EQ 4.1:  For adhesives and sealants, including printed statement of VOC content.

C. Shop Drawings:  For HVAC casings.  Include plans, elevations, sections, components, and attachments to other work.

1. Detail HVAC casing assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Sheet metal thickness(es).

3. Reinforcement and spacing.

4. Seam and joint construction.

5. Access doors including frames, hinges, and latches.

6. Filter, coil, humidifier, and other apparatus being installed in and mounted on casing.

7. Locations for access to internal components.

8. Hangers and supports including methods for building attachment, vibration isolation,[ seismic restraints,] and casing attachment.

9. Interior lighting, including switches.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

D. Welding certificates.

Retain first paragraph below for product certificates from manufacturers.

E. Product Certificates:  For acoustically critical casings, from manufacturer.

1. Show sound-absorption coefficients in each octave band lower than those scheduled when tested according to ASTM C 423.

2. Show airborne sound transmission losses lower than those scheduled when tested according to ASTM E 90.

F. Field quality-control reports.

1.5 QUALITY ASSURANCE

Retain one of first two paragraphs below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.  Retain first paragraph if only one AWS standard is applicable.  Retain second paragraph if more than one AWS standard is referenced.

A. Welding Qualifications:  Qualify procedures and personnel according to [AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports] [AWS D9.1M/D9.1, "Sheet Metal Welding Code," for casing joint and seam welding].

B. Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

2. AWS D9.1M/D9.1, "Sheet Metal Welding Code," for casing joint and seam welding.

Retain two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.

C. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-Up."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

1.6 COORDINATION

A. Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

Retain one of two paragraphs below to specify steel supports.

B. Coordinate sizes and locations of steel supports.  Supports are specified in Division 05 Section "Metal Fabrications."

C. Coordinate installation of roof curbs, [equipment supports, ]and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

PART 2 -  PRODUCTS

2.1 GENERAL CASING FABRICATION REQUIREMENTS

A. General Material Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 6, "Equipment and Casings," for acceptable materials, material thicknesses, and casing construction methods unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

1. Fabricate casings with more than 3-inch wg (750-Pa) negative static pressure according to SMACNA's "Rectangular Industrial Duct Construction Standards."

2. Casings with more than 2-inch wg (500-Pa) positive static pressure may be fabricated according to SMACNA's "Rectangular Industrial Duct Construction Standards."

B. Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

1. Exterior Surface Galvanized Coating Designation:  [G60 (Z180)] [G90 (Z275)].

2. Interior Surface Galvanized Coating Designation:

a. Sections Not Exposed to Moisture:  [G60 (Z180)] [G90 (Z275)].

b. Sections Housing and Downstream from Cooling Coil and Humidifiers:  [G90 (Z275)].

C. Stainless Steel:  ASTM A 480/A 480M, [Type 304] [Type 316], and having a[ No. 2D] <Insert finish> finish.

Antimicrobial coating in first paragraph below is an optional feature and usually applied only after casing fabrication.  See Evaluations for discussion on coatings.

D. Factory- or Shop-Applied Antimicrobial Coating:

1. Apply to the interior sheet metal surfaces of casing in contact with the airstream.  Apply untreated clear coating to the exterior surface.

2. Antimicrobial compound shall be tested for efficacy by an NRTL and registered by the EPA for use in HVAC systems.

3. Coating containing the antimicrobial compound shall have a hardness of 2H minimum when tested according to ASTM D 3363.

4. Surface-Burning Characteristics:  Maximum flame-spread index of 25 and maximum smoke-developed index of 50 according to UL 723; certified by an NRTL.

5. Applied Coating Color:  [Standard] [Black] [White].

E. Reinforcement Shapes and Plates:  ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

Retain first paragraph below if seal class or leakage class is not indicated on Drawings.

F. Sealing Requirement:  SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Seal Class A.  Seal all seams, joints, connections, and abutments to building.

G. Penetrations:  Seal all penetrations airtight.  Cover with escutcheons and gaskets, or fill with suitable compound so there is no exposed insulation.  Provide shaft seals where fan shafts penetrate casing.

H. Access Doors:  Fabricate access doors according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 6-11, "Casing Access Doors - 2-inch wg (500 Pa)," and Figure 6.12, "Casing Access Doors - 3-10-inch wg (750-2500 Pa)"; and according to pressure class of the plenum or casing section in which access doors are to be installed.

1. Size:  [20 by 54 inches (500 by 1370 mm)] <Insert size>.

2. Vision Panel:  Double-glazed, wire-reinforced safety glass with an airspace between panes and sealed with interior and exterior rubber seals.

3. Hinges:  Piano or butt hinges and latches, number and size according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

4. Latches:  Minimum of two wedge-lever-type latches, operable from inside and outside.

5. Neoprene gaskets around entire perimeters of door frames.

6. Doors shall open against air pressure.

I. Condensate Drain Pans:  Formed sections of [Type 304, stainless-steel sheet] [G90 (Z275) coated, galvanized sheet steel] complying with requirements in ASHRAE 62.1.  Pans shall extend a minimum of 12 inches (300 mm) past coil.

1. Double-wall construction shall have space between walls filled with foam insulation and sealed moisture tight.

2. Intermediate drain pan or drain trough shall collect condensate from top coil for units with stacked coils or stacked eliminators.

3. Insulation:  Polystyrene or polyurethane.

4. Slopes shall be in a minimum of two planes to collect condensate from cooling coils (including coil piping connections and return bends), eliminators, and humidifiers when units are operating at maximum catalogued face velocity across cooling coil.

Retain option in subparagraph below for units with draw-through fan configurations.

5. Each drain pan connection shall have a trap.[ Drain traps with depth and height differential between inlet and outlet equal or greater to the design static pressure plus 2-inch wg (500 Pa).] Include slab height in trap calculation.

2.2 SHOP-FABRICATED CASINGS

A. Single- and Double-Wall Casings:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for sheet metal thickness based on indicated static-pressure class unless otherwise indicated.

Retain one of first two paragraphs below.

B. Double-Wall Casing Inner Panel:  Perforated, galvanized sheet steel having 3/32-inch- (2.4-mm-) diameter perforations, with overall open area of [23] <Insert number> percent.  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for sheet metal thickness based on indicated static-pressure class unless otherwise indicated.

C. Double-Wall Casing Inner Panel:  Solid sheet steel.  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for sheet metal thickness based on indicated static-pressure class unless otherwise indicated.

Retain one of first three paragraphs below.  If the objective of interstitial insulation includes achievement of both thermal performance and sound absorption, then casings may need additional external insulation to achieve thermal portion of the objective.  See Division 23 Section "HVAC Insulation" for applicable duct or equipment insulation and installation requirements for external casing application.

D. Interstitial Insulation:  Polyurethane foam complying with NFPA 90A or NFPA 90B.

E. Interstitial Insulation:  Fibrous-glass liner complying with ASTM C 1071, NFPA 90A, or NFPA 90B; and with NAIMA AH124, "Fibrous Glass Duct Liner Standard."

Retain first subparagraph below to require thermal conductivity exceeding requirements in ASTM C 1071.  LEED Prerequisite EA 2 requires minimum thermal-resistance values for casing insulation.  Retaining subparagraph may create a restrictive proprietary specification.  If retaining, verify availability of performance with manufacturers.

1. Maximum Thermal Conductivity:  [0.27 Btu x in./h x sq. ft. x deg F (0.039 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

2. Coat insulation with antimicrobial coating.

3. Cover insulation with polyester film complying with UL 181, Class 1.

F. Interstitial Insulation:  Flexible-elastomeric duct liner complying with ASTM C 534, Type II for sheet materials and with NFPA 90A or NFPA 90B.

Retain subparagraph below to require thermal conductivity exceeding requirements in ASTM C 1071.  LEED Prerequisite EA 2 requires minimum thermal-resistance values for casing insulation.  Retaining subparagraph may create a restrictive proprietary specification.  If retaining, verify availability of performance with manufacturers.

1. Maximum Thermal Conductivity:  [0.25 Btu x in./h x sq. ft. x deg F (0.034 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

G. Fabricate casings with standing seams and angle-iron reinforcements unless otherwise indicated.

H. Fabricate close-off sheets from casing to dampers, filter frames, and coils and between stacked coils.  Use galvanized sheet steel of same thickness as casing and with a galvanized coating designation of G90 (Z275).

I. Bolt close-off sheets to frame flanges and housings.  Support coils on stands fabricated from galvanized-steel angles or channels.

J. Reinforce casings with galvanized-steel angles.

2.3 MANUFACTURED CASINGS

First paragraph below is an example of one type of factory-fabricated casing.

A. Description:  Double-wall, insulated, pressurized equipment casing.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Acoustical Surfaces, Inc.

2. AeroSonics, Inc.; a division of TUTCO, Inc.

3. Buffalo Air Handling.

4. CertainTeed Corp.; Insulation Group.

5. CLEANPAK International.

6. D&D Sound Control.

7. IACL.

8. Industrial Noise Control, Inc.

9. McGill AirSilence LLC.

10. SEMCO Incorporated.

11. Vibro-Acoustics.

12. <Insert manufacturer's name>.

C. Double-Wall Panel Fabrication:  Solid, galvanized sheet steel exterior wall and [solid] [perforated], galvanized sheet steel interior wall; with space between wall filled with insulation.

2-inch- (50-mm-) thick walls are usually standard.

1. Wall Thickness:  [2 inches (50 mm)] [4 inches (100 mm)].

2. Fabricate with a minimum number of joints.

3. Weld exterior and interior walls to perimeter; to interior, longitudinal, galvanized-steel channels; and to box-end internal closures.  Paint welds.

Retain one of first two subparagraphs below.

4. Sheet metal thickness shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for static-pressure class indicated for casing.

5. Sheet Metal Thicknesses:

a. Exterior Wall Thickness:  [0.040 inch (1.0 mm)] <Insert dimension> minimum.

b. Interior Wall Thickness:  [0.034 inch (0.85 mm)] <Insert dimension> minimum.

Retain one of first two subparagraphs below.

6. Double-Wall Casing Inner Panel:  Perforated, galvanized sheet steel having 3/32-inch- (2.4-mm-) diameter perforations, with overall open area of [23] <Insert number> percent.

7. Double-Wall Casing Inner Panel:  Solid sheet steel.

8. Fill each panel assembly with insulating material that is noncombustible, inert, mildew resistant and vermin proof and that complies with NFPA 90A.

9. Fabricate panels with continuous [tongue-and-groove] [self-locking] [tongue-and-groove or self-locking] joints effective inside and outside each panel.

D. Trim Items:  Fabricate from a minimum of 0.052-inch (1.3-mm) galvanized sheet steel, furnished in standard lengths for field cutting.

2.4 CASING LINER

If the objective of casing liner includes achievement of both thermal performance and sound absorption, then casings may need additional external insulation to achieve thermal portion of the objective.  LEED Prerequisite EA 2 requires minimum thermal-resistance values for air distribution systems.  See Division 23 Section "HVAC Insulation" for applicable duct insulation and installation requirements for external casing application.

When specifying liner by referencing ASTM C 1071, specifiers are assured of products meeting stated qualifications for corrosiveness, water-vapor sorption, fungi resistance, temperature resistance, erosion resistance, odor emission, surface-burning characteristics, apparent thermal conductivity, sound absorption coefficients, and bacteria resistance.

A. Fibrous-Glass Liner:  Comply with ASTM C 1071, NFPA 90A, or NFPA 90B and with NAIMA AH124, "Fibrous Glass Duct Liner Standard."

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. CertainTeed Corp.; Insulation Group.

b. Johns Manville.

c. Knauf Insulation.

d. Owens Corning.

e. <Insert manufacturer's name>.

Retain first subparagraph below to require thermal conductivity exceeding minimum requirements in ASTM C 1071.  Retaining subparagraph may create a restrictive proprietary specification.

2. Maximum Thermal Conductivity:

Option for thermal conductivity in first two subparagraphs below exceeds the values in ASTM C 1071.  If retaining, verify availability of performance with casing liner manufacturers.

a. Type I, Flexible:  [0.27 Btu x in./h x sq. ft. x deg F (0.039 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

b. Type II, Rigid:  [0.23 Btu x in./h x sq. ft. x deg F (0.033 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

Antimicrobial coating in first subparagraph below is an optional feature for casing liner.

3. Antimicrobial Erosion-Resistant Coating:  Apply to surface of the liner that will form the interior surface of casing to act as a moisture repellent and an erosion-resistant coating.  Antimicrobial compound shall be tested for efficacy by an NRTL and registered by the EPA for use in HVAC systems.

4. [Solvent] [Water]-Based Liner Adhesive:  Comply with NFPA 90A or NFPA 90B and with ASTM C 916.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Flexible-elastomeric casing liner in first paragraph below is not suitable for temperatures higher than 220 deg F (104 deg C).

B. Flexible-Elastomeric Casing Liner:  Preformed, cellular, closed-cell, sheet materials complying with ASTM C 534, Type II, Grade 1, and with NFPA 90A or NFPA 90B.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Aeroflex USA Inc.

b. Armacell LLC.

c. Rubatex International, LLC.

d. <Insert manufacturer's name>.

Available thicknesses are 3/8, 1/2, 3/4, and 1 inch (9.5, 13, 19, and 25 mm).  Indicate thickness on Drawings.

Surface-burning characteristics in first subparagraph below are available in limited thicknesses.  Verify maximum thickness with manufacturers.

2. Surface-Burning Characteristics:  Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

3. Liner Adhesive:  As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

C. Natural-Fiber Casing Liner:  85 percent cotton, 10 percent borate, and 5 percent polybinding fibers, treated with a microbial growth inhibitor, and complying with NFPA 90A or NFPA 90B.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Bonded Logic, Inc.

b. Reflectix Inc.

c. <Insert manufacturer's name>.

Available thicknesses are 1/2 and 1 inch (13 and 25 mm).  Indicate thickness on Drawings.

2. Maximum Thermal Conductivity:  [0.24 Btu x in./h x sq. ft. x deg F (0.034 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature when tested according to ASTM C 518.

3. Surface-Burning Characteristics:  Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

4. Liner Adhesive:  As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Insulation Pins and Washers:

1. Cupped-Head, Capacitor-Discharge-Weld Pins:  Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

2. Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm-) thick, [galvanized] [stainless] steel, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

E. Shop or Factory Application of Casing Liner:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-19, "Flexible Duct Liner Installation."

1. Adhere a single layer of indicated thickness of casing liner with at least 90 percent adhesive coverage at liner contact surface area.  Attaining indicated thickness with multiple layers of casing liner is prohibited.

2. Apply adhesive to transverse edges of liner facing upstream that do not receive metal nosing.

3. Butt transverse joints without gaps, and coat joint with adhesive.

4. Fold and compress liner in corners of casings or cut and fit to ensure butted-edge overlapping.

Retain first subparagraph below if air velocities are 2500 fpm (12.7 m/s) or higher.

5. Apply adhesive coating on longitudinal seams in casings with air velocity of 2500 fpm (12.7 m/s).

Securing method in first subparagraph below is for casings with air velocities of 2500 fpm (12.7 m/s) and lower.  Use caution when designing lined casings with air velocities higher than 2500 fpm (12.7 m/s).  See SMACNA for requirements.

6. Secure liner with mechanical fasteners 4 inches (100 mm) from corners and at intervals not exceeding 12 inches (300 mm) transversely; at 3 inches (75 mm) from transverse joints and at intervals not exceeding 18 inches (450 mm) longitudinally.

7. Secure transversely oriented liner edges facing the airstream with metal nosings that have either channel or "Z" profiles or are integrally formed from casing wall.  Fabricate edge facings at the following locations:

a. Fan discharges.

b. Intervals of lined casing preceding unlined duct.

c. Upstream edges of transverse joints in casings where air velocities are higher than 2500 fpm (12.7 m/s) or where indicated.

Retain subparagraph below if casings with air velocities higher than 4000 fpm (20.3 m/s) are anticipated; indicate locations of double-wall casings on Drawings.

8. Secure insulation between perforated sheet metal inner wall of same thickness as specified for outer wall.  Use mechanical fasteners that maintain inner wall at uniform distance from outer wall without compressing insulation.

2.5 SEALANT MATERIALS

See SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for a discussion on seam and joint sealing methods and their applications.  Retain one or more of first three paragraphs below, and identify which sealing system applies to which HVAC casings on Drawings.

A. General Sealant and Gasket Requirements:  Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

B. Water-Based Joint and Seam Sealant:

1. Application Method:  Brush on.

2. Solids Content:  Minimum 65 percent.

3. Shore A Hardness:  Minimum 20.

4. Water resistant.

5. Mold and mildew resistant.

Retain one of first two subparagraphs below.  Retain second subparagraph if low-emitting materials are required for LEED-NC Credit EQ 4.1.

6. VOC:  Maximum 75 g/L (less water).

7. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

8. Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive or negative.

9. Service:  Indoor or outdoor.

10. Substrate:  Compatible with galvanized sheet steel or stainless steel.

If retaining first paragraph below, verify acceptability with authorities having jurisdiction.

C. Solvent-Based Joint and Seam Sealant:

1. Application Method:  Brush on.

2. Base:  Synthetic rubber resin.

3. Solvent:  Toluene and heptane.

4. Solids Content:  Minimum 60 percent.

5. Shore A Hardness:  Minimum 60.

6. Water resistant.

7. Mold and mildew resistant.

Retain one of first two subparagraphs below.  Retain second subparagraph if low-emitting materials are required for LEED-NC Credit EQ 4.1.

8. VOC:  Maximum 395 g/L.

9. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

10. Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive or negative.

11. Service:  Indoor or outdoor.

12. Substrate:  Compatible with galvanized sheet steel or stainless steel.

D. Flanged Joint Sealant:  Comply with ASTM C 920.

1. General:  Single component, acid curing, silicone, elastomeric.

2. Type:  S.

3. Grade:  NS.

4. Class:  25.

5. Use:  O.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

6. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

E. Flange Gaskets:  Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine [concrete bases] [roof curbs] [and] [steel supports] for compliance with requirements for conditions affecting installation and performance of HVAC casings.

B. Examine casing insulation materials and liners before installation.  Reject casings that are wet, moisture damaged, or mold damaged.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install casings according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

B. Equipment Mounting:  Install HVAC casings on concrete base.  Comply with requirements for concrete base specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported casings, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below if casings are required to withstand seismic design loads.

C. Install seismic restraints on casings.  Comply with requirements for seismic-restraint devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Apply sealant to joints, connections, and mountings.

E. Field-cut openings for pipe and conduit penetrations; insulate and seal according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

F. Support casings on floor or foundation system.  Secure and seal to base.

G. Support components rigidly with ties, braces, brackets, [seismic restraints, ]and anchors of types that will maintain housing shape and prevent buckling.

H. Align casings accurately at connections, with 1/8-inch (3-mm) misalignment tolerance and with smooth interior surfaces.

3.3 FIELD QUALITY CONTROL

A. Tests and Inspections:

1. Perform field tests and inspections according to SMACNA's "HVAC Air Duct Leakage Test Manual."

2. Test the following systems:

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.2 - "Duct Leakage Tests" requires leak testing of at least 25 percent of total installed duct area with a pressure class in excess of 3-inch wg (750 Pa).  If applying for LEED certification or complying with ASHRAE/IESNA 90.1-2004, retain first subparagraph below to define minimum requirements.  Retain second subparagraph to define more stringent requirements.

a. Systems required by ASHRAE/IESNA 90.1-2004.

b. Supply Air:  [100] [50] <Insert value> percent of total installed duct area with a pressure class of [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value> or higher.

c. <Insert requirements of other systems>.

3. Conduct tests at static pressures equal to maximum design pressure of system or section being tested.  If pressure classes are not indicated, test entire system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.  Give seven days' advance notice for testing.

4. Determine leakage from entire system or section of system by relating leakage to surface area of test section.  Comply with requirements for leakage classification of ducts connected to casings.

5. Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

B. HVAC casings will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

3.4 CLEANING

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

A. Comply with in Division 23 Section "Metal Ducts."

END OF SECTION 233119

	HVAC CASINGS
	233119 - 1



