Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
06/03 (R 06/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238223 - UNIT VENTILATORS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include unit ventilators may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes unit ventilators and accessories with the following heating and cooling features:

Some manufacturers can provide both heating and reheat coils in same unit; however for most applications, retain heating or reheat coil.

1. [Hydronic] [Steam] [Electric] heating coil.

2. [Hydronic] [Steam] [Electric] reheat coil.

3. [Hydronic] [Direct-expansion refrigerant] cooling coil.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 23 Section "Water-Source Unitary Heat Pumps" for ground-loop, water-source heat-pump-type unit ventilators.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. BAS:  Building automation system.

B. HGBP:  Hot-gas bypass.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, and furnished specialties and accessories for each unit type and configuration.

B. LEED Submittals:

Retain first subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Plans, elevations, sections, and details.

2. Details of anchorages and attachments to structure and to supported equipment.

3. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below for ceiling-mounted unit ventilators.

1. Ceiling suspension components.

2. Method of attaching hangers to building structure.

3. Size and location of initial access modules for acoustical tile.

4. Size and location of access panels in hard ceilings to provide access to concealed units.

5. Items penetrating finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. <Insert item.>

6. Perimeter moldings.

E. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain paragraph below with or without above.

F. Samples for Verification:  For each type of unit ventilator[ and auxiliary shelves] and cabinets indicated.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

G. Manufacturer Seismic Qualification Certification:  Submit certification that unit ventilators, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

H. Field quality-control test reports.

I. Operation and Maintenance Data:  For unit ventilators to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

1. Maintenance schedules and repair part lists for motors, coils, integral controls, and filters.

J. Warranty:  Special warranty specified in this Section.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

C. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.6 COORDINATION

Delete this Article if unit ventilators are wall or floor mounted.

Edit first paragraph below to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of unit ventilators and suspension system components with other construction that penetrates or is supported by ceilings, including light fixtures, HVAC equipment, fire-suppression-system components, and partition assemblies.

B. Coordinate size and location of wall sleeves for outdoor-air intake and relief dampers.

1.7 WARRANTY

Delete this Article if remote or integral condensing unit is not required.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

Warranties vary among manufacturers from covering the whole unit for up to 4 years, to only the compressor for 5 to 10 years, or only the condenser coil for 5 years.  Extended special warranties are limited to units in the 1- to 5-ton (3.5- to 17.6-kW) range, and then are usually restricted to residential applications.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of condensing units that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Compressor failure.

b. Condenser coil leak.

Verify available warranties and insert number in subparagraphs below.

2. Warranty Period:  [Four] [Five] [10] <Insert number> years from date of Substantial Completion.

3. Warranty Period (Compressor Only):  [Five] [10] <Insert number> years from date of Substantial Completion.

4. Warranty Period (Condenser Coil Only):  [Five] <Insert number> years from date of Substantial Completion.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Unit Ventilator Filters:  Furnish <Insert number> spare filter(s) for each filter installed.

Retain subparagraph below only for integral cooling chassis unit ventilators.

2. Spare Cooling Chassis:  Furnish <Insert number> spare integral cooling chassis for each size unit installed.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Retain one of three paragraphs below.  See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Basis-of-Design Product:  The design for unit ventilators is based on <Insert manufacturer's name and product>.  Subject to compliance with requirements, provide the named product or a comparable product by one of the following:

B. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

C. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain list of manufacturers below with any of three paragraphs above.

1. Carrier Corporation.

2. Engineered Air Ltd.

3. McQuay International.

4. Nesbitt Aire, Inc.; PEF Industries, Inc.

5. Trane.

6. <Insert manufacturer's name.>

Many additional features are available for this product.  Some are mutually exclusive.  Include all features for unit ventilators that are required for Project, and identify additional features for specific units in a Unit Ventilator Schedule on the Drawings.

2.2 MANUFACTURED UNITS

A. Description:  Factory-packaged and -tested units rated according to ARI 840, ASHRAE 33, and UL 1995, including finished cabinet, filter, cooling coil, drain pan, supply-air fan and motor in [blow-] [or] [draw-]through configuration, and hydronic cooling coil.

2.3 CABINETS

Closed-cell insulation with foil or matt facing is provided by some manufacturers to reduce the possibility of fibers from glass-fiber insulation being introduced into the conditioned space.

A. Insulation:  Minimum [1/2-inch (13-mm)] [1-inch (25-mm)] <Insert thickness> thick, [coated glass fiber] [foil-covered, closed-cell foam] [matte-finish, closed-cell foam] complying with ASTM C 1071 and attached with adhesive complying with ASTM C 916.

1. Fire-Hazard Classification:  Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

2. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

B. LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.  Removable drain pans in first paragraph below are an extra feature with some manufacturers.Drain Pans:  [Plastic] [Insulated galvanized steel with plastic liner], formed as required by ASHRAE 62.1-2004.[  Drain pan shall be removable.]

C. Cabinet Frame and Access Panels:  Welded-steel frame with removable panels fastened with hex-head tamperproof fasteners[ and key-operated control and valve access doors].

1. Steel components exposed to moisture shall be hot-dip galvanized after fabrication.

D. Cabinet Finish:  Baked-on primer ready for field painting.

Retain paragraph above or first paragraph below to suit Project.  Coordinate custom-color requirements with sample submittal requirements.  Coordinate field painting with Division 09 painting Sections.

E. Cabinet Finish:  Baked enamel, in manufacturer's [standard] [custom] paint color as selected by Architect.

F. Indoor-Supply-Air Grille:  [Steel] [Aluminum], [double deflection, adjustable] [adjustable linear bar].

Note limitations of configurations when selecting an option in paragraph below.

G. Return-Air Inlet:  [Front toe space] [Back inlet with top inlet grille].

Retain first paragraph below if unit ventilators are freestanding.

H. End Panels:  Matching material and finish of unit ventilator.

I. Outdoor-Air Wall Box:  Minimum 0.1265-inch- (3.2-mm-) thick, aluminum, rain-resistant louver and box with integral eliminators and bird screen.

1. Louver Configuration:  [Horizontal] [Vertical] rain-resistant louver.

2. Louver Material:  [Aluminum] [Steel].

3. Bird Screen:  1/2-inch (13-mm) mesh screen on interior side of louver.

4. Decorative Grille:  On outside of intake.

5. Finish:  [Anodized aluminum] [Baked enamel], color as selected by Architect from manufacturer's [standard] [custom] colors.

2.4 COILS

A. Test and rate unit ventilator coils according to ASHRAE 33.

B. Hydronic Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), rated for a minimum working pressure of 200 psig (1378 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C).  Include manual air vent and drain valve.

C. Steam Coils:  Copper[ distributing] tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), rated for a minimum working pressure of 75 psig (517 kPa).

Some manufacturers limit air-to-air heat pumps to electric supplemental heating coils.

D. Electric-Resistance Heating Coils:  Nickel-chromium heating wire or tubular elements in coil fins, free of expansion noise and hum, with fuses in terminal box for overcurrent protection, and continuous limit controls for high-temperature protection.  Terminate elements in stainless-steel machine-staked terminals secured with stainless-steel hardware.

Retain paragraph below for integral or remote condensing units.

E. Indoor Refrigerant Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), and brazed joints at fittings.  Comply with ARI 210/240, and leak test to minimum 450 psig (3105 kPa) for a minimum 300-psig (2070-kPa) working pressure.  Include thermal expansion valve.

2.5 INDOOR FAN

A. Fan and Motor Board:  Removable.

1. Fan:  Forward curved, double width, centrifugal; directly connected to motor.  Thermoplastic or painted-steel wheels; and aluminum, painted-steel, or galvanized-steel fan scrolls.

2. Fan Shaft and Bearings:  Hollow steel shaft with permanently lubricated, resiliently mounted bearings.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.  Permanently lubricated ball bearings are available for motors up through 5 hp.

3. Motor:  Permanently lubricated, multispeed, resiliently mounted on motor board.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

4. Wiring Termination:  Connect motor to chassis wiring with plug connection.

2.6 DAMPERS

A. Mixing Dampers:  Galvanized-steel blades with edge and end seals and nylon bearings; with [electric] [pneumatic] actuator.

B. Outdoor-Air Dampers:  Galvanized-steel blades with edge and end seals and nylon bearings; with [electric] [pneumatic] actuator.

Face and bypass dampers in paragraph below are optional.

C. Face and Bypass Dampers:  Galvanized-steel damper blades with edge and end seals and nylon bearings; with factory-mounted [electric] [pneumatic] actuator.

Retain paragraph below to comply with LEED-NC Prerequisite EA 2.

D. Comply with ASHRAE/IESNA 90.1-2004.

2.7 ACCESSORIES

Verify availability of additional features for unit ventilators specified.

A. Exhaust Shutter:  [Barometric] [Motorized, modulating] type designed to limit room pressure to maximum 0.10-inch wg (25 kPa) with [steel] [aluminum] [fabric] damper blades including edge and end seals, in galvanized-steel frame with [outdoor] [and] [interior] wall grille.

B. Subbase:  Sheet metal floor-mounting base with leveling screws and black enamel finish.

C. Insulated false back with gasket seals on wall and outdoor-air plenum.

1. Insulation:  Minimum [1/2-inch (13-mm)] [1-inch (25-mm)] <Insert thickness> thick, [coated glass fiber] [foil-covered, closed-cell foam] [matte-finish, closed-cell foam] complying with ASTM C 1071 and attached with adhesive complying with ASTM C 916.

a. Fire-Hazard Classification:  Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

b. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Return-air plenum, 6 inches (150 mm) thick, designed to take return air from top inlet grilles in cabinets on both sides of unit ventilator with gasket seals on wall and outdoor-air plenum extension.

Retain first paragraph below for concealed unit ventilators.

E. Duct flanges for supply-, return-, and outdoor-air connections.

F. Radiation Grille:  [Steel] [Aluminum], [linear-bar] [stamped] grille with finish to match discharge-air grille.

Verify available filters with unit ventilator manufacturer.

G. Filters:  Minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one of three subparagraphs below.  Retain third subparagraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

1. Washable Foam:  70 percent arrestance and 3 MERV.

2. Glass Fiber Treated with Adhesive:  80 percent arrestance and 5 MERV.

3. Pleated Cotton-Polyester Media:  90 percent arrestance and 7 MERV.

H. Energy Recovery Wheel:

1. Casing:  Steel with manufacturer's standard paint coating and with the following:

a. Integral purge section.

b. Casing seals on periphery of rotor, on duct divider, and on purge section.

c. Support rotor on grease-lubricated ball bearings with extended grease fittings.  Mount horizontal wheels on tapered roller bearing.

2. Rotor:  Corrugated-aluminum, segmented wheel strengthened with radial spokes, and having nontoxic, noncorrosive silica-gel desiccant coating.  Construct media for passing maximum 800-micrometer solids and maximum 0.04 percent cross contamination by volume of exhaust air.  Drive rotor with belt around outside of rotor.

3. Defrost Coils:  Electric defrost coil in the exhaust airstream.

4. Drive:  Fractional horsepower motor and gear reducer, with speed changed by adjustable variable frequency controller.

5. Inlet and Discharge Fans:  Forward curved, centrifugal; resiliently mounted with flexible duct connections.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert additional subparagraphs below to suit Project.

a. Motor and Drive:  Permanently lubricated, direct driven.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

6. Filters:  1-inch- (25-mm-) thick, disposable type, mounted in galvanized-steel frame upstream of energy recovery wheel in both supply and exhaust airstreams.

7. Electrical:  Single electrical connection from attached unit ventilator.

2.8 FACTORY HYDRONIC PIPING PACKAGE

A. Piping:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper tube with wrought-copper fittings and brazed joints.  Label piping to indicate service, inlet, and outlet.  Crossover piping, [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] <Insert size> with shutoff valves.

B. Control Valves:  [Electric] [Pneumatic] actuators compatible with terminal controller and building controls.

Retain one or more of four subparagraphs below.

1. [Two] [Three]-way, [two-position] [modulating] control valve for dual-temperature-water coil.

2. [Two] [Three]-way, [two-position] [modulating] control valve for chilled-water coil.

3. [Two] [Three]-way, [two-position] [modulating] control valve for hot-water heating coil.

4. [Two] [Three]-way, [two-position] [modulating] control valve for hot-water reheat coil.

C. Hose Kits:  Minimum 400-psig (2758-kPa) working pressure, and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C).  Tag hose kits to equipment designations.

1. Length:  [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension>.

2. Minimum Diameter:  Equal to unit ventilator connection size.

D. Isolation Valves, Strainers, Unions, and Balance Valves:

1. Two-Piece Ball Valves:  Bronze body with stainless-steel ball and stem and galvanized-steel lever handle for each supply and return connection.  If balancing device is combination shutoff type with memory stop, isolation valve may be omitted on the return.

2. Calibrated-Orifice Balancing Valves:  Bronze body, ball type; 125-psig (860-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature; with calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, threaded ends, and equipped with a memory stop to retain set position.

3. Automatic Flow-Control Valve:  Brass or ferrous-metal body; 300-psig (2070-kPa) working pressure at 250 deg F (121 deg C), with removable, corrosion-resistant, tamperproof, self-cleaning piston spring; factory set to maintain constant indicated flow with plus or minus 10 percent over differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

4. Y-Pattern Hydronic Strainers:  Cast-iron body (ASTM A 126, Class B); 125-psig (860-kPa) working pressure; with threaded connections, bolted cover, perforated stainless-steel basket, and bottom drain connection.  Include minimum NPS 1/2 (DN 15) hose-end, full-port, ball-type blowdown valve in drain connection.

5. Wrought-Copper Unions:  ASME B16.22.

2.9 REMOTE CONDENSING UNITS

Retain this Article to require remote condensing units provided by unit ventilator manufacturer.

A. Description:  Factory assembled and tested; consisting of compressors, condenser coils, fans, motors, refrigerant receiver, and operating controls.  Construct, test, and rate condensing units according to ARI 210/240 and ASHRAE 15.

B. Casing:  Steel with baked-enamel finish; removable panels for access to controls, weep holes for water drainage, and mounting holes in base.

1. Casing Finish:  Baked enamel, in manufacturer's [standard] [custom] paint color as selected by Architect.

C. Compressor:  Hermetic, [scroll] [reciprocating] type; internally isolated for vibration with factory-installed safety devices as follows:

1. Antirecycle timer.

2. High-pressure cutout.

3. Low-pressure cutout or loss-of-charge switch.

4. Internal thermal-overload protection.

5. Current and voltage sensitive safety devices.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

D. Compressor Motor:  Start capacitor, relay, and contactor.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Retain first paragraph below if applying for LEED certification.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

E. Energy Efficiency:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1-2004, "Energy Standard for Buildings except Low-Rise Residential Buildings."

F. Refrigerant Piping Materials:

1. Drawn-Temper Copper Tube:  ASTM B 88, Type L (ASTM B 88M, Type B).

2. Annealed-Temper Copper Tube:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type K (ASTM B 88M, Type A)].

3. Wrought-Copper Fittings:  ASME B16.22.

Retain one of first two paragraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first paragraph or retain second paragraph to comply with Credit EA 4.

G. Refrigerant:  [R-22] [R-407C] [R-410A].

H. Refrigerant:  R-407C or R-410A.

I. Low ambient controls to permit operation down to 45 deg F (7 deg C).

J. Crankcase heater.

K. Charging and service fittings on exterior of casing.

L. Filter dryer.

Retain paragraph below for air-to-air heat pump.

M. Air-to-Air Heat Pump:  Pilot-operated, sliding-type reversing valve with replaceable magnetic coil, and controls for air-to-air heat pump operation with supplemental heat.

Retain first paragraph below for HGBP.

N. HGBP, constant-pressure expansion valve and controls to maintain continuous refrigeration system operation at 10 percent of full load.

O. Condenser:  Copper-tube, aluminum-fin coil, with liquid subcooler.

P. Condenser Fan:  Direct-drive, aluminum propeller fan; motor with thermal-overload protection.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motor:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Q. Accessories:  Polyethylene mounting base to provide a permanent foundation.

2.10 INTEGRAL COOLING CHASSIS

A. Description:  Assembly mounted within unit ventilator, factory assembled and tested; consisting of compressors, condenser coils, fans, motors, and refrigerant receivers; removable for maintenance, with plug and receptacle connections for control and power wiring.  Construct, test, and rate condensing units according to ARI 210/240 and ASHRAE 15.

B. Casing:  Galvanized steel with removable panels for access to controls and refrigerant piping.

C. Exterior Louver:  Extruded aluminum.

D. Compressor:  Hermetic, [scroll] [reciprocating] type; internally isolated for vibration with factory-installed safety devices as follows:

1. Antirecycle timer.

2. High-pressure cutout.

3. Low-pressure cutout or loss-of-charge switch.

4. Internal thermal-overload protection.

5. Current- and voltage-sensitive safety devices.

Retain first paragraph below if applying for LEED certification.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

E. Energy Efficiency:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1-2004, "Energy Standard for Buildings except Low-Rise Residential Buildings."

F. Refrigerant Piping Materials:

1. Drawn-Temper Copper Tube:  [ASTM B 88, Type L (ASTM B 88M, Type B)].

2. Annealed-Temper Copper Tube:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type K (ASTM B 88M, Type A)].

3. Wrought-Copper Fittings:  ASME B16.22.

Retain one of first two paragraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first paragraph or retain second paragraph to comply with Credit EA 4.

G. Refrigerant:  [R-22] [R-407C] [R-410A].

H. Refrigerant:  R-407C or R-410A.

I. Low ambient controls to permit operation down to 45 deg F (7 deg C).

J. Crankcase heater.

K. Charging and service fittings.

L. Filter dryer.

Retain paragraph below for air-to-air heat pump.

M. Air-to-Air Heat Pump:  Pilot-operated, sliding-type reversing valve with replaceable magnetic coil, and controls for air-to-air heat pump operation with supplemental heat.

Retain first paragraph below for HGBP.

N. HGBP, constant-pressure expansion valve and controls to maintain continuous refrigeration system operation at 10 percent of full load.

O. Condenser:  Copper-tube, aluminum-fin coil, with liquid subcooler.

P. Direct-Driven Condenser Fan:  Forward curved, double width, centrifugal; thermoplastic or painted-steel wheels and galvanized-steel fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motor:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

2.11 BASIC UNIT CONTROLS

A. Control devices and operational sequences are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete first paragraph and subparagraphs below if controls are part of overall temperature-control system.

B. Basic Unit Controls:

1. Control voltage transformer.

Verify control features with manufacturer.

2. [Wall-mounting] [Unit-mounted] thermostat with the following features.

a. Heat-cool-off switch.

b. Fan on-auto switch.

c. Fan-speed switch.

d. [Manual] [Automatic] changeover.

e. Adjustable deadband.

f. [Concealed] [Exposed] set point.

g. [Concealed] [Exposed] indication.

h. [Degree F] [Degree C] indication.

3. [Wall-mounting] [Unit-mounted] humidistat.

a. [Concealed] [Exposed] set point.

b. [Concealed] [Exposed] indication.

4. [Wall-mounting] [Unit-mounted] temperature sensor.

5. Unoccupied-period-override push button.

6. Data entry and access port.

a. Input data includes room temperature and humidity set points, and occupied and unoccupied periods.

b. Output data includes room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

C. [DDC ]Terminal Controller:

1. Safety Controls Operation:  Freezestat shall stop fan and close outdoor-air damper if air less than 38 deg F (3 deg C) enters coils.

2. Scheduled Operation:  Occupied and unoccupied periods on seven-day clock with a minimum of four programmable periods per day.

3. Unoccupied Period Override Operation:  [Two] <Insert number> hours.

4. Dual-Temperature Coil Operation:

a. Occupied Periods:  When chilled water is available, [open] [modulate] control valve if room temperature exceeds thermostat set point.  When hot water is available, [open] [modulate] control valve if room temperature falls below thermostat set point.

b. Unoccupied Periods:  When chilled water is available, close control valve.  When hot water is available, [open] [modulate] control valve if room temperature falls below thermostat setback temperature.

5. Hydronic Cooling-Coil Operation:

a. Occupied Periods:  [Open] [Modulate] control valve to provide cooling if room temperature exceeds thermostat set point.

b. Unoccupied Periods:  Close control valve.

Refrigerant coil may be cooling or heating with air-to-air heat pump.

6. Refrigerant-Coil Operation:

a. Occupied Periods:  Start compressor to maintain room temperature.

b. Unoccupied Periods:  [Stop compressor cooling] [Cycle compressor for heating to maintain setback temperature].

7. [Supplemental] Heating-Coil Operation:

a. Occupied Periods:  [Open control valve] [Modulate control valve] [Energize electric-resistance coil] to provide heating if room temperature falls below thermostat set point.

b. Unoccupied Periods:  Start fan and [open control valve] [modulate control valve] [energize electric-resistance coil] if room temperature falls below setback temperature.

c. Switch refrigerant-reversing valve to operate supplemental coil for heating when outdoor temperature is below [25 deg F (4 deg C)] <Insert temperature>.

8. Reheat-Coil Operation:

Retain first two subparagraphs below if reheat coil provides only reheat.

a. Humidity Control for Occupied Periods:  Humidistat [opens control valve] [modulates control valve] [energizes electric-resistance coil] to provide heating.  As room temperature rises above the set point, cooling coil valve [opens] [modulates] to maintain room temperature.

b. Humidity Control for Unoccupied Periods:  [Close control valve] [De-energize].

9. Outdoor-Air Damper Operation:  Open to [25] <Insert percent> percent fixed minimum intake during occupied periods, and close during unoccupied periods.

Retain subparagraph above for fixed outdoor-air intake; retain first subparagraph below for economizer cycle.  Energy recovery wheel is provided with fixed outdoor-air damper described above.

10. Outdoor-Air Damper Operation:  Open to [25] <Insert percent> percent fixed minimum intake, and maximum 100 percent of the fan capacity to comply with ASHRAE Cycle II during occupied periods, and close during unoccupied periods.  Microprocessor controller shall permit air-side economizer operation when outdoor air is less than [60 deg F (15 deg C)] <Insert temperature>.

11. Carbon Dioxide Sensor Operation:  During occupied periods, reset minimum outdoor-air ratio down to minimum [10] <Insert percent> percent to maintain maximum [800-ppm] <Insert concentration> concentration.

12. Face-and-Bypass Damper Operation:  Position damper to face of coils until room temperature equals thermostat set point; bypass after room-temperature set point is achieved.

13. Cooling Lockout:  During economizer cycle operation, block out cooling.

14. HGBP:  Open HGBP solenoid valve to maintain minimum suction pressure at compressor.

15. Energy Recovery Wheel Operation:

a. Factory-mounted and -wired, starting relay and manual motor starter for field wiring.

b. Occupied period is established by [remote signal] [room occupancy sensor].

c. Energy recovery wheel and inlet and discharge fans operate during occupied periods after room temperature set point has been achieved.

d. Energy recovery wheel operates during occupied periods, but stops when unit ventilator controls call for cooling, and outdoor-air temperatures permit free air cooling.

e. Energy recovery wheel and fans stop during unoccupied periods.

16. Controller shall have volatile-memory backup.

D. BAS Interface Requirements:

1. Interface relay for scheduled operation.

2. Interface relay to provide indication of fault at the central workstation.

3. Provide [BACnet] [or] [LonWorks] interface for central BAS workstation for the following functions:

a. Adjust set points.

b. Unit ventilator start, stop, and operating status.

c. Data inquiry to include [outdoor-air damper position,] supply- and room-air temperature[ and humidity].

d. Occupied and unoccupied schedules.

E. Electrical Connection:  Factory wire motors and controls for a single electrical connection.

2.12 METAL SHELVES AND CABINETS

Retain features required for Project.  Verify available features with manufacturer selected.  Coordinate this Article with Drawings.

A. Include manufacturer's standard cabinets to match unit ventilators with required installation hardware as indicated:

1. Open Shelving with Reinforced Shelves:

a. [Return-air plenum] [Radiation enclosure] and aluminum bar grille with finish to match unit ventilator grille.

b. Through-piping enclosure with solid top.

2. Closed Shelving with Reinforced Shelves:

a. [Return-air plenum] [Radiation enclosure] and aluminum bar grille with finish to match unit ventilator grille.

b. Through-piping enclosure with solid top.

c. Two sliding doors with key-operated locks.

3. Utility compartment with access panel with key-operated lock.

4. Wall and corner filler sections, and end panels finished to match shelving.

B. Painted Finish:  Manufacturer's [standard] [custom] baked enamel, in color selected by Architect, applied to shelving before shipping.

C. Cabinet Top:  Plastic-laminate top in color and pattern selected by Architect from manufacturer's [standard] [custom] colors.

2.13 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of unit ventilator, delete this Article and schedule unit ventilators on Drawings.

A. Fan:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (kPa).>

3. Fan Speed:  <Insert rpm.>

4. Motor Horsepower:  <Insert horsepower.>

B. Cooling Capacity:

1. Total:  <Insert Btu/h (kW).>

2. Sensible:  <Insert Btu/h (kW).>

3. Entering-Air Dry-Bulb Temperature:  <Insert deg F (deg C).>

4. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

C. Chilled-Water Coil:

1. Water Flow:  <Insert gpm (L/s).>

2. Water-Side Pressure Loss:  <Insert feet wg (kPa).>

3. Entering-Water Temperature:  <Insert deg F (deg C).>

D. Refrigerant Coil:

1. Suction Temperature:  <Insert deg F (deg C).>

E. Condensing Unit:

1. Ambient Temperature:  <Insert deg F (deg C).>

2. Compressor Power Input:  <Insert kW.>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, "Air Conditioners and Condensing Units" for cooling only equipment and "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements" for heat pump applications.

3. Cooling Energy Efficiency[ (EER)] [ (SEER)]:  <Insert value.>

Retain first subparagraph below for heat pump applications.

4. Heating Coefficient of Performance:  <Insert value.>

5. Voltage/Phase/Hertz:  <Insert values.>

6. Full-Load Amperes:  <Insert value.>

7. Maximum Circuit Amperes:  <Insert value.>

8. Maximum Overcurrent Protection:  <Insert value.>

F. Heating Capacity:

1. Output:  <Insert Btu/h (kW).>

2. Entering-Air Temperature:  <Insert deg F (deg C).>

3. Air-Temperature Rise:  <Insert deg F (deg C).>

G. Hot-Water Heating Coil:

1. Water Flow:  <Insert gpm (L/s).>

2. Water-Side Pressure Loss:  <Insert feet wg (kPa).>

3. Entering-Water Temperature:  <Insert deg F (deg C).>

H. Steam Heating Coil:

1. Inlet Steam Pressure:  <Insert psig (kPa).>

2. Condensing Capacity:  <Insert lb/h (g/s).>

I. Electric-Resistance Heating Coil:

1. Capacity:  <Insert kW.>

2. Number of Steps:  <Insert number.>

J. Reheat Capacity:

1. Output:  <Insert Btu/h (kW).>

2. Entering-Air Temperature:  <Insert deg F (deg C).>

3. Air-Temperature Rise:  <Insert deg F (deg C).>

K. Hot-Water Reheat Coil:

1. Water Flow:  <Insert gpm (L/s).>

2. Water-Side Pressure Loss:  <Insert feet wg (kPa).>

3. Entering-Water Temperature (during Cooling):  <Insert deg F (deg C).>

L. Steam Reheat Coil:

1. Inlet Steam Pressure:  <Insert psig (kPa).>

2. Condensing Rate:  <Insert lb/h (g/s).>

M. Electric-Resistance Reheat Coil:

1. Capacity:  <Insert kW.>

2. Number of Steps:  <Insert number.>

N. Filters:

Retain third option in first subparagraph below if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

1. Type:  [Washable foam] [Coated glass fiber] [Pleated cotton-polyester media].

2. Maximum Face Velocity:  <Insert fpm (m/s).>

3. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)] <Insert thickness>.

O. Energy Recovery Exhaust:

1. Airflow:  <Insert cfm (L/s).>

2. Entering-Air Dry-Bulb Temperature:  <Insert deg F (deg C).>

3. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

4. Leaving-Air Dry-Bulb Temperature:  <Insert deg F (deg C).>

5. Leaving-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

6. Fan Motor Horsepower:  <Insert horsepower.>

P. Energy Recovery Outdoor Air:

1. Airflow:  <Insert cfm (L/s).>

2. Entering-Air Dry-Bulb Temperature:  <Insert deg F (deg C).>

3. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

4. Leaving-Air Dry-Bulb Temperature:  <Insert deg F (deg C).>

5. Leaving-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

6. Motor Horsepower:  <Insert horsepower.>

Q. Energy Recovery Wheel:

1. Heat-Transfer Efficiency:  <Insert percent.>

2. Drive Motor Horsepower:  <Insert horsepower.>

R. Electrical Characteristics for Single-Point Connection:

1. Voltage/Phase/Hertz:  <Insert values.>

2. Full-Load Amperes:  <Insert value.>

3. Maximum Circuit Amperes:  <Insert value.>

4. Maximum Overcurrent Protection:  <Insert value.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas to receive unit ventilators for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in for piping and electrical connections to verify actual locations before unit ventilator installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install unit ventilators to comply with NFPA 90A.

Retain paragraph below for horizontal, suspended units.

B. Suspend horizontal unit ventilators from structure with threaded steel rods and minimum [0.25-inch (6.35-mm) static-deflection, elastomeric vibration isolation hanger] [1.0-inch (25-mm) static-deflection spring hangers].  Vibration isolators are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Verify mounting height in paragraph below with authorities having jurisdiction to comply with requirements of the Americans with Disabilities Act.

C. Verify location of thermostats, humidistats, and other exposed control sensors with Drawings and room details before installation.  Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

Retain paragraph below for condensing units not packaged with unit ventilators.

D. Refer to Division 23 Section "Packaged Compressor and Condenser Units" for condensing units matched to refrigerant cooling coil packaged in unit ventilators.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.  Specific connection requirements are as follows:

1. Install piping adjacent to machine to allow service and maintenance.

2. Connect piping to unit ventilator factory hydronic piping package.  Install piping package if shipped loose.

3. Connect condensate drain to indirect waste.

Retain paragraph below for unit ventilators with remote condensing units.

B. Install refrigerant piping as required by Division 23 Section "Refrigerant Piping," and add refrigerant as required to compensate for length of piping.

Retain first paragraph below for ducted, unit ventilators.  Coordinate duct installation requirements with Drawings and with requirements specified in Division 23 Sections "Metal Ducts," "Nonmetal Ducts," and "Air Duct Accessories."

C. Connect supply and return ducts to unit ventilators with flexible duct connectors specified in Division 23 Section "Air Duct Accessories." Comply with safety requirements in UL 1995 for duct connections.

D. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

E. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with last paragraph above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

1. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Delete first subparagraph below if units do not have electric heat.

2. Operate electric heating elements through each stage to verify proper operation and electrical connections.

3. Test and adjust controls and safety devices.  Replace damaged and malfunctioning controls and equipment.

Retain subparagraph below if energy recovery wheel is required.

4. Record temperatures entering and leaving energy recovery wheel when outdoor-air temperature is a minimum of 15 deg F (8.3 deg C) higher, or 20 deg F (11 deg C) lower, than room temperature.

C. Remove and replace malfunctioning units and retest as specified above.

3.5 ADJUSTING

Retain this Article if control devices are specified in this Section; delete if they are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

A. Adjust initial temperature and humidity set points.

B. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.6 DEMONSTRATION

Delete this Article if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain unit ventilators.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 238223

UNIT VENTILATORS
238223 - 1

