Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
09/04 (R 05/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262200 - LOW-VOLTAGE TRANSFORMERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of dry-type transformers rated 600 V and less, with capacities up to 1000 kVA:

Adjust list below to suit Project.

1. Distribution transformers.

2. Buck-boost transformers.

1.3 SUBMITTALS

A. Product Data:  Include rated nameplate data, capacities, weights, dimensions, minimum clearances, installed devices and features, and performance for each type and size of transformer indicated.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems.

C. Manufacturer Seismic Qualification Certification:  Submit certification that transformers, accessories, and components will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For testing agency.

E. Source quality-control test reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For transformers to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, retain one of first two paragraphs below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7.

C. Source Limitations:  Obtain each transformer type through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with IEEE C57.12.91, "Test Code for Dry-Type Distribution and Power Transformers."

1.5 DELIVERY, STORAGE, AND HANDLING

A. Temporary Heating:  Apply temporary heat according to manufacturer's written instructions within the enclosure of each ventilated-type unit, throughout periods during which equipment is not energized and when transformer is not in a space that is continuously under normal control of temperature and humidity.

1.6 COORDINATION

Delete first paragraph below if no transformers are floor mounted.

A. Coordinate size and location of concrete bases with actual transformer provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

B. Coordinate installation of wall-mounting and structure-hanging supports with actual transformer provided.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. ACME Electric Corporation; Power Distribution Products Division.

2. Challenger Electrical Equipment Corp.; a division of Eaton Corp.

3. Controlled Power Company.

4. Eaton Electrical Inc.; Cutler-Hammer Products.

5. Federal Pacific Transformer Company; Division of Electro-Mechanical Corp.

6. General Electric Company.

7. Hammond Co.; Matra Electric, Inc.

8. Magnetek Power Electronics Group.

9. Micron Industries Corp.

10. Myers Power Products, Inc.

11. Siemens Energy & Automation, Inc.

12. Sola/Hevi-Duty.

13. Square D; Schneider Electric.

14. <Insert manufacturer's name.>

2.2 GENERAL TRANSFORMER REQUIREMENTS

A. Description:  Factory-assembled and -tested, air-cooled units for 60-Hz service.

B. Cores:  Grain-oriented, non-aging silicon steel.

C. Coils:  Continuous windings without splices except for taps.

1. Internal Coil Connections:  Brazed or pressure type.

Usually retain aluminum option in subparagraph below.  See Evaluations for discussion of copper vs. aluminum winding material.

2. Coil Material:  [Aluminum] [Copper].

2.3 DISTRIBUTION TRANSFORMERS

A. Comply with NEMA ST 20, and list and label as complying with UL 1561.

Delete first paragraph below if seismic bracing is not required.  Coordinate with Parts 1 and 3.

B. Provide transformers that are constructed to withstand seismic forces specified in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

C. Cores:  One leg per phase.

If all transformers have same enclosure, retain one of two paragraphs and associated subparagraphs below.  Retain first paragraph for indoor transformers; second, for outdoor transformers.  If several types of enclosures are required for Project, delete paragraphs and indicate enclosure type on Drawings.

D. Enclosure:  [Ventilated] [Totally enclosed, nonventilated], NEMA 250, Type 2.

1. Core and coil shall be encapsulated within resin compound, sealing out moisture and air.

E. Enclosure:  [Ventilated] [Totally enclosed, nonventilated], NEMA 250, [Type 3R] [Type 4X, stainless steel].

1. Core and coil shall be encapsulated within resin compound, sealing out moisture and air.

Retain paragraph and subparagraph below for custom finish.

F. Transformer Enclosure Finish:  Comply with NEMA 250.

1. Finish Color:  [Gray] [ANSI 49 gray] [ANSI 61 gray].

In three paragraphs below, first option for each size is most prevalent standard with many manufacturers; second option is available from most manufacturers.  If multiple transformers are required with different tap arrangements, delete paragraphs and show tap information on Drawings.

G. Taps for Transformers Smaller Than 3 kVA:  [None] [One 5 percent tap above normal full capacity].

H. Taps for Transformers 7.5 to 24 kVA:  [One 5 percent tap above and one 5 percent tap below normal full capacity] [Two 5 percent taps below rated voltage].

I. Taps for Transformers 25 kVA and Larger:  [Two 2.5 percent taps above and two 2.5 percent taps below normal full capacity] [Two 2.5 percent taps above and four 2.5 percent taps below normal full capacity].

See Editing Instruction No. 2 in the Evaluations for discussion of insulation classes.  See "Energy Considerations" Article in the Evaluations for discussion of relative efficiencies.  If 115 or 80 deg C rating is retained in paragraph below and all transformers are 15 kVA or larger, delete "Energy Efficiency for Transformers Rated 15 kVA and Larger" Paragraph.

J. Insulation Class:  220 deg C, UL-component-recognized insulation system with a maximum of [150] [115] [80] deg C rise above 40 deg C ambient temperature.

Retain features in seven paragraphs below to suit Project.  Coordinate with Drawings.

Retain paragraph and subparagraphs below for energy-efficient transformers complying with NEMA TP 1.  See Evaluations for discussion of energy efficiency.  NEMA TP 1 excludes dry-type transformers rated below 15 kVA.

K. Energy Efficiency for Transformers Rated 15 kVA and Larger:

1. Complying with NEMA TP 1, Class 1 efficiency levels.

2. Tested according to NEMA TP 2.

Retain paragraph and subparagraphs below for transformers that will supply significant nonsinusoidal load current.  Show transformer K-factor on Drawings or in schedule.  See Evaluations for discussion of K-factors.

L. K-Factor Rating:  Transformers indicated to be K-factor rated shall comply with UL 1561 requirements for nonsinusoidal load current-handling capability to the degree defined by designated K-factor.

1. Unit shall not overheat when carrying full-load current with harmonic distortion corresponding to designated K-factor.

2. Indicate value of K-factor on transformer nameplate.

Shielding in paragraph below reduces conducted, common-mode, high-frequency transient noise to sensitive loads.  See Evaluations for discussion of shielding.

M. Electrostatic Shielding:  Each winding shall have an independent, single, full-width copper electrostatic shield arranged to minimize interwinding capacitance.

1. Arrange coil leads and terminal strips to minimize capacitive coupling between input and output terminals.

2. Include special terminal for grounding the shield.

3. Shield Effectiveness:

a. Capacitance between Primary and Secondary Windings:  Not to exceed 33 picofarads over a frequency range of 20 Hz to 1 MHz.

b. Common-Mode Noise Attenuation:  Minimum of minus 120 dBA at 0.5 to 1.5 kHz; minimum of minus 65 dBA at 1.5 to 100 kHz.

c. Normal-Mode Noise Attenuation:  Minimum of minus 52 dBA at 1.5 to 10 kHz.

Indicate wall-mounting transformers on Drawings.  Generally, factory-made wall-mounting brackets are available for transformers up to 75 kVA.  High-efficiency, shielding, and K-factor construction increase transformer weight.  Verify that wall brackets are available from specified manufacturers for specified sizes.  Verify compliance with seismic requirements.

N. Wall Brackets:  Manufacturer's standard brackets.

Retain paragraph below for installations in tropical environments where transformers might be disconnected from normal electrical supply or are lightly loaded for extended periods of time.

O. Fungus Proofing:  Permanent fungicidal treatment for coil and core.

Retain one of two paragraphs below.  Retain first if equipment sound-level ratings are required to be lower than those in NEMA ST 20.  NEMA ST 20 sound levels are as follows:  Up to 9 kVA:  40 dBA; 30 to 50 kVA:  45 dBA; 51 to 150 kVA:  50 dBA; 151 to 300 kVA:  55 dBA; 301 to 500 kVA:  60 dBA; 501 to 700 kVA:  62 dBA; 701 to 1000 kVA:  64 dBA.  See Editing Instruction No. 3 in the Evaluations for discussion of sound generated by transformers.

P. Low-Sound-Level Requirements:  Minimum of 3 dBA less than NEMA ST 20 standard sound levels when factory tested according to IEEE C57.12.91.

Q. Low-Sound-Level Requirements:  Maximum sound levels, when factory tested according to IEEE C57.12.91, as follows:

1. 9 kVA and Less:  <Insert dBA value.>

2. 30 to 50 kVA:  <Insert dBA value.>

3. 51 to 150 kVA:  <Insert dBA value.>

4. 151 to 300 kVA:  <Insert dBA value.>

5. 301 to 500 kVA:  <Insert dBA value.>

6. 501 to 750 kVA:  <Insert dBA value.>

7. 751 to 1000 kVA:  <Insert dBA value.>

2.4 BUCK-BOOST TRANSFORMERS

A. Description:  Self-cooled, two-winding dry type, rated for continuous duty and with wiring terminals suitable for connection as autotransformer.  Transformers shall comply with NEMA ST 1 and shall be listed and labeled as complying with UL 506 or UL 1561.

B. Enclosure:  Ventilated, NEMA 250, Type 2.

1. Finish Color:  [Gray] [ANSI 49 gray] [ANSI 61 gray].

2.5 IDENTIFICATION DEVICES

Retain this Article to specify nameplates.  Coordinate names of transformers with Drawings and schedules.

A. Nameplates:  Engraved, laminated-plastic or metal nameplate for each [distribution] [buck-boost] transformer, mounted with corrosion-resistant screws.  Nameplates and label products are specified in Division 26 Section "Identification for Electrical Systems."

2.6 SOURCE QUALITY CONTROL

A. Test and inspect transformers according to IEEE C57.12.91.

Retain paragraph below if retaining either "Low-Sound-Level Requirements" Paragraph in "Distribution Transformers" Article.

B. Factory Sound-Level Tests:  Conduct sound-level tests on equipment for this Project.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine conditions for compliance with enclosure- and ambient-temperature requirements for each transformer.

B. Verify that field measurements are as needed to maintain working clearances required by NFPA 70 and manufacturer's written instructions.

C. Examine walls, floors, roofs, and concrete bases for suitable mounting conditions where transformers will be installed.

Adjust 5-ohm value in first paragraph below to suit Project.

D. Verify that ground connections are in place and requirements in Division 26 Section "Grounding and Bonding for Electrical Systems" have been met.  Maximum ground resistance shall be 5 ohms at location of transformer.

E. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Verify seismic-bracing requirements with authorities having jurisdiction.  Wall-mounting transformers may not be appropriate in areas of seismic activity.

A. Install wall-mounting transformers level and plumb with wall brackets fabricated by transformer manufacturer.

Retain subparagraph below for projects in areas of seismic activity.

1. Brace wall-mounting transformers as specified in Division 26 Section "Vibration and Seismic Controls for Electrical Systems.

If appropriate, retain paragraph below for projects in areas of seismic activity.

B. Construct concrete bases and anchor floor-mounting transformers according to manufacturer's written instructions[, seismic codes applicable to Project,] and requirements in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

3.3 CONNECTIONS

A. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

B. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain one of three paragraphs below that identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain requirement for field quality-control test reports in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections and prepare test reports.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraph below to describe tests and inspections to be performed by any of the entities in three paragraphs above.

D. Tests and Inspections:

Tests referenced in subparagraph below are from NETA Acceptance Testing Specification and include inspection procedures to verify proper installation.  They also include tests and measurements of insulation resistance and turns ratios.  Cost of extensive testing may not be warranted for some projects.  Revise subparagraph to suit Project.

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

E. Remove and replace units that do not pass tests or inspections and retest as specified above.

F. Infrared Scanning:  Two months after Substantial Completion, perform an infrared scan of transformer connections.

1. Use an infrared-scanning device designed to measure temperature or detect significant deviations from normal values.  Provide documentation of device calibration.

2. Perform 2 follow-up infrared scans of transformers, one at 4 months and the other at 11 months after Substantial Completion.

3. Prepare a certified report identifying transformer checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and scanning observations after remedial action.

G. Test Labeling:  On completion of satisfactory testing of each unit, attach a dated and signed "Satisfactory Test" label to tested component.

3.5 ADJUSTING

A. Record transformer secondary voltage at each unit for at least 48 hours of typical occupancy period.  Adjust transformer taps to provide optimum voltage conditions at secondary terminals.  Optimum is defined as not exceeding nameplate voltage plus 10 percent and not being lower than nameplate voltage minus 3 percent at maximum load conditions.  Submit recording and tap settings as test results.

B. Connect buck-boost transformers to provide nameplate voltage of equipment being served, plus or minus 5 percent, at secondary terminals.

C. Output Settings Report:  Prepare a written report recording output voltages and tap settings.

3.6 CLEANING

A. Vacuum dirt and debris; do not use compressed air to assist in cleaning.

END OF SECTION 16461

	LOW-VOLTAGE TRANSFORMERS
	262200 - 1



