Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
06/02 (R 06/06)

Copyright 2002 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262923 - VARIABLE-FREQUENCY MOTOR CONTROLLERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, which requires the use of mechanical or electrical variable speed drives on fan motors used in VAV system fans that are 15 hp and larger and on motors in variable flow hydronic systems that are larger than 50 hp.

Energy savings resulting from the use of variable frequency motor controllers on motors other than required by Prerequisite EA 2 can be combined with other energy-saving measures to meet the requirements of LEED-NC Credit EA 1.

LEED-NC Credit EA 5 requires the development of a Measurement & Verification (M&V) Plan to achieve this credit.  Energy used by each VFC can be used in the simulation calibration process required by the International Performance Measurement & Verification Protocol (IPMVP), Volume III, Chapter 4, "Whole Building Calibrated Simulation" (Option D) to verify the building's compliance with this credit.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes solid-state, PWM, VFCs for speed control of three-phase, squirrel-cage induction motors.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 26 Section "Electrical Power Monitoring and Control" for monitoring and control of motor circuits.

2. Division 26 Section "Transient-Voltage Suppression for Low-Voltage Electrical Power Circuits" for low-voltage power, control, and communication surge suppressors.

1.3 DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A. BMS:  Building management system.

B. IGBT:  Integrated gate bipolar transistor.

C. LAN:  Local area network.

D. PID:  Control action, proportional plus integral plus derivative.

E. PWM:  Pulse-width modulated.

F. VFC:  Variable frequency controller.

1.4 SUBMITTALS

A. Product Data:  For each type of VFC.  Include dimensions, mounting arrangements, location for conduit entries, shipping and operating weights, and manufacturer's technical data on features, performance, electrical ratings, characteristics, and finishes.

B. Shop Drawings:  For each VFC.

1. Include dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Each installed unit's type and details.

b. Nameplate legends.

c. Short-circuit current rating of integrated unit.

Retain subparagraph below if series rating of overcurrent protective devices is used or if VFCs are used without front-end overcurrent protective devices.

d. Listed and labeled for series rating of overcurrent protective devices in combination controllers by an NRTL acceptable to authorities having jurisdiction.

Retain first subparagraph below if combination controllers are used.

e. Features, characteristics, ratings, and factory settings of each motor-control center unit.

2. Wiring Diagrams:  Power, signal, and control wiring for VFCs.  Provide schematic wiring diagram for each type of VFC.

C. Coordination Drawings:  Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around VFCs where pipe and ducts are prohibited.  Show VFC layout and relationships between electrical components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate field measurements.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

D. Manufacturer Seismic Qualification Certification:  Submit certification that VFCs, accessories, and components will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For [manufacturer] [testing agency] [manufacturer and testing agency].

Retain first paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For VFCs, all installed devices, and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

1. Routine maintenance requirements for VFCs and all installed components.

Retain subparagraph below if circuit breakers are used in VFCs.

2. Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

Coordinate two paragraphs below with Parts 2 and 3 where bypass controllers are required.

H. Load-Current and Overload-Relay Heater List:  Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

Retain paragraph above or below if motor running overload protection is specified as part of bypass controller in Part 2.

I. Load-Current and List of Settings of Adjustable Overload Relays:  Compile after motors have been installed and arrange to demonstrate that dip switch settings for motor running overload protection suit actual motor to be protected.

1.5 QUALITY ASSURANCE

A. Manufacturer Qualifications:  A qualified manufacturer.  Maintain, within 100 miles (160 km) of Project site, a service center capable of providing training, parts, and emergency maintenance and repairs.

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, retain first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

C. Source Limitations:  Obtain VFCs of a single type through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NFPA 70.

VFCs with the same functional characteristics may vary in length and depth among manufacturers.  If installation space is limited, show maximum dimensions on Drawings, ensure that equipment is available to fit, and retain paragraph below; delete if space is not a concern.

F. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for VFCs, minimum clearances between VFCs, and adjacent surfaces and other items.  Comply with indicated maximum dimensions and clearances.

1.6 DELIVERY, STORAGE, AND HANDLING

Retain first paragraph below if there are obstacles to movement of normal shipping lengths of VFCs.  Coordinate with Drawings.

A. Deliver VFCs in shipping splits of lengths that can be moved past obstructions in delivery path as indicated.

B. Store VFCs indoors in clean, dry space with uniform temperature to prevent condensation.  Protect VFCs from exposure to dirt, fumes, water, corrosive substances, and physical damage.

Delete paragraph below if indoor space is likely to be available at Project site.

C. If stored in areas subject to weather, cover VFCs to protect them from weather, dirt, dust, corrosive substances, and physical damage.  Remove loose packing and flammable materials from inside controllers; install electric heating of sufficient wattage to prevent condensation.

1.7 PROJECT CONDITIONS

A. Environmental Limitations:  Rate equipment for continuous operation, capable of driving full load without derating, under the following conditions, unless otherwise indicated:

1. Ambient Temperature:  0 to 40 deg C.

2. Humidity:  Less than 90 percent (noncondensing).

3. Altitude:  Not exceeding 3300 feet (1005 m).

4. <Insert unusual service conditions.>

Retain paragraph and subparagraphs below if interruption of existing electrical service is required.  Coordinate with requirements specified in Division 01 Section "Temporary Facilities and Controls" for temporary utilities.

B. Interruption of Existing Electrical Service:  Do not interrupt electrical service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of electrical service.

2. Indicate method of providing temporary electrical service.

3. Do not proceed with interruption of electrical service without [Architect's] [Construction Manager's] [Owner's] written permission.

Retain paragraph below if installation space for VFCs is limited; show maximum dimensions on Drawings.

C. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for VFCs, including clearances between VFCs, and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

Specify unusual environmental or service conditions here.  See Editing Instruction No. 2 in the Evaluations.  Otherwise, indicate typical environmental conditions as follows:  For VFCs installed outdoors, indicate minimum and maximum ambient temperatures and expected humidity range.

1.8 COORDINATION

A. Coordinate layout and installation of VFCs with other construction including conduit, piping, equipment, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

Retain one or both paragraphs below if required for VFCs.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

Revise two paragraphs below to refer to other Divisions, such as Division 14 for conveyor systems, if control coordination is required.

D. Coordinate features of VFCs, installed units, and accessory devices with pilot devices and control circuits to which they connect.

E. Coordinate features, accessories, and functions of each VFC and each installed unit with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Spare Fuses:  Furnish one spare for every [five] <Insert number> installed, but no fewer than one set of [three] <Insert number> of each type and rating.

2. Indicating Lights:  [Two] <Insert number> of each type installed.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. ABB Power Distribution, Inc.; ABB Control, Inc. Subsidiary.

2. Baldor Electric Company (Graham).

3. Danfoss Inc.; Danfoss Electronic Drives Div.

4. Eaton Corporation; Cutler-Hammer Products.

5. General Electric Company; GE Industrial Systems.

6. Rockwell Automation; Allen-Bradley Co.; Industrial Control Group.

7. Siemens Energy and Automation; Industrial Products Division.

8. Square D.

9. Toshiba International Corporation.

10. <Insert manufacturer's name.>

2.2 VARIABLE FREQUENCY CONTROLLERS

Two paragraphs and associated subparagraph below provide a sample specification for this type of controller; revise to suit Project.

A. Description:  NEMA ICS 2, IGBT, PWM, VFC; listed and labeled as a complete unit and arranged to provide variable speed of an NEMA MG 1, Design B, 3-phase induction motor by adjusting output voltage and frequency.

1. Provide unit suitable for operation of [standard] [premium]-efficiency motor as defined by NEMA MG 1.

B. Design and Rating:  Match load type such as fans, blowers, and pumps; and type of connection used between motor and load such as direct or through a power-transmission connection.

Retain one of three options in first paragraph below or revise ratings to suit Project.

C. Output Rating:  3-phase; 6 to [60 Hz, with voltage proportional to frequency throughout voltage range] [66 Hz, with torque constant as speed changes] [120 Hz, with horsepower constant throughout speed range].

D. Unit Operating Requirements:

Revise subparagraphs below to suit Project.

1. Input ac voltage tolerance of [208 V, plus or minus 5] [380 to 500 V, plus or minus 10] [525 to 575 V, plus or minus 10] percent.

2. Input frequency tolerance of 50/60 Hz, plus or minus 6 percent.

3. Minimum Efficiency:  96 percent at 60 Hz, full load.

4. Minimum Displacement Primary-Side Power Factor:  96 percent.

5. Overload Capability:  1.1 times the base load current for 60 seconds; 2.0 times the base load current for 3 seconds.

6. Starting Torque:  100 percent of rated torque or as indicated.

7. Speed Regulation:  Plus or minus 1 percent.

E. Isolated control interface to allow controller to follow control signal over an 11:1 speed range.

Retain one of two subparagraphs below with paragraph above.

1. Electrical Signal:  4 to 20 mA at 24 V.

2. Pneumatic Signal:  3 to 15 psig (20 to 104 kPa).

F. Internal Adjustability Capabilities:

1. Minimum Speed:  5 to 25 percent of maximum rpm.

2. Maximum Speed:  80 to 100 percent of maximum rpm.

3. Acceleration:  2 to a minimum of 22 seconds.

4. Deceleration:  2 to a minimum of 22 seconds.

5. Current Limit:  50 to a minimum of 110 percent of maximum rating.

Retain first paragraph and subparagraphs below if applicable.  Coordinate with Drawings and control sequences.

G. Self-Protection and Reliability Features:

Retain subparagraphs below to suit Project.

1. Input transient protection by means of surge suppressors.

2. Under- and overvoltage trips; inverter overtemperature, overload, and overcurrent trips.

3. Motor Overload Relay:  Adjustable and capable of NEMA ICS 2, Class [10] [20] [30] performance.

4. Notch filter to prevent operation of the controller-motor-load combination at a natural frequency of the combination.

5. Instantaneous line-to-line and line-to-ground overcurrent trips.

6. Loss-of-phase protection.

7. Reverse-phase protection.

8. Short-circuit protection.

9. Motor overtemperature fault.

H. Multiple-Motor Capability:  Controller suitable for service to multiple motors and having a separate overload relay and protection for each controlled motor.  Overload relay shall shut off controller and motors served by it when overload relay is tripped.

Retain one or both of first two paragraphs below to suit Project.

I. Automatic Reset/Restart:  Attempts three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction.  Bidirectional autospeed search shall be capable of starting into rotating loads spinning in either direction and returning motor to set speed in proper direction, without damage to controller, motor, or load.

J. Power-Interruption Protection:  To prevent motor from re-energizing after a power interruption until motor has stopped.

K. Torque Boost:  Automatically varies starting and continuous torque to at least 1.5 times the minimum torque to ensure high-starting torque and increased torque at slow speeds.

L. Motor Temperature Compensation at Slow Speeds:  Adjustable current fall-back based on output frequency for temperature protection of self-cooled, fan-ventilated motors at slow speeds.

If input voltage or current distortion due to harmonic generation in controller is a concern, consult manufacturer for options available to mitigate harmonic distortion.  Options may include dc bus link reactors, isolation transformers, active and passive harmonic filters, and phase shifting transformers.  Insert requirements in paragraph below.

M. Input Line Conditioning:  <Insert requirements.>

If controller output voltage exceeds motor pulse-withstand capability, consult manufacturer for options available for conditioning output voltage.  Options may include line inductors, output limit filters, sine wave filters, and motor termination filters.  Insert requirements in first paragraph below.

N. VFC Output Filtering:  <Insert requirements.>

O. Status Lights:  Door-mounted LED indicators shall indicate the following conditions:

1. Power on.

2. Run.

3. Overvoltage.

4. Line fault.

5. Overcurrent.

6. External fault.

P. Panel-Mounted Operator Station:  Start-stop and auto-manual selector switches with manual speed control potentiometer and elapsed time meter.

Q. Indicating Devices:  Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate the following controller parameters:

1. Output frequency (Hz).

2. Motor speed (rpm).

3. Motor status (running, stop, fault).

4. Motor current (amperes).

5. Motor torque (percent).

6. Fault or alarming status (code).

7. PID feedback signal (percent).

8. DC-link voltage (VDC).

9. Set-point frequency (Hz).

10. Motor output voltage (V).

Retain first paragraph and subparagraphs below if control signal interface is required.

R. Control Signal Interface:

1. Electric Input Signal Interface:  A minimum of 2 analog inputs (0 to 10 V or 0/4-20 mA) and 6 programmable digital inputs.

2. Pneumatic Input Signal Interface:  3 to 15 psig (20 to 104 kPa).

3. Remote Signal Inputs:  Capability to accept any of the following speed-setting input signals from the BMS or other control systems:

a. 0 to 10-V dc.

b. 0-20 or 4-20 mA.

c. Potentiometer using up/down digital inputs.

d. Fixed frequencies using digital inputs.

e. RS485.

f. Keypad display for local hand operation.

4. Output Signal Interface:

a. A minimum of 1 analog output signal (0/4-20 mA), which can be programmed to any of the following:

1) Output frequency (Hz).

2) Output current (load).

3) DC-link voltage (VDC).

4) Motor torque (percent).

5) Motor speed (rpm).

6) Set-point frequency (Hz).

5. Remote Indication Interface:  A minimum of 2 dry circuit relay outputs (120-V ac, 1 A) for remote indication of the following:

a. Motor running.

b. Set-point speed reached.

c. Fault and warning indication (overtemperature or overcurrent).

d. PID high- or low-speed limits reached.

S. Communications:  Provide an RS485 interface allowing VFC to be used with an external system within a multidrop LAN configuration.  Interface shall allow all parameter settings of VFC to be programmed via BMS control.  Provide capability for VFC to retain these settings within the nonvolatile memory.

T. Manual Bypass:  Magnetic contactor arranged to safely transfer motor between controller output and bypass controller circuit when motor is at zero speed.  Controller-off-bypass selector switch sets mode, and indicator lights give indication of mode selected.  Unit shall be capable of stable operation (starting, stopping, and running), with motor completely disconnected from controller (no load).

Retain paragraph above or below or delete both.  For large horsepower motors, consider using a reduced-voltage bypass controller instead of full-voltage controller below; revise to suit Project.

U. Bypass Controller:  NEMA ICS 2, full-voltage, nonreversing enclosed controller with across-the-line starting capability in manual-bypass mode.  Provide motor overload protection under both modes of operation with control logic that allows common start-stop capability in either mode.

Not all manufacturers offer all options in paragraph below.  Coordinate with manufacturers selected.

V. Integral Disconnecting Means:  [NEMA AB 1, instantaneous-trip circuit breaker] [NEMA AB 1, molded-case switch] [NEMA KS 1, nonfusible switch] [NEMA KS 1, fusible switch] with lockable handle.

Retain paragraph above or below or delete both.

W. Isolating Switch:  Non-load-break switch arranged to isolate VFC and permit safe troubleshooting and testing, both energized and de-energized, while motor is operating in bypass mode.

If retaining paragraph below, consider adding Specifications for remote indicating devices.

X. Remote Indicating Circuit Terminals:  Mode selection, controller status, and controller fault.

2.3 ENCLOSURES

NEMA 250, Type 1 enclosure is normally standard.  If specialized enclosures are required, consult manufacturer and insert requirements in this Article.

A. <Insert enclosure requirements.>

2.4 ACCESSORIES

A. Devices shall be factory installed in controller enclosure, unless otherwise indicated.

Retain two paragraphs below if applicable.  Coordinate with Drawings.

B. Push-Button Stations, Pilot Lights, and Selector Switches:  NEMA ICS 2, heavy-duty type.

C. Stop and Lockout Push-Button Station:  Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

Retain first paragraph below if required.

D. Control Relays:  Auxiliary and adjustable time-delay relays.

E. Standard Displays:

1. Output frequency (Hz).

2. Set-point frequency (Hz).

3. Motor current (amperes).

4. DC-link voltage (VDC).

5. Motor torque (percent).

6. Motor speed (rpm).

7. Motor output voltage (V).

F. Historical Logging Information and Displays:

1. Real-time clock with current time and date.

2. Running log of total power versus time.

3. Total run time.

4. Fault log, maintaining last four faults with time and date stamp for each.

Retain paragraph below with three external current transformers.  Requires external current transformers to monitor status of input circuit.

G. Current-Sensing, Phase-Failure Relays for Bypass Controller:  Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

2.5 FACTORY FINISHES

Revise this Article to include custom colors.  Coordinate custom-color requirements with sample submittal requirements.

A. Finish:  Manufacturer's standard <Insert color> paint applied to factory-assembled and -tested VFCs before shipping.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas, surfaces, and substrates to receive VFCs for compliance with requirements, installation tolerances, <Insert Project-specific conditions,> and other conditions affecting performance.

B. Examine roughing-in for conduit systems to verify actual locations of conduit connections before VFC installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

Delete this Article if VFCs and control devices and their types and features are delineated on Drawings.

A. Select features of each VFC to coordinate with ratings and characteristics of supply circuit and motor; required control sequence; and duty cycle of motor, controller, and load.

B. Select horsepower rating of controllers to suit motor controlled.

3.3 INSTALLATION

Coordinate this Article with Drawings.

Retain paragraph below if required and specify alternative anchoring.  Coordinate mounting methods with Drawings, including surface-mounting requirements for small controllers.  Add requirements for special anchorage and seismic restraint if applicable.

A. Anchor each VFC assembly to steel-channel sills arranged and sized according to manufacturer's written instructions.  Attach by bolting.  Level and grout sills flush with mounting surface.

Coordinate mounting and anchoring of VFCs with drawing details.  If drawing details are explicit, delete paragraph below.  Retain for floor-mounting equipment.

B. Install VFCs on concrete bases.

Retain first paragraph below if seismic controls are Project requirement.  Coordinate with Drawings.

C. Comply with mounting and anchoring requirements specified in Division 26 Section "Hangers and Supports for Electrical Systems."

D. Controller Fuses:  Install fuses in each fusible switch.  Comply with requirements in Division 26 Section "Fuses."

3.4 CONCRETE BASES

Retain this Article for floor-mounting units.

A. Coordinate size and location of concrete bases.  Verify structural requirements with structural engineer.

B. Concrete base is specified in Division 26 Section "Common Work Results for Electrical," and concrete materials and installation requirements are specified in Division 03.

3.5 IDENTIFICATION

A. Identify VFCs, components, and control wiring according to Division 26 Section "Identification for Electrical Systems."

If specific operational procedures are required in emergency situations, specify below.  Show specific information to be included in framed instructions on Drawings; delete paragraph below if not required.

B. Operating Instructions:  Frame printed operating instructions for VFCs, including control sequences and emergency procedures.  Fabricate frame of finished metal, and cover instructions with clear acrylic plastic.  Mount on front of VFC units.

3.6 CONTROL WIRING INSTALLATION

Retain this Article if applicable or if remote control or indication is not required.

A. Install wiring between VFCs and remote devices according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

B. Bundle, train, and support wiring in enclosures.

C. Connect hand-off-automatic switch and other automatic-control devices where applicable.

1. Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

2. Connect selector switches with control circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.7 CONNECTIONS

Coordinate conduit installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Conduit installation requirements are specified in other Division 26 Sections.  Drawings indicate general arrangement of conduit, fittings, and specialties.

B. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

3.8 FIELD QUALITY CONTROL

Retain paragraph and subparagraphs below to require Contractor to prepare VFCs for manufacturer's field service technician and for acceptance testing.

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each enclosed controller element, bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

Retain paragraph and subparagraphs below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  For solid-state, variable frequency controllers and solid-state, reduced-voltage controllers, supervision by personnel familiar with equipment is important.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to perform the following:

1. Inspect controllers, wiring, components, connections, and equipment installation.[  Test and adjust controllers, components, and equipment.]

2. Assist in field testing of equipment[ including pretesting and adjusting of solid-state controllers].

3. Report results in writing.

Retain one of three paragraphs below.

C. Testing Agency:  Owner will engage a qualified testing and inspecting agency to perform field tests and inspections and prepare test reports.

D. Testing Agency:  Engage a qualified testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

E. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with either of last two paragraphs above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

1. Perform each electrical test and visual and mechanical inspection, except optional tests, stated in NETA ATS.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3.9 ADJUSTING

This Article assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use; delete if adjustable devices are not used.

A. Set field-adjustable switches and circuit-breaker trip ranges.

3.10 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain variable frequency controllers.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 262923

VARIABLE-FREQUENCY MOTOR CONTROLLERS
262923 - 1

