Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
12/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 263600 - TRANSFER SWITCHES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes transfer switches rated 600 V and less, including the following:

1. Automatic transfer switches.

2. Bypass/isolation switches.

3. Nonautomatic transfer switches.

4. Remote annunciation systems.

5. Remote annunciation and control systems.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 21 Section "Electric-Drive, Centrifugal Fire Pumps" for automatic transfer switches for fire pumps.

2. Division 21 Section "Electric-Drive, Vertical-Turbine Fire Pumps" for automatic transfer switches for fire pumps.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include rated capacities, weights, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  Dimensioned plans, elevations, sections, and details showing minimum clearances, conductor entry provisions, gutter space, installed features and devices, and material lists for each switch specified.

Retain subparagraph below if retaining Part 2 "Bypass/Isolation Switches" Article.

1. Single-Line Diagram:  Show connections between transfer switch, bypass/isolation switch, power sources, and load; and show interlocking provisions for each combined transfer switch and bypass/isolation switch.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

C. Manufacturer Seismic Qualification Certification:  Submit certification that transfer switches accessories, and components will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For [manufacturer] [and] [testing agency].

Retain first paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For each type of product to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

1. Features and operating sequences, both automatic and manual.

2. List of all factory settings of relays; provide relay-setting and calibration instructions, including software, where applicable.

1.4 QUALITY ASSURANCE

A. Manufacturer Qualifications:  Maintain a service center capable of providing training, parts, and emergency maintenance repairs within a response period of less than eight hours from time of notification.

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and associated subparagraph below if Contractor selects testing agency.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

C. Source Limitations:  Obtain [automatic transfer switches] [bypass/isolation switches] [nonautomatic transfer switches] [remote annunciators] [and] [remote annunciator and control panels] through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NEMA ICS 1.

F. Comply with NFPA 70.

Retain one or both of first two paragraphs below if applicable to Project.

G. Comply with NFPA 99.

H. Comply with NFPA 110.

I. Comply with UL 1008 unless requirements of these Specifications are stricter.

1.5 PROJECT CONDITIONS

Retain this Article if interruption of existing electrical service is required.

A. Interruption of Existing Electrical Service:  Do not interrupt electrical service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of electrical service.

2. Do not proceed with interruption of electrical service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.6 COORDINATION

Retain this Article for floor-mounting equipment.

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Contactor Transfer Switches:

a. AC Data Systems, Inc.

b. Caterpillar; Engine Div.

c. Emerson; ASCO Power Technologies, LP.

d. Generac Power Systems, Inc.

e. GE Zenith Controls.

f. Kohler Power Systems; Generator Division.

g. Onan/Cummins Power Generation; Industrial Business Group.

h. Russelectric, Inc.

i. Spectrum Detroit Diesel.

j. <Insert manufacturer's name.>

2. Transfer Switches Using Molded-Case Switches or Circuit Breakers:

a. AC Data Systems, Inc.

b. Eaton Electrical Inc.; Cutler-Hammer.

c. GE Zenith Controls.

d. Hubbell Industrial Controls, Inc.

e. Lake Shore Electric Corporation.

f. <Insert manufacturer's name.>

2.2 GENERAL TRANSFER-SWITCH PRODUCT REQUIREMENTS

Coordinate paragraph below with Drawings and indicate percentage of tungsten filament lamp load for switches where it exceeds 30 percent.  This percentage may affect switch selection.  Some manufacturers' ratings for some switch lines apply to all classes of load, including tungsten lamps.

A. Indicated Current Ratings:  Apply as defined in UL 1008 for continuous loading and total system transfer, including tungsten filament lamp loads not exceeding 30 percent of switch ampere rating, unless otherwise indicated.

Indicate required ratings on Drawings.  See Editing Instruction No. 3 in the Evaluations.

B. Tested Fault-Current Closing and Withstand Ratings:  Adequate for duty imposed by protective devices at installation locations in Project under the fault conditions indicated, based on testing according to UL 1008.

Retain subparagraph below if this Section includes automatic transfer switches based on molded-case-switch or circuit-breaker products or if design includes fault-current protection internal to transfer switch.

1. Where transfer switch includes internal fault-current protection, rating of switch and trip unit combination shall exceed indicated fault-current value at installation location.

C. Solid-State Controls:  Repetitive accuracy of all settings shall be plus or minus 2 percent or better over an operating temperature range of minus 20 to plus 70 deg C.

D. Resistance to Damage by Voltage Transients:  Components shall meet or exceed voltage-surge withstand capability requirements when tested according to IEEE C62.41.  Components shall meet or exceed voltage-impulse withstand test of NEMA ICS 1.

E. Electrical Operation:  Accomplish by a nonfused, momentarily energized solenoid or electric-motor-operated mechanism, mechanically and electrically interlocked in both directions.

F. Switch Characteristics:  Designed for continuous-duty repetitive transfer of full-rated current between active power sources.

Delete first subparagraph below if units using switching components designed for molded-case switches or insulated-case circuit breakers are permissible.

1. Limitation:  Switches using molded-case switches or circuit breakers or insulated-case circuit-breaker components are not acceptable.

2. Switch Action:  Double throw; mechanically held in both directions.

3. Contacts:  Silver composition or silver alloy for load-current switching.  Conventional automatic transfer-switch units, rated 225 A and higher, shall have separate arcing contacts.

Retain paragraph below and select appropriate option if four-pole transfer switches are required.  See Editing Instruction No. 4 in the Evaluations.  Coordinate with Drawings.

G. Neutral Switching.  Where four-pole switches are indicated, provide [neutral pole switched simultaneously with phase poles] [overlapping neutral contacts].

Retain paragraph below for single-phase, three-wire systems or three-phase, four-wire systems without neutral switching.  Coordinate with Drawings.

H. Neutral Terminal:  Solid and fully rated, unless otherwise indicated.

Retain paragraph below if required for heavy nonlinear loads.  This requirement may result in some suppliers' oversizing certain switches to provide an oversize neutral.  Coordinate with Drawings.

I. Oversize Neutral:  Ampacity and switch rating of neutral path through units indicated for oversize neutral shall be double the nominal rating of circuit in which switch is installed.

Retain paragraph below if one or more switches are exposed to outdoor temperatures and humidity.  Coordinate with Drawings.

J. Heater:  Equip switches exposed to outdoor temperatures and humidity, and other units indicated, with an internal heater.  Provide thermostat within enclosure to control heater.

Retain paragraph and subparagraphs below if charger for generator starting batteries is to be located in transfer switch.  Select first option in first subparagraph for same generator units; consider second option for units 250 kW and larger.

K. Battery Charger:  For generator starting batteries.

1. Float type rated [2] [10] A.

2. Ammeter to display charging current.

3. Fused ac inputs and dc outputs.

Retain first paragraph below if required.  Coordinate with Drawings.

L. Annunciation, Control, and Programming Interface Components:  Devices at transfer switches for communicating with remote programming devices, annunciators, or annunciator and control panels shall have communication capability matched with remote device.

M. Factory Wiring:  Train and bundle factory wiring and label, consistent with Shop Drawings, either by color-code or by numbered or lettered wire and cable tape markers at terminations.  Color-coding and wire and cable tape markers are specified in Division 26 Section "Identification for Electrical Systems."

1. Designated Terminals:  Pressure type, suitable for types and sizes of field wiring indicated.

2. Power-Terminal Arrangement and Field-Wiring Space:  Suitable for top, side, or bottom entrance of feeder conductors as indicated.

3. Control Wiring:  Equipped with lugs suitable for connection to terminal strips.

Use NEMA 250, Type 12 enclosure if environment is generally dusty.

N. Enclosures:  General-purpose NEMA 250, Type [1] [3R] [12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

2.3 AUTOMATIC TRANSFER SWITCHES

A. Comply with Level 1 equipment according to NFPA 110.

B. Switching Arrangement:  Double-throw type, incapable of pauses or intermediate position stops during normal functioning, unless otherwise indicated.

Retain one of two paragraphs below.  First is optional feature with some manufacturers.

C. Manual Switch Operation:  Under load, with door closed and with either or both sources energized.  Transfer time is same as for electrical operation.  Control circuit automatically disconnects from electrical operator during manual operation.

D. Manual Switch Operation:  Unloaded.  Control circuit automatically disconnects from electrical operator during manual operation.

Retain paragraph below if required for control to minimize elevator disruption or for other purposes.

E. Signal-Before-Transfer Contacts:  A set of normally open/normally closed dry contacts operates in advance of retransfer to normal source.  Interval is adjustable from 1 to 30 seconds.

Retain paragraph below if digital communication system is used for remote annunciation or for remote annunciation and control.

F. Digital Communication Interface:  Matched to capability of remote annunciator or annunciator and control panel.

Retain paragraph below if transfer switches based on molded-case-switch or circuit-breaker components are acceptable for Project.

G. Transfer Switches Based on Molded-Case-Switch Components:  Comply with NEMA AB 1, UL 489, and UL 869A.

Retain paragraph and subparagraphs below for loads intolerant of interruptions or for switching large-motor loads.  Coordinate with remainder of this Article and with Drawings.  See Editing Instruction No. 5 in the Evaluations.

H. Automatic Closed-Transition Transfer Switches:  Include the following functions and characteristics:

1. Fully automatic make-before-break operation.

2. Load transfer without interruption, through momentary interconnection of both power sources not exceeding 100 ms.

3. Initiation of No-Interruption Transfer:  Controlled by in-phase monitor and sensors confirming both sources are present and acceptable.

a. Initiation occurs without active control of generator.

b. Controls ensure that closed-transition load transfer closure occurs only when the 2 sources are within plus or minus 5 electrical degrees maximum, and plus or minus 5 percent maximum voltage difference.

4. Failure of power source serving load initiates automatic break-before-make transfer.

Retain one of three paragraphs below to specify alternatives for switching large-motor loads.  Delete all if retaining "Automatic Closed-Transition Transfer Switches" Paragraph above for units serving large motors.  Indicate on Drawings which switches require these features.  See Editing Instruction No. 5 in the Evaluations.

I. In-Phase Monitor:  Factory-wired, internal relay controls transfer so it occurs only when the two sources are synchronized in phase.  Relay compares phase relationship and frequency difference between normal and emergency sources and initiates transfer when both sources are within 15 electrical degrees, and only if transfer can be completed within 60 electrical degrees.  Transfer is initiated only if both sources are within 2 Hz of nominal frequency and 70 percent or more of nominal voltage.

J. Motor Disconnect and Timing Relay:  Controls designate starters so they disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer.  Control connection to motor starters is through wiring external to automatic transfer switch.  Time delay for reconnecting individual motor loads is adjustable between 1 and 60 seconds, and settings are as indicated.  Relay contacts handling motor-control circuit inrush and seal currents are rated for actual currents to be encountered.

K. Programmed Neutral Switch Position:  Switch operator has a programmed neutral position arranged to provide a midpoint between the two working switch positions, with an intentional, time-controlled pause at midpoint during transfer.  Pause is adjustable from 0.5 to 30 seconds minimum and factory set for 0.5 second, unless otherwise indicated.  Time delay occurs for both transfer directions.  Pause is disabled unless both sources are live.

Edit paragraph and subparagraphs below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternate," if such terms are used elsewhere in the Construction Documents.

L. Automatic Transfer-Switch Features:

Revise pickup, dropout, and time-delay settings in first four subparagraphs below to suit application, and retain required features.

First subparagraph specifies three-phase undervoltage monitor.  Retain if loss of one phase of normal source would be a problem for loads downstream from transfer switch.  Similar option is available for emergency source.

1. Undervoltage Sensing for Each Phase of Normal Source:  Sense low phase-to-ground voltage on each phase.  Pickup voltage shall be adjustable from 85 to 100 percent of nominal, and dropout voltage is adjustable from 75 to 98 percent of pickup value.  Factory set for pickup at 90 percent and dropout at 85 percent.

2. Adjustable Time Delay:  For override of normal-source voltage sensing to delay transfer and engine start signals.  Adjustable from zero to six seconds, and factory set for one second.

3. Voltage/Frequency Lockout Relay:  Prevent premature transfer to generator.  Pickup voltage shall be adjustable from 85 to 100 percent of nominal.  Factory set for pickup at 90 percent.  Pickup frequency shall be adjustable from 90 to 100 percent of nominal.  Factory set for pickup at 95 percent.

4. Time Delay for Retransfer to Normal Source:  Adjustable from 0 to 30 minutes, and factory set for 10 minutes to automatically defeat delay on loss of voltage or sustained undervoltage of emergency source, provided normal supply has been restored.

5. Test Switch:  Simulate normal-source failure.

6. Switch-Position Pilot Lights:  Indicate source to which load is connected.

7. Source-Available Indicating Lights:  Supervise sources via transfer-switch normal- and emergency-source sensing circuits.

a. Normal Power Supervision:  Green light with nameplate engraved "Normal Source Available."

b. Emergency Power Supervision:  Red light with nameplate engraved "Emergency Source Available."

8. Unassigned Auxiliary Contacts:  Two normally open, single-pole, double-throw contacts for each switch position, rated 10 A at 240-V ac.

9. Transfer Override Switch:  Overrides automatic retransfer control so automatic transfer switch will remain connected to emergency power source regardless of condition of normal source.  Pilot light indicates override status.

Retain subparagraph below if needed to coordinate with engine generator.  Do not duplicate control features furnished with generator.  See Editing Instruction No. 6 in the Evaluations.

10. Engine Starting Contacts:  One isolated and normally closed, and one isolated and normally open; rated 10 A at 32-V dc minimum.

Retain one of first two subparagraphs below.

11. Engine Shutdown Contacts:  Instantaneous; shall initiate shutdown sequence at remote engine-generator controls after retransfer of load to normal source.

12. Engine Shutdown Contacts:  Time delay adjustable from zero to five minutes, and factory set for five minutes.  Contacts shall initiate shutdown at remote engine-generator controls after retransfer of load to normal source.

13. Engine-Generator Exerciser:  Solid-state, programmable-time switch starts engine generator and transfers load to it from normal source for a preset time, then retransfers and shuts down engine after a preset cool-down period.  Initiates exercise cycle at preset intervals adjustable from 7 to 30 days.  Running periods are adjustable from 10 to 30 minutes.  Factory settings are for 7-day exercise cycle, 20-minute running period, and 5-minute cool-down period.  Exerciser features include the following:

a. Exerciser Transfer Selector Switch:  Permits selection of exercise with and without load transfer.

b. Push-button programming control with digital display of settings.

c. Integral battery operation of time switch when normal control power is not available.

2.4 BYPASS/ISOLATION SWITCHES

A. Comply with requirements for Level 1 equipment according to NFPA 110.

B. Description:  Manual type, arranged to select and connect either source of power directly to load, isolating transfer switch from load and from both power sources.  Include the following features for each combined automatic transfer switch and bypass/isolation switch:

1. Means to lock bypass/isolation switch in the position that isolates transfer switch with an arrangement that permits complete electrical testing of transfer switch while isolated.  While isolated, interlocks prevent transfer-switch operation, except for testing or maintenance.

2. Drawout Arrangement for Transfer Switch:  Provide physical separation from live parts and accessibility for testing and maintenance operations.

3. Bypass/Isolation Switch Current, Voltage, Closing, and Short-Circuit Withstand Ratings:  Equal to or greater than those of associated automatic transfer switch, and with same phase arrangement and number of poles.

4. Contact temperatures of bypass/isolation switches shall not exceed those of automatic transfer-switch contacts when they are carrying rated load.

5. Operability:  Constructed so load bypass and transfer-switch isolation can be performed by 1 person in no more than 2 operations in 15 seconds or less.

6. Legend:  Manufacturer's standard legend for control labels and instruction signs shall describe operating instructions.

7. Maintainability:  Fabricate to allow convenient removal of major components from front without removing other parts or main power conductors.

C. Interconnection of Bypass/Isolation Switches with Automatic Transfer Switches:  Factory-installed copper bus bars; plated at connection points and braced for the indicated available short-circuit current.

2.5 NONAUTOMATIC TRANSFER SWITCHES

Retain one of first two paragraphs below for basic switch type.  First is less costly and complies with most manual transfer requirements.

A. Operation:  Electrically actuated by push buttons designated "Normal Source" and "Alternate Source."  Switch shall be capable of transferring load in either direction with either or both sources energized.

B. Operation:  Electrically actuated by push buttons designated "Normal Source" and "Alternate Source."  In addition, removable manual handle provides quick-make, quick-break manual-switching action.  Switch shall be capable of electrically or manually transferring load in either direction with either or both sources energized.  Control circuit disconnects from electrical operator during manual operation.

C. Double-Throw Switching Arrangement:  Incapable of pauses or intermediate position stops during switching sequence.

D. Nonautomatic Transfer-Switch Accessories:

1. Pilot Lights:  Indicate source to which load is connected.

2. Source-Available Indicating Lights:  Supervise sources via transfer-switch normal- and alternate-source sensing circuits.

a. Normal Power Supervision:  Green light with nameplate engraved "Normal Source Available."

b. Emergency Power Supervision:  Red light with nameplate engraved "Alternate Source Available."

3. Unassigned Auxiliary Contacts:  One set of normally closed contacts for each switch position, rated 10 A at 240-V ac.

Delete one or both of first two articles below.  Coordinate location of equipment and wiring with Drawings.  Coordinate with transfer-switch description and with Division 26 Section "Engine Generators."  Edit retained Article to specify required system features and functions.  See Editing Instruction No. 2 in the Evaluations.

2.6 REMOTE ANNUNCIATOR SYSTEM

A. Functional Description:  Remote annunciator panel shall annunciate conditions for indicated transfer switches.  Annunciation shall include the following:

1. Sources available, as defined by actual pickup and dropout settings of transfer-switch controls.

2. Switch position.

3. Switch in test mode.

4. Failure of communication link.

B. Annunciator Panel:  LED-lamp type with audible signal and silencing switch.

1. Indicating Lights:  Grouped for each transfer switch monitored.

2. Label each group, indicating transfer switch it monitors, location of switch, and identity of load it serves.

3. Mounting:  Flush, modular, steel cabinet, unless otherwise indicated.

4. Lamp Test:  Push-to-test or lamp-test switch on front panel.

2.7 REMOTE ANNUNCIATOR AND CONTROL SYSTEM

A. Functional Description:  Include the following functions for indicated transfer switches:

1. Indication of sources available, as defined by actual pickup and dropout settings of transfer-switch controls.

2. Indication of switch position.

3. Indication of switch in test mode.

4. Indication of failure of digital communication link.

5. Key-switch or user-code access to control functions of panel.

6. Control of switch-test initiation.

Delete one or both subparagraphs below.

7. Control of switch operation in either direction.

8. Control of time-delay bypass for transfer to normal source.

Retain first paragraph below with any combination of functions in subparagraphs above.

B. Malfunction of annunciator, annunciation and control panel, or communication link shall not affect functions of automatic transfer switch.  In the event of failure of communication link, automatic transfer switch automatically reverts to stand-alone, self-contained operation.  Automatic transfer-switch sensing, controlling, or operating function shall not depend on remote panel for proper operation.

C. Remote Annunciation and Control Panel:  Solid-state components.  Include the following features:

1. Controls and indicating lights grouped together for each transfer switch.

2. Label each indicating light control group.  Indicate transfer switch it controls, location of switch, and load it serves.

3. Digital Communication Capability:  Matched to that of transfer switches supervised.

Coordinate description in subparagraph below with floor plan representation and details on Drawings.

4. Mounting:  Flush, modular, steel cabinet, unless otherwise indicated.

2.8 SOURCE QUALITY CONTROL

A. Factory test and inspect components, assembled switches, and associated equipment.  Ensure proper operation.  Check transfer time and voltage, frequency, and time-delay settings for compliance with specified requirements.  Perform dielectric strength test complying with NEMA ICS 1.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain applicable mounting paragraphs in this Article.  Coordinate with Drawings.

Retain paragraph below if seismic controls are a project requirement.  Coordinate with Drawings.

A. Design each fastener and support to carry load indicated by seismic requirements and according to seismic-restraint details.  See Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

Retain paragraph below for floor-mounting switches and coordinate with Drawings.

B. Floor-Mounting Switch:  Anchor to floor by bolting.

Retain subparagraph below to require floor-mounting switches to be installed on concrete bases.  Coordinate with Drawings.

1. Concrete Bases:  4 inches (100 mm) high, reinforced, with chamfered edges.  Extend base no more than 4 inches (100 mm) in all directions beyond the maximum dimensions of switch, unless otherwise indicated or unless required for seismic support.  Construct concrete bases according to Division 26 Section "Hangers and Supports for Electrical Systems."

C. Annunciator and Control Panel Mounting:  Flush in wall, unless otherwise indicated.

D. Identify components according to Division 26 Section "Identification for Electrical Systems."

E. Set field-adjustable intervals and delays, relays, and engine exerciser clock.

3.2 CONNECTIONS

Retain first paragraph below if connections are to remote annunciator, control panel, or motor controller.  Coordinate with Drawings.

A. Wiring to Remote Components:  Match type and number of cables and conductors to control and communication requirements of transfer switches as recommended by manufacturer.  Increase raceway sizes at no additional cost to Owner if necessary to accommodate required wiring.

B. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

C. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain one of three paragraphs below.  If retaining first paragraph, retain first option if Owner engages agency; retain second option if Contractor engages agency.  If retaining second option, retain requirement for field quality-control test reports in Part 1 "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified independent testing and inspecting agency to perform tests and inspections and prepare test reports.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraphs below if Contractor performs tests and inspections.  Delete if retaining "Testing Agency" Paragraph above.

C. Perform tests and inspections and prepare test reports.

Retain first subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installation, including connections, and to assist in testing.

2. After installing equipment and after electrical circuitry has been energized, test for compliance with requirements.

3. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

4. Measure insulation resistance phase-to-phase and phase-to-ground with insulation-resistance tester.  Include external annunciation and control circuits.  Use test voltages and procedure recommended by manufacturer.  Comply with manufacturer's specified minimum resistance.

a. Check for electrical continuity of circuits and for short circuits.

b. Inspect for physical damage, proper installation and connection, and integrity of barriers, covers, and safety features.

c. Verify that manual transfer warnings are properly placed.

d. Perform manual transfer operation.

5. After energizing circuits, demonstrate interlocking sequence and operational function for each switch at least three times.

a. Simulate power failures of normal source to automatic transfer switches and of emergency source with normal source available.

Retain test in first subparagraph below if three-phase undervoltage sensing is specified in Part 2.  Test requires advance preparation by testing agency.

b. Simulate loss of phase-to-ground voltage for each phase of normal source.

c. Verify time-delay settings.

d. Verify pickup and dropout voltages by data readout or inspection of control settings.

e. Test bypass/isolation unit functional modes and related automatic transfer-switch operations.

Usually require test in first subparagraph below only for critical and extensive installations and for switches rated 1600 A and more in other installations.

f. Perform contact-resistance test across main contacts and correct values exceeding 500 microhms and values for 1 pole deviating by more than 50 percent from other poles.

g. Verify proper sequence and correct timing of automatic engine starting, transfer time delay, retransfer time delay on restoration of normal power, and engine cool-down and shutdown.

Retain subparagraph and associated subparagraph below if protective devices for circuits connected to transfer switches include ground-fault protection.

6. Ground-Fault Tests:  Coordinate with testing of ground-fault protective devices for power delivery from both sources.

a. Verify grounding connections and locations and ratings of sensors.

Retain paragraph and subparagraphs below if retaining "Testing Agency" Paragraph above.  Delete if Contractor performs tests and inspections.

D. Testing Agency's Tests and Inspections:

1. After installing equipment and after electrical circuitry has been energized, test for compliance with requirements.

2. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

3. Measure insulation resistance phase-to-phase and phase-to-ground with insulation-resistance tester.  Include external annunciation and control circuits.  Use test voltages and procedure recommended by manufacturer.  Comply with manufacturer's specified minimum resistance.

a. Check for electrical continuity of circuits and for short circuits.

b. Inspect for physical damage, proper installation and connection, and integrity of barriers, covers, and safety features.

c. Verify that manual transfer warnings are properly placed.

d. Perform manual transfer operation.

4. After energizing circuits, demonstrate interlocking sequence and operational function for each switch at least three times.

a. Simulate power failures of normal source to automatic transfer switches and of emergency source with normal source available.

Retain test in first subparagraph below if three-phase undervoltage sensing is specified in Part 2.  Test requires advance preparation by testing agency.

b. Simulate loss of phase-to-ground voltage for each phase of normal source.

c. Verify time-delay settings.

d. Verify pickup and dropout voltages by data readout or inspection of control settings.

e. Test bypass/isolation unit functional modes and related automatic transfer-switch operations.

Usually require test in first subparagraph below only for critical and extensive installations and for switches rated 1600 A and more in other installations.

f. Perform contact-resistance test across main contacts and correct values exceeding 500 microhms and values for 1 pole deviating by more than 50 percent from other poles.

g. Verify proper sequence and correct timing of automatic engine starting, transfer time delay, retransfer time delay on restoration of normal power, and engine cool-down and shutdown.

Retain subparagraph and associated subparagraph below if protective devices for circuits connected to transfer switches include ground-fault protection.

5. Ground-Fault Tests:  Coordinate with testing of ground-fault protective devices for power delivery from both sources.

a. Verify grounding connections and locations and ratings of sensors.

Observe reaction of circuit-interrupting devices when simulated fault current is applied at sensors.  Retain first paragraph below if automatic transfer switch is associated with generator.

E. Coordinate tests with tests of generator and run them concurrently.

F. Report results of tests and inspections in writing.  Record adjustable relay settings and measured insulation and contact resistances and time delays.  Attach a label or tag to each tested component indicating satisfactory completion of tests.

G. Remove and replace malfunctioning units and retest as specified above.

Edit paragraph and subparagraphs below to suit types of switches specified.

H. Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switch.  Remove all access panels so joints and connections are accessible to portable scanner.

1. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each switch 11 months after date of Substantial Completion.

2. Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

3. Record of Infrared Scanning:  Prepare a certified report that identifies switches checked and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain transfer switches and related equipment as specified below.  Refer to Division 01 Section "Demonstration and Training."

Retain paragraph below if generators are in Project.

B. Coordinate this training with that for generator equipment.

END OF SECTION 263600

	TRANSFER SWITCHES
	263600 - 1



