Copyright 2005 AIA
MASTERSPEC Full Length
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 270500 - COMMON WORK RESULTS FOR COMMUNICATIONS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Communications equipment coordination and installation.

2. Sleeves for pathways and cables.

3. Sleeve seals.

4. Grout.

5. Common communications installation requirements.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. EPDM:  Ethylene-propylene-diene terpolymer rubber.

B. NBR:  Acrylonitrile-butadiene rubber.

1.4 SUBMITTALS

A. Product Data:  For sleeve seals.

1.5 COORDINATION

A. Coordinate arrangement, mounting, and support of communications equipment:

1. To allow maximum possible headroom unless specific mounting heights that reduce headroom are indicated.

2. To provide for ease of disconnecting the equipment with minimum interference to other installations.

3. To allow right of way for piping and conduit installed at required slope.

4. So connecting pathways, cables, wireways, cable trays, and busways will be clear of obstructions and of the working and access space of other equipment.

B. Coordinate installation of required supporting devices and set sleeves in cast-in-place concrete, masonry walls, and other structural components as they are constructed.

C. Coordinate location of access panels and doors for communications items that are behind finished surfaces or otherwise concealed.  Access doors and panels are specified in Division 08 Section "Access Doors and Frames."

D. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 07 Section "Penetration Firestopping."."

PART 2 -  PRODUCTS

2.1 SLEEVES FOR PATHWAYS AND CABLES

Retain one of first two paragraphs below for penetrations through exterior walls above and below grade.

A. Steel Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.

B. Cast-Iron Pipe Sleeves:  Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.

C. Sleeves for Rectangular Openings:  Galvanized sheet steel.

1. Minimum Metal Thickness:

a. For sleeve cross-section rectangle perimeter less than 50 inches (1270 mm) and no side more than 16 inches (400 mm), thickness shall be 0.052 inch (1.3 mm).

b. For sleeve cross-section rectangle perimeter equal to, or more than, 50 inches (1270 mm) and 1 or more sides equal to, or more than, 16 inches (400 mm), thickness shall be 0.138 inch (3.5 mm).

2.2 SLEEVE SEALS

Retain this article if annular space between pipe sleeves and pathways or cables must be sealed against hydrostatic pressure.  Sleeve seals are usually furnished with EPDM sealing elements, plastic pressure plates, and carbon-steel bolts.  NBR and silicone sealing elements, carbon- and stainless-steel pressure plates, and stainless-steel bolts are available for special applications.

A. Description:  Modular sealing device, designed for field assembly, to fill annular space between sleeve and pathway or cable.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Advance Products & Systems, Inc.

b. Calpico, Inc.

c. Metraflex Co.

d. Pipeline Seal and Insulator, Inc.

e. <Insert manufacturer's name.>

3. Sealing Elements:  [EPDM] [NBR] <Insert other> interlocking links shaped to fit surface of cable or conduit.  Include type and number required for material and size of pathway or cable.

4. Pressure Plates:  [Plastic] [Carbon steel] [Stainless steel].  Include two for each sealing element.

5. Connecting Bolts and Nuts:  [Carbon steel with corrosion-resistant coating] [Stainless steel] of length required to secure pressure plates to sealing elements.  Include one for each sealing element.

2.3 GROUT

A. Nonmetallic, Shrinkage-Resistant Grout:  ASTM C 1107, factory-packaged, nonmetallic aggregate grout, noncorrosive, nonstaining, mixed with water to consistency suitable for application and a 30-minute working time.

PART 3 -  EXECUTION

3.1 COMMON REQUIREMENTS FOR COMMUNICATIONS INSTALLATION

A. Comply with NECA 1.

B. Measure indicated mounting heights to bottom of unit for suspended items and to center of unit for wall-mounting items.

C. Headroom Maintenance:  If mounting heights or other location criteria are not indicated, arrange and install components and equipment to provide maximum possible headroom consistent with these requirements.

D. Equipment:  Install to facilitate service, maintenance, and repair or replacement of components of both communications equipment and other nearby installations.  Connect in such a way as to facilitate future disconnecting with minimum interference with other items in the vicinity.

E. Right of Way:  Give to piping systems installed at a required slope.

3.2 SLEEVE INSTALLATION FOR COMMUNICATIONS PENETRATIONS

A. Communications penetrations occur when pathways, cables, wireways, or cable trays penetrate concrete slabs, concrete or masonry walls, or fire-rated floor and wall assemblies.

B. Concrete Slabs and Walls:  Install sleeves for penetrations unless core-drilled holes or formed openings are used.  Install sleeves during erection of slabs and walls.

C. Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.

D. Fire-Rated Assemblies:  Install sleeves for penetrations of fire-rated floor and wall assemblies unless openings compatible with firestop system used are fabricated during construction of floor or wall.

E. Cut sleeves to length for mounting flush with both surfaces of walls.

F. Extend sleeves installed in floors [2 inches (50 mm)] <Insert dimension> above finished floor level.

G. Size pipe sleeves to provide [1/4-inch (6.4-mm)] <Insert dimension> annular clear space between sleeve and pathway or cable, unless indicated otherwise.

H. Seal space outside of sleeves with grout for penetrations of concrete and masonry

1. Promptly pack grout solidly between sleeve and wall so no voids remain.  Tool exposed surfaces smooth; protect grout while curing.

I. Interior Penetrations of Non-Fire-Rated Walls and Floors:  Seal annular space between sleeve and pathway or cable, using joint sealant appropriate for size, depth, and location of joint.  Comply with requirements in Division 07 Section "Joint Sealants.".

J. Fire-Rated-Assembly Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at pathway and cable penetrations.  Install sleeves and seal pathway and cable penetration sleeves with firestop materials.  Comply with requirements in Division 07 Section "Penetration Firestopping."

K. Roof-Penetration Sleeves:  Seal penetration of individual pathways and cables with flexible boot-type flashing units applied in coordination with roofing work.

L. Aboveground, Exterior-Wall Penetrations:  Seal penetrations using [steel] [cast-iron] pipe sleeves and mechanical sleeve seals.  Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

M. Underground, Exterior-Wall Penetrations:  Install cast-iron pipe sleeves.  Size sleeves to allow for 1-inch (25-mm) annular clear space between pathway or cable and sleeve for installing mechanical sleeve seals.

3.3 SLEEVE-SEAL INSTALLATION

A. Install to seal exterior wall penetrations.

B. Use type and number of sealing elements recommended by manufacturer for pathway or cable material and size.  Position pathway or cable in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between pathway or cable and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

3.4 FIRESTOPPING

A. Apply firestopping to penetrations of fire-rated floor and wall assemblies for communications installations to restore original fire-resistance rating of assembly.  Firestopping materials and installation requirements are specified in Division 07 Section "Penetration Firestopping."

END OF SECTION 270500

	COMMON WORK RESULTS FOR COMMUNICATIONS
	270500 - 1



