Copyright 2001 and 2005 AIA
MASTERSPEC Full Length
12/01 (R 03/06)

Copyright 2001 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 334100 - STORM UTILITY DRAINAGE PIPING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes gravity-flow, nonpressure[ and force-main, pressure] storm drainage outside the building, with the following components:

Adjust list below to suit Project.

1. Special fittings for expansion and deflection.

2. Backwater valves.

3. Cleanouts.

4. Drains.

5. Corrosion-protection piping encasement.

6. [Precast concrete] [Cast-in-place concrete] [Fiberglass] manholes.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. EPDM:  Ethylene-propylene-diene-monomer rubber.

C. FRP:  Fiberglass-reinforced plastic.

D. LLDPE:  Linear low-density, polyethylene plastic.

E. PE:  Polyethylene plastic.

F. PP:  Polypropylene plastic.

G. PVC:  Polyvinyl chloride plastic.

H. RTRF:  Glass-fiber-reinforced, thermosetting-resin fitting.

I. RTRP:  Glass-fiber-reinforced, thermosetting-resin pipe.

J. TPE:  Thermoplastic elastomer.

1.4 PERFORMANCE REQUIREMENTS

A. Gravity-Flow, Nonpressure, Drainage-Piping Pressure Rating:  [10-foot head of water (30 kPa)] <Insert other>.  Pipe joints shall be at least silttight, unless otherwise indicated.

B. Force-Main, Pressure-Piping Pressure Rating:  At least equal to system operating pressure but not less than [50 psig (345 kPa)] [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert other>.

1.5 SUBMITTALS

A. Product Data:  For the following:

1. Special pipe fittings.

2. Backwater valves.

3. Drains.

4. Channel drainage systems.

5. Storage and leaching chambers.

B. Shop Drawings:  For the following:

1. Manholes:  Include plans, elevations, sections, details, and frames and covers.[ Include design calculations, and concrete design-mix report for cast-in-place manholes.]

2. [Catch Basins] [Catch Basins and Stormwater Inlets] [Stormwater Inlets].  Include plans, elevations, sections, details, and frames, covers, and grates.

3. Stormwater Detention Structures:  Include plans, elevations, sections, details, frames and covers, design calculations, and concrete design-mix report.

Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Show pipe sizes, locations, and elevations.  Show other piping in same trench and clearances from storm drainage system piping.  Indicate interface and spatial relationship between manholes, piping, and proximate structures.

Retain paragraph below if profiles are not shown on Drawings.

D. Profile Drawings:  Show system piping in elevation.  Draw profiles at horizontal scale of not less than 1 inch equals 50 feet (1:500) and vertical scale of not less than 1 inch equals 5 feet (1:50).  Indicate manholes and piping.  Show types, sizes, materials, and elevations of other utilities crossing system piping.

Retain paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Do not store plastic manholes, pipe, and fittings in direct sunlight.

B. Protect pipe, pipe fittings, and seals from dirt and damage.

Delete first paragraph below if only cast-in-place manholes are specified.

C. Handle manholes according to manufacturer's written rigging instructions.

D. Handle [catch basins] [catch basins and stormwater inlets] [stormwater inlets] according to manufacturer's written rigging instructions.

1.7 PROJECT CONDITIONS

Delete this Article if no interruption of existing storm drainage service is required.

A. Interruption of Existing Storm Drainage Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of service.

2. Do not proceed with interruption of service without [Architect's] [Construction Manager's] [Owner's] written permission.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 PIPING MATERIALS

See "Writing Guide" Article in Evaluations for a discussion of this Section's organization and the most efficient way to edit this Section.

A. Refer to Part 3 "Piping Applications" Article for applications of pipe, fitting, and joining materials.

2.3 HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS

Pipe and fittings in this Article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

A. Pipe and Fittings:  ASTM A 74, [Service class] [Service and Extra-Heavy classes] [Extra-Heavy class].

B. Gaskets:  ASTM C 564, rubber.

C. Calking Materials:  ASTM B 29, pure lead and oakum or hemp fiber.

2.4 HUBLESS CAST-IRON SOIL PIPE AND FITTINGS

Pipe, fittings, and couplings in this Article are available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

A. Pipe and Fittings:  ASTM A 888 or CISPI 301.

B. Shielded Couplings:  ASTM C 1277 assembly of metal shield or housing, corrosion-resistant fasteners, and rubber sleeve with integral, center pipe stop.

Couplings in paragraph and subparagraphs below are economical.  They may not be suitable for installation in corrosive soil.

C. Shielded, Stainless-Steel Couplings:  CISPI 310, with ASTM A 666, Type 301, stainless-steel corrugated shield; stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. Dallas Specialty & Mfg. Co.

c. Fernco Inc.

d. Ideal Div.; Stant Corp.

e. Mission Rubber Company; a division of MCP Industries, Inc.

f. Tyler Pipe; Soil Pipe Div.

g. <Insert manufacturer's name.>

2. Couplings for NPS 1-1/2 to NPS 4 (DN 40 to DN 100):  2-1/8-inch- (54-mm-) wide shield with 2 bands.

3. Couplings for NPS 5 and NPS 6 (DN 125 and DN 150):  3-inch- (76-mm-) wide shield with 4 bands.

4. Couplings for NPS 8 and NPS 10 (DN 200 and DN 250):  4-inch- (102-mm-) wide shield with 4 bands.

Couplings in first two paragraphs and associated subparagraphs below cover various configurations of manufacturers' nonstandard, "heavy-duty" shielded, stainless-steel couplings.  There is a new standard being developed for these couplings and this description (including dimensions) will comply.

D. Heavy-Duty, Shielded, Stainless-Steel Couplings, NPS 10 (DN 250) and Smaller:  With ASTM A 666, Type 301 or Type 304, stainless-steel shield; 2 or more stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. Clamp-All Corp.

c. Dallas Specialty & Mfg. Co.

d. Ideal Div.; Stant Corp.

e. Mission Rubber Company; a division of MCP Industries, Inc.

f. Tyler Pipe; Soil Pipe Div.

g. <Insert manufacturer's name.>

2. Couplings for NPS 1-1/2 to NPS 4 (DN 40 to DN 100):  3 inches (76 mm).

3. Couplings for NPS 5 to NPS 10 (DN 125 to DN 250):  4 inches (102 mm).

E. Heavy-Duty, Shielded, Stainless-Steel Couplings, NPS 12 and NPS 15 (DN 300 and DN 375):  With ASTM A 666, Type 301 or Type 304, stainless-steel shield; stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. Ideal Div.; Stant Corp.

c. Mission Rubber Company; a division of MCP Industries, Inc.

d. Tyler Pipe; Soil Pipe Div.

e. <Insert manufacturer's name.>

2. Couplings:  5-1/2-inch- (140-mm-) wide shield with 6 bands.

F. Heavy-Duty, Cast-Iron Couplings:  ASTM A 48, two-piece, cast-iron housing; stainless-steel bolts and nuts; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. MG Piping Products Co.

b. <Insert manufacturer's name.>

2. Couplings for NPS 1-1/2 to NPS 4 (DN 40 to DN 100):  2-1/8-inch- (54-mm-) wide housing with 2 bolts.

3. Couplings for NPS 5 and NPS 6 (DN 125 and DN 150):  3-1/8-inch- (80-mm-) wide housing with 4 bolts.

4. Couplings for NPS 8 and NPS 10 (DN 200 and DN 250):  4-inch- (102-mm-) wide housing with 4 bolts.

Coupling in paragraph below should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

G. Unshielded Couplings:  ASTM C 1461, rigid, sleeve-type, reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. <Insert manufacturer's name.>

2. Couplings for NPS 1-1/2 to NPS 4 (DN 40 to DN 100):  Sleeve with two bands.

2.5 DUCTILE-IRON CULVERT PIPE AND FITTINGS

Pipe in paragraph below should be available in NPS 14 to NPS 64 (DN 350 to DN 1600).  Joints are gasket type.

A. Pipe:  ASTM A 716, for push-on joints.

Fittings in paragraph below should be available in NPS 3 to NPS 48 (DN 80 to DN 1200).

B. Standard Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

Fittings in first paragraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600) and NPS 54 to NPS 64 (DN 1350 to DN 1600).

C. Compact Fittings:  AWWA C153, for push-on joints.

D. Gaskets:  AWWA C111, rubber.

2.6 DUCTILE-IRON PRESSURE PIPE AND FITTINGS

Piping materials in this Article should be available in NPS 3 to NPS 30 (DN 80 to DN 750).  Joints are gasket type.

A. Pipe:  AWWA C151, for push-on joints.

Fittings in paragraph below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

B. Standard Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

Fittings in first paragraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600) and NPS 54 to NPS 64 (DN 1350 to DN 1600).

C. Compact Fittings:  AWWA C153, for push-on joints.

D. Gaskets:  AWWA C111, rubber.

2.7 STEEL PIPE AND FITTINGS

Piping material in this Article is available in NPS 4 to NPS 144 (DN 100 to DN 3600).  Standard joints with bands are soiltight.  Special joints with bands and O-rings are silttight.

A. Corrugated-Steel Pipe and Fittings:  ASTM A 760/A 760M, Type I with fittings of similar form and construction as pipe.

1. Special-Joint Bands:  Corrugated steel with O-ring seals.

2. Standard-Joint Bands:  Corrugated steel.

3. Coating:  [Aluminum] [Zinc].

2.8 ALUMINUM PIPE AND FITTINGS

Piping material in this Article is available in NPS 4 to NPS 120 (DN 100 to DN 3000).  Standard joints with bands are soiltight.  Special joints with bands and O-rings are silttight.

A. Corrugated Aluminum Pipe and Fittings:  ASTM B 745/B 745M, Type I with fittings of similar form and construction as pipe.

1. Special-Joint Bands:  Corrugated steel with O-ring seals.

2. Standard-Joint Bands:  Corrugated steel.

2.9 ABS PIPE AND FITTINGS

Piping material in this Article should be available in 3 SDRs and in NPS 3 to NPS 12 (DN 80 to DN 300).  Verify availability.  Joints are solvent-cemented and gasket types.

A. ABS Sewer Pipe and Fittings:  ASTM D 2751, with bell-and-spigot ends for gasketed joints.

1. NPS 3 to NPS 6 (DN 80 to DN 150):  SDR 35.

2. NPS 8 to NPS 12 (DN 200 to DN 300):  SDR 42.

3. Gaskets:  ASTM F 477, elastomeric seals.

2.10 PE PIPE AND FITTINGS

Piping in paragraph below is available in NPS 3 to NPS 10 (DN 80 to DN 250).  Joints are coupling type.

A. Corrugated PE Drainage Pipe and Fittings NPS 10 (DN 250) and Smaller:  AASHTO M 252M, Type S, with smooth waterway for coupling joints.

Joints made using couplings in subparagraph below are silttight.

1. Silttight Couplings:  PE sleeve with ASTM D 1056, Type 2, Class A, Grade 2 gasket material that mates with tube and fittings.

Joints made using couplings in subparagraph below are soiltight.

2. Soiltight Couplings:  AASHTO M 252M, corrugated, matching tube and fittings.

Piping in subparagraph below is available in NPS 12 to NPS 48 (DN 300 to DN 1200).  Joints are coupling type.

3. Corrugated PE Pipe and Fittings NPS 12 to NPS 48 (DN 250 to DN 1200):  AASHTO M 294M, Type S, with smooth waterway for coupling joints.

Joints made using couplings in subparagraph below are silttight.

4. Silttight Couplings:  PE sleeve with ASTM D 1056, Type 2, Class A, Grade 2 gasket material that mates with pipe and fittings.

Joints made using couplings in subparagraph below are soiltight.

5. Soiltight Couplings:  AASHTO M 294M, corrugated, matching pipe and fittings.

Piping in paragraph below is available in NPS 12 to NPS 48 (DN 300 to DN 1200).  Joints are coupling type.

B. Corrugated PE Pipe and Fittings NPS 56 and NPS 60 (DN 1400 and DN 1524):  AASHTO MP7, Type S, with smooth waterway for coupling joints.

Joints made using couplings in subparagraph below are silttight.

1. Silttight Couplings:  PE sleeve with ASTM D 1056, Type 2, Class A, Grade 2 gasket material that mates with pipe and fittings.

Joints made using couplings in subparagraph below are soiltight.

2. Soiltight Couplings:  AASHTO MP7, corrugated, matching pipe and fittings.

2.11 PVC PIPE AND FITTINGS

Pipe in paragraph below is available in NPS 4 to NPS 12 (DN 100 to DN 300).  Joints are gasket type.

A. PVC Pressure Pipe:  AWWA C900, Class [100] [150] [200], for gasketed joints and using ASTM F 477, elastomeric seals.

1. Fittings NPS 4 to NPS 8 (DN 100 to DN 200):  PVC pressure fittings complying with AWWA C907, for gasketed joints and using ASTM F 477, elastomeric seals.

Ductile-iron fittings in subparagraph below mate with PVC pressure pipe and are available in NPS 3 to NPS 24 (DN 80 to DN 600).  Joints are gasket type.

2. Fittings NPS 10 (DN 250) and Larger:  Ductile-iron, compact fittings complying with AWWA C153, for push-on joints and using AWWA C111, rubber gaskets.

Piping in paragraph below is available in NPS 1/8 to NPS 24 (DN 6 to DN 600).  Joints are solvent-cemented type.

B. PVC Water-Service Pipe and Fittings:  ASTM D 1785, Schedule [40] [80] pipe, with plain ends for solvent-cemented joints with [ASTM D 2466, Schedule 40] [ASTM D 2467, Schedule 80], socket-type fittings.

Piping in paragraph below is available in NPS 1-1/2 to NPS 12 (DN 40 to DN 300).  Joints are solvent-cemented type.

C. PVC Cellular-Core Pipe and Fittings:  ASTM F 891, Sewer and Drain Series, PS 50 minimum stiffness pipe with ASTM D 3034, [SDR 35] <Insert other>, socket-type fittings for solvent-cemented joints.

Piping in paragraph below is available in 4 SDRs and in NPS 4 to NPS 15 (DN 100 to DN 375).  Joints are solvent-cemented and gasket types.

D. PVC Sewer Pipe and Fittings, NPS 15 (DN 375) and Smaller:  ASTM D 3034, [SDR 35] <Insert other>, with bell-and-spigot ends for gasketed joints with ASTM F 477, elastomeric seals.

Piping in paragraph below is available in 2 thicknesses and in NPS 18 to NPS 36 (DN 450 to DN 900).  Joints are gasket type.

E. PVC Sewer Pipe and Fittings, NPS 18 (DN 450) and Larger:  ASTM F 679, T-[1] [2] wall thickness, with bell-and-spigot ends for gasketed joints with ASTM F 477, elastomeric seals.

Piping in paragraph below is available in at least NPS 8 to NPS 30 (DN 200 to DN 750).  Standard includes NPS 4 to NPS 48 (DN 100 to DN 1200), but availability in all sizes is uncertain.  Joints are gasket type and are watertight.

F. PVC Profile Gravity Sewer Pipe and Fittings:  ASTM F 794 pipe, with bell-and-spigot ends; ASTM D 3034 fittings, with bell ends; and ASTM F 477, elastomeric seals.

2.12 FIBERGLASS PIPE AND FITTINGS

Piping in first paragraph below is available in NPS 8 to NPS 144 (DN 200 to DN 3600).  Joints are gasket type.

A. Fiberglass Sewer Pipe:  ASTM D 3262, RTRP for gasketed joints fabricated with Type [2, polyester] [2, polyester or Type 4, epoxy] [ 4, epoxy] resin.

1. Liner:  [1, reinforced thermoset] [2, nonreinforced thermoset] [3, thermoplastic] [4, no liner].

2. Grade:  [Reinforced, surface layer matching pipe resin] [Nonreinforced, surface layer matching pipe resin] [No surface layer] <Insert other>.

3. Stiffness:  [A, 9 psig (62 kPa)] [B, 18 psig (124 kPa)] [C, 36 psig (248 kPa)] [D, 72 psig (496 kPa)].

B. Fiberglass Nonpressure Fittings:  ASTM D 3840, RTRF for gasketed joints.

1. Laminating Resin:  Type [1, polyester] [1, polyester or Type 2, epoxy] [2, epoxy] resin.

2. Reinforcement:  Grade with finish compatible with resin.

C. Gaskets:  ASTM F 477, elastomeric seals.

2.13 CONCRETE PIPE AND FITTINGS

Concrete pipe in this Article is available in many variations of class and wall thickness.  Review the applicable standard before making selection.

Piping in paragraph below is available in 3 classes and in NPS 4 to NPS 36 (DN 100 to DN 900).  Joints are gasket type.

A. Nonreinforced-Concrete Sewer Pipe and Fittings:  ASTM C 14 (ASTM C 14M), Class [1] [2] [3], with [bell-and-spigot] [or] [groove and tongue] ends and [gasketed joints with ASTM C 443 (ASTM C 443M), rubber gaskets] [sealant joints with ASTM C 990 (ASTM C 990M), bitumen or butyl-rubber sealant].

Piping in paragraph below is available in 5 classes and 3 wall thicknesses, and in NPS 12 to NPS 144 (DN 300 to DN 3600).  Not all classes and wall thicknesses are available.  Joints are gasket type.

B. Reinforced-Concrete Sewer Pipe and Fittings:  ASTM C 76 (ASTM C 76M), with [bell-and-spigot] [or] [groove and tongue] ends and [gasketed joints with ASTM C 443 (ASTM C 443M), rubber gaskets] [sealant joints with ASTM C 990 (ASTM C 990M), bitumen or butyl-rubber sealant].

Retain subparagraph below only for NPS 60 to NPS 144 (DN 1500 to DN 3600).

1. Class I, Wall [A] [B].

Retain one of four subparagraphs below for NPS 12 to NPS 144 (DN 300 to DN 3600).

2. Class II, Wall [A] [B] [C].

3. Class III, Wall [A] [B] [C].

4. Class IV, Wall [A] [B] [C].

5. Class V, Wall [B] [C].

2.14 NONPRESSURE-TYPE PIPE COUPLINGS

A. Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping.  Include ends of same sizes as piping to be joined, and corrosion-resistant-metal tension band and tightening mechanism on each end.

B. Sleeve Materials:

1. For Concrete Pipes:  ASTM C 443 (ASTM C 443M), rubber.

2. For Cast-Iron Soil Pipes:  ASTM C 564, rubber.

3. For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

4. For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

C. Unshielded Flexible Couplings:  Elastomeric sleeve with[ stainless-steel shear ring and] corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Dallas Specialty & Mfg. Co.

b. Fernco Inc.

c. Logan Clay Products Company (The).

d. Mission Rubber Company; a division of MCP Industries, Inc.

e. NDS Inc.

f. Plastic Oddities, Inc.

g. <Insert manufacturer's name.>

D. Shielded Flexible Couplings:  ASTM C 1460, elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Cascade Waterworks Mfg.

b. Dallas Specialty & Mfg. Co.

c. Mission Rubber Company; a division of MCP Industries, Inc.

d. <Insert manufacturer's name.>

E. Ring-Type Flexible Couplings:  Elastomeric compression seal with dimensions to fit inside bell of larger pipe and for spigot of smaller pipe to fit inside ring.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Fernco Inc.

b. Logan Clay Products Company (The).

c. Mission Rubber Company; a division of MCP Industries, Inc.

d. <Insert manufacturer's name.>

Coupling in paragraph below should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

F. Nonpressure-Type Rigid Couplings:  ASTM C 1461, sleeve-type reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ANACO.

b. <Insert manufacturer's name.>

2.15 PRESSURE-TYPE PIPE COUPLINGS

A. Reducing or transition, metal, bolted, sleeve-type, reducing or transition coupling, for joining underground pressure piping.  Include [150-psig (1035-kPa)] [200-psig (1380-kPa)] <Insert other> minimum pressure rating and ends of same sizes as piping to be joined.

B. Tubular-Sleeve Couplings:  AWWA C219, with center sleeve, gaskets, end rings, and bolt fasteners.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Cascade Waterworks Mfg.

b. Dresser, Inc.; DMD Div.

c. Ford Meter Box Company, Inc. (The); Pipe Products Div.

d. JCM Industries.

e. Romac Industries, Inc.

f. Smith-Blair, Inc.

g. Viking Johnson.

h. <Insert manufacturer's name.>

2. Center-Sleeve Material:  [Manufacturer's standard] [Carbon steel] [Stainless steel] [Ductile iron] [Malleable iron].

3. Gasket Material:  Natural or synthetic rubber.

4. Metal Component Finish:  Corrosion-resistant coating or material.

C. Split-Sleeve Couplings:  With split sleeve with sealing pad and closure plates, O-ring gaskets, and bolt fasteners.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Brico Industries.

b. <Insert manufacturer's name.>

2. Sleeve Material:  [Manufacturer's standard] [Carbon steel] [Stainless steel].

3. Sleeve Dimensions:  Of thickness and width required to provide pressure rating.

4. Gasket Material:  O-rings made of EPDM rubber, unless otherwise indicated.

5. Metal Component Finish:  Corrosion-resistant coating or material.

2.16 SPECIAL PIPE FITTINGS

Special pipe fittings in this Article are for buried, ductile-iron pressure pipe and other pipe with same diameters.

Expansion joints in paragraph below provide both offset and expansion.  Indicate minimum required offset and expansion data on Drawings.

A. Ductile-Iron Flexible Expansion Joints:  Compound fitting with combination of flanged and mechanical-joint ends complying with AWWA C110 or AWWA C153.  Include 2 gasketed ball-joint sections and 1 or more gasketed sleeve sections, rated for 250-psig (1725-kPa) minimum working pressure and for offset and expansion indicated.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. EBAA Iron Sales, Inc.

b. Romac Industries, Inc.

c. Star Pipe Products.

d. <Insert manufacturer's name.>

Fittings in paragraph below provide deflection only.

B. Ductile-Iron Deflection Fittings:  Compound coupling fitting with ball joint, flexing section, gaskets, and restrained-joint ends complying with AWWA C110 or AWWA C153.  Include rating for 250-psig (1725-kPa) minimum working pressure and for up to 15 degrees of deflection.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. EBAA Iron Sales, Inc.

b. <Insert manufacturer's name.>

Expansion joints in paragraph below provide linear expansion only.

C. Ductile-Iron Expansion Joints:  Three-piece assembly of telescoping sleeve with gaskets and restrained-type, ductile-iron[ or steel with protective coating], bell-and-spigot end sections complying with AWWA C110 or AWWA C153.  Include rating for 250-psig (1725-kPa) minimum working pressure and for expansion indicated.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Dresser, Inc.; DMD Div.

b. EBAA Iron Sales, Inc.

c. JCM Industries.

d. Smith-Blair, Inc.

e. <Insert manufacturer's name.>

2.17 BACKWATER VALVES

A. Gray-Iron Backwater Valves:  ASME A112.14.1, gray-iron body and bolted cover, with bronze seat.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Josam Company.

b. Smith, Jay R. Mfg. Co.

c. Wade Div.; Tyler Pipe.

d. Watts Industries, Inc.

e. Watts Industries, Inc.; Enpoco, Inc. Div.

f. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

g. <Insert manufacturer's name.>

2. Horizontal Type:  With swing check valve and hub-and-spigot ends.

3. Combination Horizontal and Manual Gate-Valve Type:  With swing check valve, integral gate valve, and hub-and-spigot ends.

4. Terminal Type:  With bronze seat, swing check valve, and hub inlet.

B. PVC Backwater Valves:  Horizontal type; with PVC body, PVC removable cover, and PVC swing check valve.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Canplas Inc.

b. IPS Corporation.

c. NDS Inc.

d. Plastic Oddities, Inc.

e. Sioux Chief Manufacturing Company, Inc.

f. Zurn Industries, Inc.; Zurn Light Commercial Specialty Plumbing Products.

g. <Insert manufacturer's name.>

2.18 CLEANOUTS

A. Gray-Iron Cleanouts:  ASME A112.36.2M, round, gray-iron housing with clamping device and round, secured, scoriated, gray-iron cover.  Include gray-iron ferrule with inside calk or spigot connection and countersunk, tapered-thread, brass closure plug.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Josam Company.

b. MIFAB Manufacturing, Inc.

c. Smith, Jay R. Mfg. Co.

d. Wade Div.; Tyler Pipe.

e. Watts Industries, Inc.

f. Watts Industries, Inc.; Enpoco, Inc. Div.

g. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

h. <Insert manufacturer's name.>

2. Top-Loading Classification(s):  [Light] [Medium] [Heavy] [and] [Extra-heavy] duty.

3. Sewer Pipe Fitting and Riser to Cleanout:  ASTM A 74, Service class, cast-iron soil pipe and fittings.

B. PVC Cleanouts:  PVC body with PVC threaded plug.  Include PVC sewer pipe fitting and riser to cleanout of same material as sewer piping.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Canplas Inc.

b. IPS Corporation.

c. NDS Inc.

d. Plastic Oddities, Inc.

e. Sioux Chief Manufacturing Company, Inc.

f. Zurn Industries, Inc.; Zurn Light Commercial Specialty Plumbing Products.

g. <Insert manufacturer's name.>

2.19 DRAINS

A. Gray-Iron Area Drains:  ASME A112.21.1M, round body with anchor flange and round[ secured] grate.  Include bottom outlet with inside calk or spigot connection, of sizes indicated.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Josam Company.

b. MIFAB Manufacturing, Inc.

c. Smith, Jay R. Mfg. Co.

d. Wade Div.; Tyler Pipe.

e. Watts Industries, Inc.

f. Watts Industries, Inc.; Enpoco, Inc. Div.

g. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

h. <Insert manufacturer's name.>

2. Top-Loading Classification(s):  [Medium] [Medium and heavy] [Heavy] duty.

B. Gray-Iron Trench Drains:  ASME A112.21.1M, 6-inch- (150-mm-) wide top surface, rectangular body with anchor flange or other anchoring device, and rectangular[ secured] grate.  Include units of total length indicated and number of bottom outlets with inside calk or spigot connections, of sizes indicated.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Josam Company.

b. Smith, Jay R. Mfg. Co.

c. Wade Div.; Tyler Pipe.

d. Watts Industries, Inc.

e. Watts Industries, Inc.; Enpoco, Inc. Div.

f. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

g. <Insert manufacturer's name.>

2. Top-Loading Classification(s):  [Medium] [Heavy] [Extra-heavy] [Medium and heavy] [Medium and extra-heavy] [Heavy and extra-heavy] [Medium, heavy, and extra-heavy] duty.

C. Steel Trench Drains:  Factory fabricated from ASTM A 242/A 242M, welded steel plate to form rectangular body with uniform bottom slope of 2 percent down toward outlet, anchor flange, and grate.  Include units of total length indicated, bottom outlet of size indicated, outlet strainer, acid-resistant enamel coating on inside and outside surfaces, and grate with openings of total free area at least two times cross-sectional area of outlet.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Rockford Sanitary Systems, Inc.

b. <Insert manufacturer's name.>

2. Plate Thickness(es):  [1/8 inch (3.2 mm)] [1/8 inch (3.2 mm) and 1/4 inch (6.4 mm)] [1/4 inch (6.4 mm)].

3. Overall Width(s):  [7-1/2 inches (190 mm)] [7-1/2 inches (190 mm) and 12-1/3 inches (313 mm)] [12-1/3 inches (313 mm)].

a. Grate Openings:  [1/4 inch (6.4 mm) circular] [3/8 inch (9.5 mm) circular] [3/8 inch (9.5 mm) circular or 3/8-by-3-inch (9.5-by-76-mm) slots] [3/8-by-3-inch (9.5-by-76-mm) slots].

2.20 CORROSION-PROTECTION PIPING ENCASEMENT

A. Encasement for Underground Metal Piping:  ASTM A 674 or AWWA C105.

1. Form:  [Sheet] [Sheet or tube] [Tube].

Retain one of first three subparagraphs below.

2. Material:  LLDPE film of 0.008-inch (0.20-mm) minimum thickness.

3. Material:  LLDPE film of 0.008-inch (0.20-mm) minimum thickness or high-density, crosslaminated PE film of 0.004-inch (0.10-mm) minimum thickness.

4. Material:  High-density, crosslaminated PE film of 0.004-inch (0.10-mm) minimum thickness.

5. Color:  [Black] [Natural] <Insert other>.

2.21 MANHOLES

A. Standard Precast Concrete Manholes:  ASTM C 478 (ASTM C 478M), precast, reinforced concrete, of depth indicated, with provision for sealant joints.

1. Diameter:  48 inches (1200 mm) minimum, unless otherwise indicated.

2. Ballast:  Increase thickness of precast concrete sections or add concrete to base section, as required to prevent flotation.

3. Base Section:  6-inch (150-mm) minimum thickness for floor slab and 4-inch (102-mm) minimum thickness for walls and base riser section, and having separate base slab or base section with integral floor.

4. Riser Sections:  4-inch (102-mm) minimum thickness, and lengths to provide depth indicated.

5. Top Section:  Eccentric-cone type unless concentric-cone or flat-slab-top type is indicated.  Top of cone of size that matches grade rings.

6. Joint Sealant:  ASTM C 990 (ASTM C 990M), bitumen or butyl rubber.

Retain first subparagraph below unless not required.

7. Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

8. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than [60 inches (1500 mm)] <Insert other>.

Retain one of two subparagraphs below if required.

9. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and diameter matching manhole frame and cover.  Include sealant recommended by ring manufacturer.

10. Grade Rings:  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, to match diameter of manhole frame and cover.

Subparagraph below is optional for precast concrete manholes.  Retain only if required and coating will be plant applied.  Verify availability.

11. Protective Coating:  Plant-applied, [SSPC-Paint 16, coal-tar, epoxy-polyamide paint] <Insert other>; [10-mil (0.26-mm)] [15-mil (0.38-mm)] <Insert other> minimum thickness applied to [exterior] [exterior and interior] [interior] surfaces.

Retain subparagraph and associated subparagraphs below only if required.  Buried manholes with risers to grade require manhole frames and covers only at top of riser.

12. Manhole Frames and Covers:  Ferrous; 24-inch (610-mm) ID by 7- to 9-inch (175- to 225-mm) riser with 4-inch- (102-mm-) minimum width flange and 26-inch- (660-mm-) diameter cover.  Include indented top design with lettering cast into cover, using wording equivalent to "STORM SEWER."

a. Material:  [ASTM A 536, Grade 60-40-18 ductile] [ASTM A 48, Class 35 gray] iron, unless otherwise indicated.

Subparagraph below is optional.  Retain only if required and coating will be foundry applied.  Verify availability.

b. Protective Coating:  Foundry-applied, SSPC-Paint 16, coal-tar, epoxy-polyamide paint; [10-mil (0.26-mm)] [15-mil (0.38-mm)] minimum thickness applied to all surfaces, unless otherwise indicated.

B. Designed Precast Concrete Manholes:  ASTM C 913; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.

1. Ballast:  Increase thickness of one or more precast concrete sections or add concrete to manhole, as required to prevent flotation.

2. Joint Sealant:  ASTM C 990 (ASTM C 990M), bitumen or butyl rubber.

Retain first subparagraph below unless not required.

3. Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

4. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than [60 inches (1500 mm)] <Insert other>.

Retain one of two subparagraphs below if required.

5. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and diameter matching manhole frame and cover.  Include sealant recommended by ring manufacturer.

6. Grade Rings:  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, to match diameter of manhole frame and cover.

Subparagraph below is optional for precast concrete manholes.  Retain only if required and coating will be plant applied.  Verify availability.

7. Protective Coating:  Plant-applied, [SSPC-Paint 16, coal-tar, epoxy-polyamide paint] <Insert other>; [10-mil (0.26-mm)] [15-mil (0.38-mm)] <Insert other> minimum thickness applied to [exterior] [exterior and interior] [interior] surfaces.

Retain subparagraph and associated subparagraphs below only if required.  Buried manholes with risers to grade require manhole frames and covers only at top of riser.

8. Manhole Frames and Covers:  Ferrous; 24-inch (610-mm) ID by 7- to 9-inch (175- to 225-mm) riser with 4-inch- (102-mm-) minimum width flange and 26-inch- (660-mm-) diameter cover.  Include indented top design with lettering cast into cover, using wording equivalent to "STORM SEWER."

a. Material:  [ASTM A 536, Grade 60-40-18 ductile] [ASTM A 48, Class 35 gray] iron, unless otherwise indicated.

Subparagraph below is optional.  Retain only if required and coating will be foundry applied.  Verify availability.

b. Protective Coating:  Foundry-applied, SSPC-Paint 16, coal-tar, epoxy-polyamide paint; [10-mil (0.26-mm)] [15-mil (0.38-mm)] minimum thickness applied to all surfaces, unless otherwise indicated.

C. Cast-in-Place Concrete Manholes:  Construct of reinforced-concrete bottom, walls, and top; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, dimensions, and appurtenances indicated.

1. Ballast:  Increase thickness of concrete, as required to prevent flotation.

Retain first subparagraph below unless not required.

2. Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

3. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than [60 inches (1500 mm)] <Insert other>.

Retain one of two subparagraphs below if required.

4. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and diameter matching manhole frame and cover.  Include sealant recommended by ring manufacturer.

5. Grade Rings:  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, to match diameter of manhole frame and cover.

Retain subparagraph and associated subparagraphs below only if required.  Buried manholes with risers to grade require manhole frames and covers only at top of riser.

6. Manhole Frames and Covers:  Ferrous; 24-inch (610-mm) ID by 7- to 9-inch (175- to 225-mm) riser with 4-inch- (102-mm-) minimum width flange and 26-inch- (660-mm-) diameter cover.  Include indented top design with lettering cast into cover, using wording equivalent to "STORM SEWER."

a. Material:  [ASTM A 536, Grade 60-40-18 ductile] [ASTM A 48, Class 35 gray] iron, unless otherwise indicated.

Subparagraph below is otional.  Retain only if required and coating will be foundry applied.  Verify availability.

b. Protective Coating:  Foundry-applied, SSPC-Paint 16, coal-tar, epoxy-polyamide paint; [10-mil (0.26-mm)] [15-mil (0.38-mm)] minimum thickness applied to all surfaces, unless otherwise indicated.

D. Fiberglass Manholes:  ASTM D 3753, fabricated, FRP.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Associated Fiberglass Enterprises.

b. Containment Solutions, Inc.

c. L.F. Manufacturing, Inc.

d. <Insert manufacturer's name.>

2. Diameter:  48 inches (1200 mm) minimum, unless otherwise indicated.

3. Ballast:  Increase thickness of concrete base, as required to prevent flotation.

4. Base Section:  Concrete, 6-inch (150-mm) minimum thickness.

Retain first subparagraph below unless not required.

5. Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

6. Steps:  Individual FRP steps or FRP ladder, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than [60 inches (1500 mm)] <Insert other>.

Retain one of two subparagraphs below if required.

7. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and diameter matching manhole frame and cover.  Include sealant recommended by ring manufacturer.

8. Grade Rings:  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, to match diameter of manhole frame and cover.

Retain subparagraph and associated subparagraphs below only if required.  Buried manholes with risers to grade require manhole frames and covers only at top of the riser.

9. Manhole Frames and Covers:  Ferrous; 24-inch (610-mm) ID by 7- to 9-inch (175- to 225-mm) riser with 4-inch- (102-mm-) minimum width flange and 26-inch- (660-mm-) diameter cover.  Include indented top design with lettering cast into cover, using wording equivalent to "STORM SEWER."

a. Material:  [ASTM A 536, Grade 60-40-18 ductile] [ASTM A 48, Class 35 gray] iron, unless otherwise indicated.

Subparagraph below is optional.  Retain only if required and coating will be foundry applied.  Verify availability.

b. Protective Coating:  Foundry-applied, SSPC-Paint 16, coal-tar, epoxy-polyamide paint; [10-mil (0.26-mm)] [15-mil (0.38-mm)] minimum thickness applied to all surfaces, unless otherwise indicated.

2.22 CONCRETE

A. General:  Cast-in-place concrete according to ACI 318/318R, ACI 350R, and the following:

1. Cement:  ASTM C 150, Type II.

2. Fine Aggregate:  ASTM C 33, sand.

3. Coarse Aggregate:  ASTM C 33, crushed gravel.

4. Water:  Potable.

B. Portland Cement Design Mix:  4000 psi (27.6 MPa) minimum, with 0.45 maximum water-cementitious materials ratio.

1. Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2. Reinforcement Bars:  ASTM A 615/A 615M, Grade 60 (420 MPa), deformed steel.

C. Ballast and Pipe Supports:  Portland cement design mix, 3000 psi (20.7 MPa) minimum, with 0.58 maximum water-cementitious materials ratio.

1. Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2. Reinforcement Bars:  ASTM A 615/A 615M, Grade 60 (420 MPa), deformed steel.

2.23 POLYMER-CONCRETE, CHANNEL DRAINAGE SYSTEMS

A. Description, General:  Modular system of precast, polymer-concrete channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.  Include number of units required to form total lengths indicated.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. ABT, Inc.

2. ACO Polymer Products, Inc.

3. Innovative Plastics Products. Inc.

4. Mea-Josam Div.; Josam Company.

5. Strongwell; Lenoir City Div.

6. <Insert manufacturer's name.>

Retain one of first three paragraphs and associated subparagraphs below.

C. Sloped-Invert, Polymer-Concrete Systems:  Include the following components:

1. Channel Sections:  Interlocking-joint, precast, modular units with end caps.  Include 4-inch (102-mm) inside width and deep, rounded bottom, with built-in invert slope of 0.6 percent and with outlets in number, sizes, and locations indicated.  Include extension sections necessary for required depth.

Delete first subparagraph below if not required.

a. Frame:  Include gray-iron or steel frame for grate.

2. Grates with manufacturer's designation "[Heavy] [Medium] Duty," with slots or perforations that fit recesses in channels.

a. Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel].

3. Covers:  Solid gray iron, if indicated.

Delete subparagraph below if not required.

4. Locking Mechanism:  Manufacturer's standard device for securing grates to channel sections.

D. Narrow-Width, Level-Invert, Polymer-Concrete Systems:  Include the following components:

1. Channel Sections:  Interlocking-joint, precast, modular units with end caps.  Include 5-inch (127-mm) inside width and 9-3/4-inch- (248-mm-) deep, rounded bottom, with level invert and with NPS 4 (DN 100) outlets in number and locations indicated.

2. Grates with slots or perforations that fit recesses in channels.

a. Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel].

3. Covers:  Solid gray iron, if indicated.

Delete subparagraph below if not required.

4. Locking Mechanism:  Manufacturer's standard device for securing grates to channel sections.

E. Wide-Width, Level-Invert, Polymer-Concrete Systems:  Include the following components:

1. Channel Sections:  Interlocking-joint, precast, modular units with end caps.  Include 8-inch (203-mm) inside width and 13-3/4-inch- (350-mm-) deep, rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

2. Grates with slots or other openings that fit recesses in channels.

a. Material:  [Fiberglass] [Gray iron].

3. Covers:  Solid gray iron, if indicated.

Delete subparagraph below if not required.

4. Locking Mechanism:  Manufacturer's standard device for securing grates to channel sections.

F. Drainage Specialties:  Precast, polymer-concrete units.

Revise four subparagraphs and associated subparagraphs below to suit Project.

1. Large Catch Basins:  24-by-12-inch (610-by-305-mm) polymer-concrete body, with outlets in number and sizes indicated.  Include gray-iron slotted grate.

Delete first subparagraph below if not required.

a. Frame:  Include gray-iron or steel frame for grate.

2. Small Catch Basins:  19- to 24-inch by approximately 6-inch (483- to 610-mm by approximately 150-mm) polymer-concrete body, with outlets in number and sizes indicated.  Include gray-iron slotted grate.

Delete first subparagraph below if not required.

a. Frame:  Include gray-iron or steel frame for grate.

3. Oil Interceptors:  Polymer-concrete body with interior baffle and 4 steel support channels and two 1/4-inch- (6.4-mm-) thick, steel-plate covers.

a. Capacity:  [140 gal. (530 L)] [200 gal. (757 L)] [260 gal. (984 L)].

b. Inlet and Outlet:  [NPS 4 (DN 100)] [NPS 6 (DN 150)].

4. Sediment Interceptors:  27-inch- (686-mm-) square, polymer-concrete body, with outlets in number and sizes indicated.  Include 24-inch- (610-mm-) square, gray-iron frame and slotted grate.

G. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

H. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

2.24 PLASTIC, CHANNEL DRAINAGE SYSTEMS

Retain systems in this Article only in areas of light traffic unless entire system is of heavy-duty construction.

A. Description, General:  Modular system of plastic channel sections, grates, and appurtenances; designed so grates fit into frames without rocking or rattling.  Include number of units required to form total lengths indicated.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. ACO Polymer Prod.

2. MultiDrain Corp.

3. NDS Inc.

4. Tuf-Tite, Inc.

5. Zurn Industries, Inc.; Zurn Light Commercial Specialty Plumbing Products.

6. <Insert manufacturer's name.>

C. Fiberglass Systems:  Include the following components:

1. Channel Sections:  Interlocking-joint, fiberglass modular units, with built-in invert slope of approximately 1 percent and with end caps.  Include rounded or inclined inside bottom surface, with outlets in number, sizes, and locations indicated.

a. Width:  [6 inches (150 mm)] [6 or 8 inches (150 or 203 mm)] [8 inches (203 mm)].

2. Factory- or field-attached frames that fit channel sections and grates.

a. Material:  [Galvanized steel] [Stainless steel] [Manufacturer's standard metal].

3. Grates with slots or perforations that fit frames.

a. Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel].

4. Covers:  Solid gray iron, if indicated.

5. Drainage Specialties:  Include the following plastic components:

a. Large Catch Basins:  24-inch- (610-mm-) square plastic body, with outlets in number and sizes indicated.  Include gray-iron frame and slotted grate.

b. Small Catch Basins:  12-by-24-inch (305-by-610-mm) plastic body, with outlets in number and sizes indicated.  Include gray-iron frame and slotted grate.

D. PE Systems:  Include the following components:

1. Channel Sections:  Interlocking-joint, PE modular units, 4 inches (102 mm) wide, with end caps.  Include rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

2. Grates:  PE, ladder shaped; with stainless-steel screws.

3. Color:  Gray, unless otherwise indicated.

4. Drainage Specialties:  Include the following PE components:

Retain one of five subparagraphs below.

a. Drains:  4-inch- (102-mm-) diameter, round, slotted top; with NPS 4 (DN 100) bottom outlet.

b. Drains:  8-inch- (203-mm-) diameter, round, slotted top; with NPS 6 (DN 150) bottom outlet.

c. Drains:  4-inch- (102-mm-) square, slotted top; with NPS 3 (DN 80) bottom outlet.

d. Drains:  8-inch- (203-mm-) square, slotted top; with NPS 6 (DN 150) bottom outlet.

e. Catch Basins:  12-inch- (305-mm-) square plastic body, with outlets in number and sizes indicated.  Include PE slotted grate 11-3/4 inches (298 mm) square by 1-1/8 inches (28.6 mm) thick.

E. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

F. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

2.25 CATCH BASINS

A. Standard Precast Concrete Catch Basins:  ASTM C 478 (ASTM C 478M), precast, reinforced concrete, of depth indicated, with provision for sealant joints.

1. Base Section:  6-inch (150-mm) minimum thickness for floor slab and 4-inch (102-mm) minimum thickness for walls and base riser section, and having separate base slab or base section with integral floor.

2. Riser Sections:  4-inch (102-mm) minimum thickness, 48-inch (1220-mm) diameter, and lengths to provide depth indicated.

3. Top Section:  Eccentric-cone type unless concentric-cone or flat-slab-top type is indicated.  Top of cone of size that matches grade rings.

4. Joint Sealant:  ASTM C 990 (ASTM C 990M), bitumen or butyl rubber.

Retain one of first two subparagraphs below if required.

5. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and shape matching catch basin frame and grate.  Include sealant recommended by ring manufacturer.

6. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch (150- to 229-mm) total thickness, that match 24-inch- (610-mm-) diameter frame and grate.

7. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of catch basin to finished grade is less than [60 inches (1500 mm)] <Insert other>.

8. Pipe Connectors:  ASTM C 923 (ASTM C 923M), resilient, of size required, for each pipe connecting to base section.

B. Designed Precast Concrete Catch Basins:  ASTM C 913, precast, reinforced concrete; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.

1. Joint Sealants:  ASTM C 990 (ASTM C 990M), bitumen or butyl rubber.

Retain one of first two subparagraphs below if required.

2. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and shape matching catch basin frame and grate.  Include sealant recommended by ring manufacturer.

3. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch (150- to 229-mm) total thickness, that match 24-inch- (610-mm-) diameter frame and grate.

4. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of catch basin to finished grade is less than [60 inches (1500 mm)] <Insert other>.

5. Pipe Connectors:  ASTM C 923 (ASTM C 923M), resilient, of size required, for each pipe connecting to base section.

C. Cast-in-Place Concrete, Catch Basins:  Construct of reinforced concrete; designed according to ASTM C 890 for structural loading; of depth, shape, dimensions, and appurtenances indicated.

1. Bottom, Walls, and Top:  Reinforced concrete.

2. Channels and Benches:  Concrete.

3. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of catch basin to finished grade is less than [60 inches (1500 mm)] <Insert other>.

Retain paragraph and subparagraphs below for rectangular structures.

D. Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for A-16, structural loading.  Include flat grate with small square or short-slotted drainage openings.

1. Size:  24 by 24 inches (610 by 610 mm) minimum, unless otherwise indicated.

2. Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

Retain paragraph and subparagraphs above or paragraph and subparagraph below.

Retain paragraph below for round, manhole-type structures.

E. Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for A-16, structural loading.  Include 24-inch (610-mm) ID by 7- to 9-inch (178- to 229-mm) riser with 4-inch (102-mm) minimum width flange, and 26-inch- (660-mm-) diameter flat grate with small square or short-slotted drainage openings.

1. Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

2.26 STORMWATER INLETS

Stormwater inlets are made of precast concrete, cast-in-place concrete, and brick.  Select from six inlet paragraphs in this Article.

Revise three paragraphs below to suit utility requirements.

A. Curb Inlets:  Made with vertical curb opening, of materials and dimensions according to utility standards.

B. Gutter Inlets:  Made with horizontal gutter opening, of materials and dimensions according to utility standards.  Include heavy-duty frames and grates.

C. Combination Inlets:  Made with vertical curb and horizontal gutter openings, of materials and dimensions according to utility standards.  Include heavy-duty frames and grates.

Retain paragraph below with either of last two paragraphs above.

D. Frames and Grates:  Heavy-duty frames and grates according to utility standards.

Retain, edit, or delete four paragraphs above or below.

Revise three paragraphs below to suit Project, and detail on Drawings.

E. Curb Inlets:  Vertical curb opening, of materials and dimensions indicated.

F. Gutter Inlets:  Horizontal gutter opening, of materials and dimensions indicated.  Include heavy-duty frames and grates.

G. Combination Inlets:  Vertical curb and horizontal gutter openings, of materials and dimensions indicated.  Include heavy-duty frames and grates.

Retain paragraph below with either of last two paragraphs above.

H. Frames and Grates:  Dimensions, opening pattern, free area, and other attributes indicated.

See Division 05 Section "Metal Gratings" for fabricated-steel grating.

2.27 STORMWATER DETENTION STRUCTURES

Detail these structures.  They are usually made of cast-in-place concrete or sections of large piping and often include features for special applications.

A. Cast-in-Place Concrete, Stormwater Detention Structures:  Construct of reinforced-concrete bottom, walls, and top; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, dimensions, and appurtenances indicated.

1. Ballast:  Increase thickness of concrete, as required to prevent flotation.

Delete first subparagraph below if grade rings are not required and edit "Manhole Frames and Covers" Paragraph if frame will be cast in concrete top.

2. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch (150- to 229-mm) total thickness, that match 24-inch- (610-mm-) diameter frame and cover.

3. Steps:  [Individual FRP steps or FRP ladder] [Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] [ASTM A 615/A 615M, deformed, 1/2-inch (13-mm) steel reinforcing rods encased in ASTM D 4101, PP] <Insert other>, wide enough to allow worker to place both feet on 1 step and designed to prevent lateral slippage off of step.  Cast or anchor steps into sidewalls at 12- to 16-inch (300- to 400-mm) intervals.  Omit steps if total depth from floor of structure to finished grade is less than [60 inches (1500 mm)] <Insert other>.

B. Manhole Frames and Covers:  ASTM A 536, Grade 60-40-18, ductile-iron castings designed for heavy-duty service.  Include 24-inch (610-mm) ID by 7- to 9-inch (178- to 229-mm) riser with 4-inch (102-mm) minimum width flange, and 26-inch- (660-mm-) diameter cover.  Include indented top design with lettering "STORM SEWER" cast into cover.

2.28 PIPE OUTLETS

Revise this Article to suit Project, and detail on Drawings.  Delete first paragraph below if piping includes flared outlet fittings and concrete head walls are not required.

A. Head Walls:  Cast-in-place reinforced concrete, with apron and tapered sides.

B. Riprap Basins:  Broken, irregular size and shape, graded stone according to NSSGA's "Quarried Stone for Erosion and Sediment Control."

Retain one of three subparagraphs below or insert another grade.  Refer to NSSGA's "Quarried Stone for Erosion and Sediment Control" for sizes.

1. Average Size:  NSSGA No. R-3, screen opening 2 inches (51 mm).

2. Average Size:  NSSGA No. R-4, screen opening 3 inches (76 mm).

3. Average Size:  NSSGA No. R-5, screen opening 5 inches (127 mm).

Delete two paragraphs below unless these sizes of stone are required.

C. Filter Stone:  According to NSSGA's "Quarried Stone for Erosion and Sediment Control," No. FS-2, No. 4 screen opening, average-size, graded stone.

D. Energy Dissipaters:  According to NSSGA's "Quarried Stone for Erosion and Sediment Control," No. A-1, 3-ton (2700-kg) average weight armor stone, unless otherwise indicated.

2.29 DRY WELLS

Retain one of three paragraphs and associated subparagraphs below.  Detail on Drawings.

A. Description:  ASTM C 913, precast, reinforced, perforated concrete rings.  Include the following:

1. Floor:  Cast-in-place concrete.

2. Cover:  Liftoff-type concrete cover with cast-in lift rings.

3. Wall Thickness:  4 inches (102 mm) minimum with 1-inch (25-mm) diameter or 1-by-3-inch- (25-by-76-mm-) maximum slotted perforations arranged in rows parallel to axis of ring.

a. Total Free Area of Perforations:  Approximately 15 percent of ring interior surface.

b. Ring Construction:  Designed to be self-aligning.

4. Filtering Material:  ASTM D 448, Size No. 24, 3/4- to 2-1/2-inch (19- to 63-mm) washed, crushed stone or gravel.

B. Description:  Manufactured PE side panels and top cover that assemble into 50-gal. (190-L) storage capacity units.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Flo-Well Products, Ltd.

b. <Insert manufacturer's name.>

2. Side Panels:  With knockout ports for piping and seepage holes.

3. Top Cover:  With knockout port for drain.

4. Filter Fabric:  As recommended by unit manufacturer.

5. Filtering Material:  ASTM D 448, Size No. 24, 3/4- to 2-1/2-inch (19- to 63-mm) washed, crushed stone or gravel.

C. Description:  Constructed-in-place aggregate type.  Include the following:

1. Lining:  Clay or concrete bricks.

Retain subparagraph above or first subparagraph below.

2. Lining:  Concrete blocks or precast concrete rings with notches or weep holes.

3. Filtering Material:  ASTM D 448, Size No. 24, 3/4- to 2-1/2-inch (19- to 63-mm) washed, crushed stone or gravel.

4. Cover:  Precast, reinforced-concrete slab, designed for structural loading according to ASTM C 890 and made according to ASTM C 913.  Include slab dimensions that will extend 12 inches (300 mm) minimum beyond edge of excavation, with bituminous coating over entire surface.  Cast cover with opening for manhole in center.

5. Manhole:  24-inch- (610-mm-) diameter, reinforced-concrete access lid with steel lift rings.  Include bituminous coating over entire surface.

2.30 STORMWATER DISPOSAL SYSTEMS

Retain one of two paragraphs and associated subparagraphs below.

A. Chamber Systems:

Chambers made by different manufacturers are not uniform but are similar with different capacities.  Detail systems and indicate total chamber capacities on Drawings.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Advanced Drainage Systems, Inc.

b. Cultec, Inc.

c. Hancor, Inc.

d. Infiltrator Systems, Inc.

e. <Insert manufacturer's name.>

2. Storage and Leaching Chambers:  Molded PE with perforated sides and open bottom.  Include number of chambers, distribution piping, end plates, and other standard components as required for system total capacity.

3. Filtering Material:  ASTM D 448, Size No. 24, 3/4- to 2-1/2-inch (19- to 63-mm) washed, crushed stone or gravel.

4. Filter Mat:  Geotextile woven or spun filter fabric, in 1 or more layers, for minimum total unit weight of 4 oz./sq. yd. (135 g/sq. m).

B. Pipe Systems:  Perforated manifold, header, and lateral piping complying with AASHTO M 252M for NPS 10 (DN 250) and smaller, AASHTO M 294M for NPS 12 to NPS 48 (DN 250 to DN 1200), and AASHTO MP7 for NPS 54 and NPS 60 (DN 1350 and DN 1500).  Include proprietary fittings, couplings, seals, and filter fabric.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Advanced Drainage Systems, Inc.

b. Hancor, Inc.

c. <Insert manufacturer's name.>

2.31 MISCELLANEOUS MATERIALS

Retain this Article if painting of concrete manholes or ferrous frames and covers is required.

A. Paint:  SSPC-Paint 16.

B. PE Sheeting:  ASTM D 4397, with at least 8-mil (0.2-mm) thickness[ or other equivalent, impervious material].

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavation, trenching, and backfilling are specified in Division 31 Section "Earth Moving."

3.2 PIPING APPLICATIONS

A. Pipe couplings and special pipe fittings with pressure ratings at least equal to piping rating may be used in applications below, unless otherwise indicated.

1. Use nonpressure-type flexible couplings where required to join gravity-flow, nonpressure sewer piping, unless otherwise indicated.

a. [Unshielded] [Shielded] flexible [or rigid ]couplings for same or minor difference OD pipes.

b. Unshielded, increaser/reducer-pattern, flexible [or rigid ]couplings for pipes with different OD.

c. Ring-type flexible couplings for piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

2. Use pressure-type pipe couplings for force-main joints.

B. Special Pipe Fittings:  Use for pipe expansion and deflection.  Pipe couplings and special pipe fittings with pressure ratings at least equal to piping rating may be used in applications below, unless otherwise indicated.

Retain option in paragraph below to allow Contractor to select piping materials from those retained.

C. Gravity-Flow, Nonpressure Sewer Piping:  Use[ any of] the following pipe materials for each size range:

Retain one or more of nine subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. NPS 3 (DN 80):  Hub-and-spigot, [Extra-Heavy] [Service] class, cast-iron soil pipe and fittings; [gaskets; and gasketed] [calking materials; and calked] joints.

2. NPS 3 (DN 80):  Hubless cast-iron soil pipe and fittings; [shielded, stainless-steel] [heavy-duty, shielded, stainless-steel] [heavy-duty, cast-iron] [unshielded] couplings; and coupled joints.

3. NPS 3 (DN 80):  NPS 4 (DN 100) corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

4. NPS 3 (DN 80):  NPS 4 (DN 100) corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

5. NPS 3 (DN 80):  ABS, SDR 35, sewer pipe and fittings; gaskets; and gasketed joints.

6. NPS 3 (DN 80):  Corrugated PE drainage pipe and fittings, [silttight] [soiltight] couplings, and coupled joints.

7. NPS 3 (DN 80):  PVC water-service pipe; PVC Schedule 40, water-service-pipe fittings; and solvent-cemented joints.

8. NPS 3 (DN 80):  NPS 4 (DN 100) PVC sewer pipe and fittings; gaskets; and gasketed joints.

9. NPS 3 (DN 80):  NPS 4 (DN 100) Class [1] [2] [3], nonreinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of nine subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

10. NPS 4 to NPS 6 (DN 100 to DN 150):  Hub-and-spigot, [Extra-Heavy] [Service] class, cast-iron soil pipe and fittings; [gaskets; and gasketed] [calking materials; and calked] joints.

11. NPS 4 to NPS 6 (DN 100 to DN 150):  Hubless cast-iron soil pipe and fittings; [shielded, stainless-steel] [heavy-duty, shielded, stainless-steel] [heavy-duty, cast-iron] couplings; and coupled joints.

12. NPS 4 and NPS 6 (DN 100 and DN 150):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

13. NPS 4 and NPS 6 (DN 100 and DN 150):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

14. NPS 4 and NPS 6 (DN 100 and DN 150):  ABS, SDR 35, sewer pipe and fittings; gaskets; and gasketed joints.

15. NPS 4 and NPS 6 (DN 100 and DN 150):  Corrugated PE drainage pipe and fittings, [silttight] [soiltight] couplings, and coupled joints.

16. NPS 4 and NPS 6 (DN 100 and DN 150):  Cellular-core PVC pipe, PVC sewer pipe fittings, and solvent-cemented joints.

17. NPS 4 and NPS 6 (DN 100 and DN 150):  PVC sewer pipe and fittings, gaskets, and gasketed joints.

18. NPS 4 and NPS 6 (DN 100 and DN 150):  Class [1] [2] [3], nonreinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of 13 subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

19. NPS 8 to NPS 12 (DN 200 to DN 300):  Hub-and-spigot, [Extra-Heavy] [Service] class, cast-iron soil pipe and fittings; [gaskets; and gasketed] [calking materials; and calked] joints.

20. NPS 8 to NPS 12 (DN 200 to DN 300):  Hubless cast-iron soil pipe and fittings; [shielded, stainless-steel] [heavy-duty, shielded, stainless-steel] [heavy-duty, cast-iron] couplings; and coupled joints.

21. NPS 8 to NPS 12 (DN 200 to DN 300):  NPS 14 (DN 350) ductile-iron culvert pipe, ductile-iron standard[ or compact] fittings, gaskets, and gasketed joints.

22. NPS 8 to NPS 12 (DN 200 to DN 300):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

23. NPS 8 to NPS 12 (DN 200 to DN 300):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

24. NPS 8 to NPS 12 (DN 200 to DN 300):  ABS, SDR 42, sewer pipe and fittings; gaskets, and gasketed joints.

25. NPS 8 to NPS 12 (DN 200 to DN 300):  Corrugated PE drainage pipe and fittings in NPS 8 and NPS 10 (DN 200 and DN 250) and corrugated PE pipe and fittings in NPS 12 (DN 300), [silttight] [soiltight] couplings, and coupled joints.

26. NPS 8 to NPS 12 (DN 200 to DN 300):  Cellular-core PVC pipe, PVC sewer pipe fittings, and solvent-cemented joints.

27. NPS 8 to NPS 12 (DN 200 to DN 300):  PVC sewer pipe and fittings, gaskets, and gasketed joints.

28. NPS 8 to NPS 12 (DN 200 to DN 300):  PVC profile gravity sewer pipe and fittings, gaskets, and gasketed joints.

29. NPS 8 to NPS 12 (DN 200 to DN 300):  Fiberglass Type [2] [2 or 4] [4], Class [II] [III] [IV] [V], <Insert liner if required>, <Insert stiffness if required>, sewer RTRP, Type [1] [1 or 2] [2] RTRF, gaskets, and gasketed joints.

30. NPS 8 to NPS 12 (DN 200 to DN 300):  Nonreinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

31. NPS 8 to NPS 12 (DN 200 to DN 300):  NPS 12 (DN 300) reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of 11 subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

32. NPS 15 (DN 375):  Hub-and-spigot, [Extra-Heavy] [Service] class, cast-iron soil pipe and fittings; [gaskets; and gasketed] [calking materials; and calked] joints.

33. NPS 15 (DN 375):  Hubless cast-iron soil pipe and fittings; [shielded, stainless-steel] [heavy-duty, shielded, stainless-steel] [heavy-duty, cast-iron] couplings; and coupled joints.

34. NPS 15 (DN 375):  NPS 16 (DN 400) ductile-iron culvert pipe, ductile-iron standard[ or compact] fittings, gaskets, and gasketed joints.

35. NPS 15 (DN 375):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

36. NPS 15 (DN 375):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

37. NPS 15 (DN 375):  Corrugated PE pipe and fittings, [silttight] [soiltight] couplings, and coupled joints.

38. NPS 15 (DN 375):  PVC sewer pipe and fittings, gaskets, and gasketed joints.

39. NPS 15 (DN 375):  PVC profile gravity sewer pipe and fittings, gaskets, and gasketed joints.

40. NPS 15 (DN 375):  Fiberglass Type [2] [2 or 4] [4], Class [II] [III] [IV] [V], <Insert liner if required>, <Insert stiffness if required>, sewer RTRP, Type [1] [1 or 2] [2] RTRF, gaskets, and gasketed joints.

41. NPS 15 (DN 375):  Nonreinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

42. NPS 15 (DN 375):  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of nine subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

43. NPS 18 to NPS 36 (DN 450 to DN 900):  Ductile-iron culvert pipe, ductile-iron standard[ or compact] fittings, gaskets, and gasketed joints.

44. NPS 18 to NPS 36 (DN 450 to DN 900):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

45. NPS 18 to NPS 36 (DN 450 to DN 900):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

46. NPS 18 to NPS 36 (DN 450 to DN 900):  Corrugated PE pipe and fittings, [silttight] [soiltight] couplings, and coupled joints.

47. NPS 18 to NPS 36 (DN 450 to DN 900):  PVC sewer pipe and fittings, gaskets, and gasketed joints.

48. NPS 18 to NPS 36 (DN 450 to DN 900):  PVC profile gravity sewer pipe and fittings, gaskets, and gasketed joints.

49. NPS 18 to NPS 36 (DN 450 to DN 900):  Fiberglass Type [2] [2 or 4] [4], Class [II] [III] [IV] [V], <Insert liner if required>, <Insert stiffness if required>, sewer RTRP, Type [1] [1 or 2] [2] RTRF, gaskets, and gasketed joints.

50. NPS 18 to NPS 36 (DN 450 to DN 900):  Nonreinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

51. NPS 18 to NPS 36 (DN 450 to DN 900):  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of six subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

52. NPS 42 to NPS 64 (DN 1050 to DN 1600):  Ductile-iron culvert pipe, ductile-iron standard[ or compact] fittings, gaskets, and gasketed joints.

53. NPS 42 to NPS 64 (DN 1050 to DN 1600):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

54. NPS 42 to NPS 60 (DN 1050 to DN 1500):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

55. NPS 42 to NPS 60 (DN 1050 to DN 1500):  Corrugated PE pipe and fittings, [silttight] [soiltight] couplings, and coupled joints.

56. NPS 42 to NPS 60 (DN 1050 to DN 1500):  Fiberglass Type [2] [2 or 4] [4], Class [II] [III] [IV] [V], <Insert liner if required>, <Insert stiffness if required>, sewer RTRP, Type [1] [1 or 2] [2] RTRF, gaskets, and gasketed joints.

57. NPS 42 to NPS 60 (DN 1050 to DN 1500):  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

58. NPS 66 to NPS 144 (DN 1650 to DN 3600):  Corrugated steel pipe and fittings, [standard] [special]-joint bands, and banded joints.

59. NPS 66 to NPS 120 (DN 1650 to DN 3000):  Corrugated aluminum pipe and fittings, [standard] [special]-joint bands, and banded joints.

60. NPS 66 to NPS 144 (DN 1650 to DN 3600):  Fiberglass Type [2] [2 or 4] [4], Class [II] [III] [IV] [V], <Insert liner if required>, <Insert stiffness if required>, sewer RTRP, Type [1] [1 or 2] [2] RTRF, gaskets, and gasketed joints.

61. NPS 66 to NPS 144 (DN 1650 to DN 3600):  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

Retain option in paragraph below to allow Contractor to select piping materials from those retained.

D. Force-Main Pressure Piping:  Use[ any of] the following pipe materials for each size range:

1. NPS 2 (DN 50):  PVC Schedule [40] [80], water-service pipe; PVC Schedule [40] [80], water-service-pipe fittings; and solvent-cemented joints.

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

2. NPS 3 (DN 80):  Ductile-iron pressure pipe; ductile-iron standard or compact fittings; gaskets; and gasketed joints.

3. NPS 3 (DN 80):  PVC Schedule [40] [80], water-service pipe; PVC Schedule [40] [80], water-service-pipe fittings; and solvent-cemented joints.

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

4. NPS 4 (DN 100):  Ductile-iron pressure pipe; ductile-iron standard or compact fittings; gaskets; and gasketed joints.

5. NPS 4 (DN 100):  PVC pressure pipe, PVC pressure fittings, gaskets, and gasketed joints.

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

6. NPS 6 to NPS 8 (DN 150 to DN 200):  Ductile-iron pressure pipe; standard- or compact-pattern, ductile-iron fittings; gaskets; and gasketed joints.

7. NPS 6 to NPS 8 (DN 150 to DN 200):  PVC pressure pipe, PVC pressure fittings, gaskets, and gasketed joints.

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

8. NPS 10 and NPS 12 (DN 250 and DN 300):  Ductile-iron pressure pipe; standard- or compact-pattern, ductile-iron fittings; gaskets; and gasketed joints.

9. NPS 10 and NPS 12 (DN 250 and DN 300):  PVC pressure pipe; compact-pattern, ductile-iron fittings; gaskets; and gasketed joints.

3.3 PIPING INSTALLATION

A. General Locations and Arrangements:  Drawing plans and details indicate general location and arrangement of underground storm drainage piping.  Location and arrangement of piping layout take design considerations into account.  Install piping as indicated, to extent practical.  Where specific installation is not indicated, follow piping manufacturer's written instructions.

B. Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.

C. Install manholes for changes in direction unless fittings are indicated.  Use fittings for branch connections unless direct tap into existing sewer is indicated.

D. Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

E. Tunneling:  Install pipe under streets or other obstructions that cannot be disturbed by tunneling, jacking, or a combination of both.

F. Install gravity-flow, nonpressure drainage piping according to the following:

Revise three subparagraphs below to suit Project.

1. Install piping pitched down in direction of flow, at minimum slope of [1] [2] <Insert other> percent, unless otherwise indicated.

2. Install piping [NPS 6 (DN 150)] <Insert other> and larger with restrained joints at tee fittings and at changes in direction.  Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

3. Install piping with [36-inch (915-mm)] [48-inch (1220-mm)] [60-inch (1525-mm)] [72-inch (1830-mm)] <Insert other> minimum cover.

Retain subparagraph above or first subparagraph below.

4. Install piping below frost line.

5. Install hub-and-spigot, cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

6. Install hubless cast-iron soil piping according to CISPI C310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

7. Install ductile-iron culvert piping according to ASTM A 716.

8. Install ductile-iron and special fittings according to AWWA C600 or AWWA M41.

9. Install corrugated steel piping according to ASTM A 798/A 798M.

10. Install corrugated aluminum piping according to ASTM B 788/B 788M.

11. Install ABS sewer piping according to ASTM D 2321 and ASTM F 1668.

12. Install PE corrugated sewer piping according to CPPA's "Recommended Installation Practices for Corrugated Polyethylene Pipe and Fittings."

13. Install PVC cellular-core piping according to ASTM D 2321 and ASTM F 1668.

14. Install PVC sewer piping according to ASTM D 2321 and ASTM F 1668.

15. Install PVC profile gravity sewer piping according to ASTM D 2321 and ASTM F 1668.

16. Install fiberglass sewer piping according to ASTM D 3839 and ASTM F 1668.

17. Install nonreinforced-concrete sewer piping according to ASTM C 1479 and ACPA's "Concrete Pipe Installation Manual."

18. Install reinforced-concrete sewer piping according to ASTM C 1479 and ACPA's "Concrete Pipe Installation Manual."

G. Install force-main pressure piping according to the following:

Revise two subparagraphs below to suit Project.

1. Install piping with restrained joints at tee fittings and at horizontal and vertical changes in direction.  Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

2. Install piping with [36-inch (915-mm)] [48-inch (1220-mm)] [60-inch (1525-mm)] [72-inch (1830-mm)] <Insert other> minimum cover.

Retain subparagraph above or first subparagraph below.

3. Install piping below frost line.

4. Install ductile-iron pressure piping according to AWWA C600 or AWWA M41.

5. Install ductile-iron special fittings according to AWWA C600.

6. Install PVC pressure piping according to AWWA M23 or ASTM D 2774 and ASTM F 1668.

7. Install PVC water-service piping according to ASTM D 2774 and ASTM F 1668.

Retain paragraph and subparagraphs below only if required.

H. Install corrosion-protection piping encasement over the following underground metal piping according to ASTM A 674 or AWWA C105:

1. Hub-and-spigot, cast-iron soil pipe and fittings.

2. Hubless cast-iron soil pipe and fittings.

3. Ductile-iron pipe and fittings.

4. Special pipe fittings.

3.4 PIPE JOINT CONSTRUCTION

A. Basic pipe joint construction is specified in Division 33 Section "Common Work Results for Utilities." Where specific joint construction is not indicated, follow piping manufacturer's written instructions.

B. Join gravity-flow, nonpressure drainage piping according to the following:

1. Join hub-and-spigot, cast-iron soil piping with gasket joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

2. Join hub-and-spigot, cast-iron soil piping with calked joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for lead and oakum calked joints.

3. Join hubless cast-iron soil piping according to CISPI C310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for hubless-coupling joints.

4. Join ductile-iron culvert piping according to AWWA C600 for push-on joints.

5. Join ductile-iron and special fittings according to AWWA C600 or AWWA M41.

6. Join corrugated steel sewer piping according to ASTM A 798/A 798M.

7. Join corrugated aluminum sewer piping according to ASTM B 788/B 788M.

8. Join ABS sewer piping according to ASTM D 2321 and ASTM D 2751 for elastomeric-seal joints.

9. Join corrugated PE piping according to CPPA 100 and the following:

a. Use silttight couplings for Type 2, silttight joints.

b. Use soiltight couplings for Type 1, soiltight joints.

10. Join PVC cellular-core piping according to ASTM D 2321 and ASTM F 891 for solvent-cement joints.

11. Join PVC sewer piping according to ASTM D 2321 and ASTM D 3034 for elastomeric-seal joints or ASTM D 3034 for elastomeric gasket joints.

12. Join PVC profile gravity sewer piping according to ASTM D 2321 for elastomeric-seal joints or ASTM F 794 for gasketed joints.

13. Join fiberglass sewer piping according to ASTM D 3839 for elastomeric-seal joints.

14. Join nonreinforced-concrete sewer piping according to ASTM C 14 (ASTM C 14M) and ACPA's "Concrete Pipe Installation Manual" for rubber-gasket joints.

15. Join reinforced-concrete sewer piping according to ACPA's "Concrete Pipe Installation Manual" for rubber-gasket joints.

16. Join dissimilar pipe materials with nonpressure-type flexible[ or rigid] couplings.

C. Join force-main pressure piping according to the following:

1. Join ductile-iron pressure piping according to AWWA C660 or AWWA M41 for push-on joints.

2. Join ductile-iron special fittings according to AWWA C660 or AWWA M41 for push-on joints.

3. Join PVC pressure piping according to AWWA M23 for gasketed joints.

4. Join PVC water-service piping according to ASTM D 2855 for solvent-cemented joints.

D. Join dissimilar pipe materials with pressure-type couplings.

3.5 BACKWATER VALVE INSTALLATION

A. Install horizontal-type backwater valves in piping where indicated.

B. Install combination horizontal and manual gate valve type in piping and in manholes where indicated.

C. Install terminal-type backwater valves on end of piping and in manholes where indicated.

3.6 CLEANOUT INSTALLATION

A. Install cleanouts and riser extension from sewer pipe to cleanout at grade.  Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts and cast-iron soil pipe for riser extensions to cleanouts.  Install piping so cleanouts open in direction of flow in sewer pipe.

1. Use light-duty, top-loading classification cleanouts in [earth or unpaved foot-traffic] <Insert other> areas.

2. Use medium-duty, top-loading classification cleanouts in [paved foot-traffic] <Insert other> areas.

3. Use heavy-duty, top-loading classification cleanouts in [vehicle-traffic service] <Insert other> areas.

4. Use extra-heavy-duty, top-loading classification cleanouts in [roads] <Insert other> areas.

B. Set cleanout frames and covers in earth in cast-in-place concrete block, [18 by 18 by 12 inches (450 by 450 by 300 mm)] <Insert other> deep.  Set with tops [1 inch (25 mm)] <Insert other> above surrounding earth grade.

C. Set cleanout frames and covers in concrete pavement with tops flush with pavement surface.

3.7 DRAIN INSTALLATION

A. Install type of drains in locations indicated.

1. Use light-duty, top-loading classification drains in [earth or unpaved foot-traffic] <Insert other> areas.

2. Use medium-duty, top-loading classification drains in [paved foot-traffic] <Insert other> areas.

3. Use heavy-duty, top-loading classification drains in [vehicle-traffic service] <Insert other> areas.

4. Use extra-heavy-duty, top-loading classification drains in [roads] <Insert other> areas.

B. Embed drains in 4-inch (102-mm) minimum depth of concrete around bottom and sides.

C. Fasten grates to drains if indicated.

D. Set drain frames and covers with tops flush with pavement surface.

E. Assemble trench sections with flanged joints.

F. Embed trench sections in [4-inch (102-mm)] <Insert other> minimum concrete around bottom and sides.

3.8 MANHOLE INSTALLATION

A. General:  Install manholes, complete with appurtenances and accessories indicated.

B. Install precast concrete manhole sections according to ASTM C 891.

Cast-in-place manholes in paragraph below require data or details on Drawings.

C. Construct cast-in-place manholes as indicated.

Retain first paragraph below if paint is to be field applied to exterior surfaces of cast-in-place concrete manholes.

D. Install PE sheeting on earth where cast-in-place-concrete manholes are to be built.

E. Install FRP manholes according to manufacturer's written instructions.

F. Set tops of frames and covers flush with finished surface of manholes that occur in pavements.  Set tops [3 inches (76 mm)] <Insert other> above finished surface elsewhere, unless otherwise indicated.

3.9 CATCH BASIN INSTALLATION

A. Construct catch basins to sizes and shapes indicated.

B. Set frames and grates to elevations indicated.

3.10 STORMWATER INLET[ AND OUTLET] INSTALLATION

A. Construct inlet head walls, aprons, and sides of reinforced concrete, as indicated.

B. Construct riprap of broken stone, as indicated.

C. Install outlets that spill onto grade, anchored with concrete, where indicated.

D. Install outlets that spill onto grade, with flared end sections that match pipe, where indicated.

E. Construct energy dissipaters at outlets, as indicated.

3.11 DRY WELL INSTALLATION

A. Excavate hole to diameter of at least 6 inches (150 mm) greater than outside of dry well.  Do not extend excavation into ground-water table.

B. Install precast, concrete-ring dry wells according to the following:

1. Assemble rings to depth indicated.

2. Extend rings to height where top of cover will be approximately 8 inches (203 mm) below finished grade.

3. Backfill bottom of inside of rings with filtering material to level at least 12 inches (300 mm) above bottom.

4. Extend effluent inlet pipe 12 inches (300 mm) into rings and terminate into side of tee fitting.

5. Backfill around outside of rings with filtering material to top level of rings.

6. Install cover over top of rings.

C. Install manufactured, PE dry wells according to manufacturer's written instructions and the following:

1. Assemble and install panels and cover.

2. Backfill bottom of inside of unit with filtering material to level at least [12 inches (300 mm)] <Insert other> above bottom.

3. Extend effluent inlet pipe [12 inches (300 mm)] <Insert other> into unit and terminate into side of tee fitting.

4. Install filter fabric around outside of unit.

5. Install filtering material around outside of unit.

D. Install constructed-in-place dry wells according to the following:

1. Install brick lining material dry and laid flat, with staggered joints for seepage.  Build to diameter and depth indicated.

2. Install block lining material dry, with staggered joints and 20 percent minimum of blocks on side for seepage.  Install precast concrete rings with notches or weep holes for seepage.  Build to diameter and depth indicated.

3. Extend lining material to height where top of manhole will be approximately [8 inches (203 mm)] <Insert other> below finished grade.

4. Backfill bottom of inside of lining with filtering material to level at least [12 inches (300 mm)] <Insert other> above bottom.

5. Extend effluent inlet pipe [12 inches (300 mm)] <Insert other> into lining and terminate into side of tee fitting.

6. Backfill around outside of lining with filtering material to top level of lining.

7. Install manhole over top of dry well.  Support cover on undisturbed soil.  Do not support cover on lining.

3.12 CONCRETE PLACEMENT

A. Place cast-in-place concrete according to ACI 318/318R.

3.13 DRAINAGE SYSTEM INSTALLATION

A. Assemble and install components according to manufacturer's written instructions.

B. Install with top surfaces of components, except piping, flush with finished surface.

C. Assemble channel sections to form slope down toward drain outlets.  Use sealants, adhesives, fasteners, and other materials recommended by system manufacturer.

D. Embed channel sections and drainage specialties in [4-inch (102-mm)] <Insert other> minimum concrete around bottom and sides.

E. Fasten grates to channel sections if indicated.

F. Assemble channel sections with flanged or interlocking joints.

G. Embed channel sections in [4-inch (102-mm)] <Insert other> minimum concrete around bottom and sides.

3.14 STORMWATER DISPOSAL SYSTEM INSTALLATION

A. Chamber Systems:  Excavate trenches of width and depth, and install system and backfill according to chamber manufacturer's written instructions.  Include storage and leaching chambers, filtering material, and filter mat.

Retain paragraph above or below that matches system specified in Part 2.

B. Piping Systems:  Excavate trenches of width and depth, and install piping system, filter fabric, and backfill according to piping manufacturer's written instructions.

3.15 CONNECTIONS

A. Connect nonpressure, gravity-flow drainage piping in building's storm building drains specified in Division 22 Section "Facility Storm Drainage Piping."

B. Connect force-main pressure piping to building's storm drainage force mains specified in Division 22 Section "Facility Storm Drainage Piping." Terminate piping where indicated.

1. Use commercially manufactured wye fittings for piping branch connections.  Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye fitting, plus 6-inch (150-mm) overlap, with not less than 6 inches (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

2. Make branch connections from side into existing piping, NPS 4 to NPS 20 (DN 100 to DN 500).  Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye with not less than 6 inches (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

3. Make branch connections from side into existing piping, NPS 21 (DN 525) or larger, or to underground manholes and structures by cutting opening into existing unit large enough to allow 3 inches (76 mm) of concrete to be packed around entering connection.  Cut end of connection pipe passing through pipe or structure wall to conform to shape of and be flush with inside wall, unless otherwise indicated.  On outside of pipe, manhole, or structure wall, encase entering connection in 6 inches (150 mm) of concrete for minimum length of 12 inches (300 mm) to provide additional support of collar from connection to undisturbed ground.

a. Use concrete that will attain a minimum 28-day compressive strength of 3000 psi (20.7 MPa), unless otherwise indicated.

b. Use epoxy-bonding compound as interface between new and existing concrete and piping materials.

4. Protect existing piping, manholes, and structures to prevent concrete or debris from entering while making tap connections.  Remove debris or other extraneous material that may accumulate.

C. Connect to sediment interceptors specified in Division 22 Section "Sanitary Waste Interceptors."

3.16 CLOSING ABANDONED STORM DRAINAGE SYSTEMS

Revise this Article to suit Project.

A. Abandoned Piping:  Close open ends of abandoned underground piping indicated to remain in place.  Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed.  Use either procedure below:

1. Close open ends of piping with at least [8-inch- (203-mm-)] <Insert other> thick, brick masonry bulkheads.

2. Close open ends of piping with threaded metal caps, plastic plugs, or other acceptable methods suitable for size and type of material being closed.  Do not use wood plugs.

B. Abandoned Manholes and Structures:  Excavate around manholes and structures as required and use one procedure below:

1. Remove manhole or structure and close open ends of remaining piping.

2. Remove top of manhole or structure down to at least [36 inches (915 mm)] <Insert other> below final grade.  Fill to within [12 inches (300 mm)] <Insert other> of top with stone, rubble, gravel, or compacted dirt.  Fill to top with concrete.

C. Backfill to grade according to Division 31 Section "Earth Moving."

3.17 PAINTING

Retain this Article if paint is to be field applied to concrete manholes or ferrous frames and covers.

A. Clean and prepare concrete manhole surfaces for field painting.  Remove loose efflorescence, chalk, dust, grease, oils, and release agents.  Roughen surface as required to remove glaze.  Paint the following concrete surfaces as recommended by paint manufacturer:

1. Cast-in-Place-Concrete Manholes:  All [exterior, except bottom] [exterior, except bottom and all interior] [interior].

2. Precast Concrete Manholes:  All [exterior] [exterior and interior] [interior].

B. Prepare ferrous frame and cover surfaces according to SSPC-PA 1 and paint according to SSPC-PA 1 and SSPC-Paint 16.  Do not paint surfaces with foundry-applied, corrosion-resistant coating.

3.18 IDENTIFICATION

A. Materials and their installation are specified in Division 31 Section "Earth Moving." Arrange for installation of green warning tape directly over piping and at outside edge of underground structures.

1. Use[ warning tape or] detectable warning tape over ferrous piping.

2. Use detectable warning tape over nonferrous piping and over edges of underground structures.

3.19 FIELD QUALITY CONTROL

A. Inspect interior of piping to determine whether line displacement or other damage has occurred.  Inspect after approximately 24 inches (610 mm) of backfill is in place, and again at completion of Project.

1. Submit separate reports for each system inspection.

2. Defects requiring correction include the following:

a. Alignment:  Less than full diameter of inside of pipe is visible between structures.

b. Deflection:  Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 92.5 percent of piping diameter.

c. Crushed, broken, cracked, or otherwise damaged piping.

d. Infiltration:  Water leakage into piping.

e. Exfiltration:  Water leakage from or around piping.

3. Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

4. Reinspect and repeat procedure until results are satisfactory.

B. Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

1. Do not enclose, cover, or put into service before inspection and approval.

2. Test completed piping systems according to authorities having jurisdiction.

3. Schedule tests and inspections by authorities having jurisdiction with at least 24 hours' advance notice.

4. Submit separate report for each test.

Retain test in first subparagraph and associated subparagraphs below only if required.

5. Gravity-Flow Storm Drainage Piping:  Test according to requirements of authorities having jurisdiction, UNI-B-6, and the following:

a. Exception:  Piping with soiltight joints unless required by authorities having jurisdiction.

b. Option:  Test plastic piping according to ASTM F 1417.

c. Option:  Test concrete piping according to ASTM C 924 (ASTM C 924M).

6. Force-Main Storm Drainage Piping:  Perform hydrostatic test after thrust blocks, supports, and anchors have hardened.  Test at pressure not less than 1-1/2 times the maximum system operating pressure, but not less than [150 psig (1035 kPa)] <Insert other>.

a. Ductile-Iron Piping:  Test according to AWWA C600, "Hydraulic Testing" Section.

b. PVC Piping:  Test according to AWWA M23, "Testing and Maintenance" Chapter.

C. Leaks and loss in test pressure constitute defects that must be repaired.

D. Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

3.20 CLEANING

A. Clean interior of piping of dirt and superfluous materials.[ Flush with potable water.]

END OF SECTION 334100

	STORM UTILITY DRAINAGE PIPING
	334100 - 1



