Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
03/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 334600 - SUBDRAINAGE
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes subdrainage systems for the following:

Retain one or more subparagraphs below to suit Project.

1. Foundations.

2. Underslab areas.

3. Plaza decks.

4. Retaining walls.

5. Landscaped areas.

Retain paragraph and subparagraph below if molded-sheet drainage panels are specified in a Division 07Division 7 Section.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 07 waterproofing Sections for molded-sheet drainage panels.

1.3 DEFINITIONS

Retain abbreviations and terms that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. HDPE:  High-density polyethylene plastic.

C. PE:  Polyethylene plastic.

D. PP:  Polypropylene plastic.

E. PS:  Polystyrene plastic.

F. PVC:  Polyvinyl chloride plastic.

G. Subdrainage:  Drainage system that collects and removes subsurface or seepage water.

1.4 SUBMITTALS

Revise paragraph and subparagraphs below to suit Project.

A. Product Data:  For the following:

1. Perforated-wall pipe and fittings.

2. Solid-wall pipe and fittings.

3. Drainage conduits.

4. Drainage panels.

5. Geotextile filter fabrics.

Retain paragraph below only if drainage panels are to be installed directly onto waterproofing membrane.

B. Approval of waterproofing manufacturer's service agent for use of drainage panels against and for waterproofing membrane protection.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements"Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to edit this Section.

A. Refer to the "Piping Applications" Article in Part 3 for applications of pipe, tube, fitting, and joining materials.

2.3 PERFORATED-WALL PIPES AND FITTINGS

Pipe materials in this Article have perforated walls and are joined with tight joints.

A. Perforated PE Pipe and Fittings:

Perforated PE pipe and fittings in subparagraph below are available in NPS 3 to NPS 6 (DN 80 to DN 150).  Joints are coupling type.

1. NPS 6 (DN 150) and Smaller:  ASTM F 405 or AASHTO M 252, Type CP; corrugated, for coupled joints.

Perforated PE pipe and fittings in first subparagraph below are available in NPS 8 to NPS 24 (DN 200 to DN 600).  Joints are coupling type.

2. NPS 8 (DN 200) and Larger:  ASTM F 667; AASHTO M 252, Type CP; or AASHTO M 294, Type CP; corrugated; for coupled joints.

3. Couplings:  Manufacturer's standard, band type.

Perforated PVC sewer pipe and fittings in paragraph below are available in NPS 4 (DN 100) only.  Joints are bell-and-spigot, loose type.

B. Perforated PVC Sewer Pipe and Fittings:  ASTM D 2729, bell-and-spigot ends, for loose joints.

Perforated clay pipe and fittings in paragraph and subparagraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600).  Joints are socket-and-spigot, closed type.

C. Perforated Clay Pipe and Fittings:  ASTM C 700, Standard- and Extra-Strength classes, unglazed, socket-and-spigot ends, for gasketed joints.

1. Gaskets:  ASTM C 425, rubber.

Perforated concrete pipe and fittings in paragraph and subparagraph below are available in NPS 4 to NPS 24 (DN 100 to DN 600).  Joints are socket-and-spigot type.

D. Perforated Concrete Pipe and Fittings:  ASTM C 444 (ASTM C 444M), Type 1, and applicable requirements in ASTM C 14 (ASTM C 14M), Class 2, socket-and-spigot ends for gasketed joints.

1. Gaskets:  ASTM C 443 (ASTM C 443M), rubber.

2.4 SOLID-WALL PIPES AND FITTINGS

Pipe materials in this Article have solid walls (without perforations) and are joined with tight joints.  They are used for headers and piping if inlet of water is not required.

ABS sewer pipe and fittings in paragraph and subparagraphs below are available in NPS 2 to NPS 12 (DN 50 to DN 300).

A. ABS Sewer Pipe and Fittings:  ASTM D 2751.

1. Solvent Cement:  ASTM D 2235.

2. Gaskets:  ASTM F 477, elastomeric seal.

Cast-iron soil pipe and fittings in paragraph and subparagraph below are available in NPS 2 to NPS 15 (DN 50 to DN 375).  Joints are hub-and-spigot, gasket type.

B. Cast-Iron Soil Pipe and Fittings:  ASTM A 74, Service and Extra-Heavy classes, hub-and-spigot ends, gray, for gasketed joints.

1. Gaskets:  ASTM C 564, rubber, of thickness matching class of pipe.

PE drainage tubing and fittings in paragraph and subparagraph below are available in NPS 4 to NPS 10 (DN 100 to DN 250).  Joints are coupling type.

C. PE Drainage Tubing and Fittings:  AASHTO M 252, Type S, corrugated, with smooth waterway, for coupled joints.

1. Couplings:  AASHTO M 252, corrugated, band type, matching tubing and fittings.

PE pipe and fittings in paragraph and subparagraph below are available in NPS 12 to NPS 36 (DN 300 to DN 900).  Joints are coupling type.

D. PE Pipe and Fittings:  AASHTO M 294, Type S, corrugated, with smooth waterway, for coupled joints.

1. Couplings:  AASHTO M 294, corrugated, band type, matching tubing and fittings.

PVC sewer pipe and fittings in paragraph and subparagraph below are available in NPS 4 to NPS 15 (DN 100 to DN 375).  Joints are bell-and-spigot, gasket type.

E. PVC Sewer Pipe and Fittings:  ASTM D 3034, SDR 35, bell-and-spigot ends, for gasketed joints.

1. Gaskets:  ASTM F 477, elastomeric seal.

2.5 SPECIAL PIPE COUPLINGS

A. Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping.  Include ends of same sizes as piping to be joined and corrosion-resistant metal tension band and tightening mechanism on each end.

1. Sleeve Materials:

a. For Concrete Pipes:  ASTM C 443 (ASTM C 443M), rubber.

b. For Cast-Iron Soil Pipes:  ASTM C 564, rubber.

c. For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

d. For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

2. Unshielded Flexible Couplings:  Elastomeric sleeve with[ stainless-steel shear ring and] corrosion-resistant metal tension band and tightening mechanism on each end.

3. Shielded Flexible Couplings:  ASTM C 1460, elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant metal tension band and tightening mechanism on each end.

2.6 CLEANOUTS

A. Cast-Iron Cleanouts:  ASME A112.36.2M; with round-flanged, cast-iron housing; and secured, scoriated, Medium-Duty Loading class, cast-iron cover.  Include cast-iron ferrule and countersunk, brass cleanout plug.

B. Copper-Alloy Cleanouts:  ASME A112.36.2M; with round-flanged, cast-iron housing with clamping device; and scoriated, [Light] [Medium]-Duty Loading class, [copper-alloy] <Insert material> cover.  Include countersunk, brass cleanout plug.

C. PVC Cleanouts:  ASTM D 3034, PVC cleanout threaded plug and threaded pipe hub.

2.7 DRAINAGE CONDUITS

Refer to the table for drainage conduits at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

ASTM D 4716 computes in-plane flow rate by gpm/ft. (cu. m/s per m) of unit width.  Manufacturers typically use gpm (L/min.) for an indicated size, and this unit of measure is used for drainage conduits in this Section for ease of comparison.  Verify flow of selected drainage conduits.

A. Molded-Sheet Drainage Conduits:  Prefabricated geocomposite with cuspated, molded-plastic drainage core wrapped in geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Wick Drain Corporation.

b. JDR Enterprises, Inc.

c. TC Mirafi.

d. <Insert manufacturer's name.>

2. Nominal Size:  12 inches (305 mm) high by approximately 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [30 gpm (114 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain "Nominal Size" Subparagraph and associated subparagraph above or below.

3. Nominal Size:  18 inches (457 mm) high by approximately 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [45 gpm (170 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain two subparagraphs below with "Nominal Size" Subparagraph and associated subparagraph selected above.

4. Filter Fabric:  PP geotextile.

5. Fittings:  HDPE with combination NPS 4 and NPS 6 (DN 100 and DN 150) outlet connection.

B. Multipipe Drainage Conduits:  Prefabricated geocomposite with interconnected, corrugated, perforated-pipe core molded from HDPE complying with ASTM D 1248 and wrapped in geotextile filter fabric.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Varicore Technologies, Inc.

b. <Insert manufacturer's name.>

Retain one "Nominal Size" Subparagraph and associated subparagraph below.

2. Nominal Size:  6 inches (152 mm) high by approximately 1-1/4 inches (31 mm) thick.

a. Minimum In-Plane Flow:  [15 gpm (57 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

3. Nominal Size:  12 inches (305 mm) high by approximately 1-1/4 inches (31 mm) thick.

a. Minimum In-Plane Flow:  [30 gpm (114 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

4. Nominal Size:  18 inches (457 mm) high by approximately 1-1/4 inches (31 mm) thick.

a. Minimum In-Plane Flow:  [45 gpm (170 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain three subparagraphs below with "Nominal Size" Subparagraph and associated subparagraph selected above.

5. Filter Fabric:  Nonwoven, needle-punched geotextile.

6. Fittings:  HDPE with combination NPS 4 and NPS 6 (DN 100 and DN 150) outlet connection.

7. Couplings:  HDPE.

C. Single-Pipe Drainage Conduits:  Prefabricated geocomposite with perforated corrugated core molded from HDPE complying with ASTM D 3350 and wrapped in geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Advanced Drainage Systems.

b. <Insert manufacturer's name.>

2. Nominal Size:  12 inches (305 mm) high by approximately 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [30 gpm (114 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain "Nominal Size" Subparagraph and associated subparagraph above or below.

3. Nominal Size:  18 inches (457 mm) high by approximately 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [45 gpm (170 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain three subparagraphs below with "Nominal Size" Subparagraph and associated subparagraph selected above.

4. Filter Fabric:  Nonwoven, PP geotextile.

5. Fittings:  HDPE with combination NPS 4 and NPS 6 (DN 100 and DN 150) outlet connection.

6. Couplings:  Corrugated HDPE band.

D. Mesh Fabric Drainage Conduits:  Prefabricated geocomposite with plastic-filament drainage core wrapped in geotextile filter fabric.  Include fittings for bends and connection to drainage piping.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Colbond Geosynthetics.

b. <Insert manufacturer's name.>

2. Nominal Size:  6 inches (2-mm) high by approximately 0.9 inch (23 mm) thick.

a. Minimum In-Plane Flow:  [2.4 gpm (9.1 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

3. Filter Fabric:  Nonwoven geotextile made of PP or polyester fibers or combination of both.  Flow rates range from 120 to 200 gpm/sq. ft. (81 to 136 L/s per sq. m) when tested according to ASTM D 4491.

E. Ring Fabric Drainage Conduits:  Drainage conduit with HDPE-rings-in-grid-pattern drainage core, for field-applied geotextile filter fabric.  Include fittings for bends and connection to drainage piping.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Invisible Structures, Inc.

b. <Insert manufacturer's name.>

2. Nominal Size:  0.5 m high by 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [82 gpm (310 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

Retain "Nominal Size" Subparagraph and associated subparagraph above or below.

3. Nominal Size:  1 m high by 1 inch (25 mm) thick.

a. Minimum In-Plane Flow:  [164 gpm (621 L/min.)] <Insert value> at hydraulic gradient of [1.0] <Insert value> when tested according to ASTM D 4716.

4. Filter Fabric:  Specified in Part 2 "Geotextile Filter Fabrics" Article.

2.8 DRAINAGE PANELS

Retain this Article if drainage panels are specified in this Section.  Delete if drainage panels are specified in a Division 07Division 7 waterproofing Section.

Refer to the table for drainage panels at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

ASTM D 4716 computes in-plane flow rate by gpm/ft. (cu. m/s per m) of unit width.  Manufacturers typically use gpm/ft. (L/min. per m) of unit width, and this unit of measure is used for drainage panels in this Section for ease of comparison.  Verify flow rate of selected drainage panels.

A. Molded-Sheet Drainage Panels:  Prefabricated geocomposite, [36 to 60 inches (915 to 1525 mm)] <Insert dimension> wide with drainage core faced with geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Wick Drain Corporation.

b. Cosella-Dorken.

c. Eljen Corp.

d. Greenstreak, Inc.

e. JDR Enterprises, Inc.

f. LINQ Industrial Fabrics, Inc.

g. Midwest Diversified Technologies Incorporated.

h. TC Mirafi.

i. <Insert manufacturer's name.>

2. Drainage Core:  Three-dimensional, nonbiodegradable, molded PP or PS.

a. Minimum Compressive Strength:  [10,000 lbf/sq. ft. (479 kPa)] [15,000 lbf/sq. ft. (718 kPa)] [18,000 lbf/sq. ft. (862 kPa)] [21,000 lbf/sq. ft. (1005 kPa)] <Insert value> when tested according to ASTM D 1621.

Flow rate varies with hydraulic gradient, thickness, and capacity of drainage core.  A hydraulic gradient of 1.0 is commonly quoted for vertical applications with maximum gravity flow.  Horizontal applications will have reduced flow rates, and manufacturers commonly report tests at hydraulic gradients of 0.05 or 0.1.  Flow rate is also influenced by compressive loading of drainage panel.  Manufacturers report various values such as 3600 lbf/sq. ft. or 25 psig (172 kPa).

b. Minimum In-Plane Flow Rate:  [2.8 gpm/ft. (35 L/min. per m)] [7 gpm/ft. (87 L/min. per m)] [15 gpm/ft. (188 L/min. per m)] <Insert value> of unit width at hydraulic gradient of [1.0] <Insert value> and compressive stress of [25 psig (172 kPa)] <Insert value> when tested according to ASTM D 4716.

Retain nonwoven geotextile and properties in subparagraph and associated subparagraphs below for walls and, if applicable, deck or plaza applications.

3. Filter Fabric:  Nonwoven needle-punched geotextile, manufactured for subsurface drainage, made from polyolefins or polyesters; with elongation greater than 50 percent; complying with the following properties determined according to AASHTO M 288:

Survivability rates a geotextile's ability to withstand installation stresses and is divided into 3 classes by AASHTO M 288.  Survivability measures grab, seam, tear, puncture, and burst strength.  Class 2 is default class recommended by AASHTO M 288 for subsurface drainage.  Select Class 1 in subparagraph below if higher strength is required; select Class 3 if lower strength is sufficient.

a. Survivability:  Class [1] [2] [3].

AASHTO M 288 bases selection of apparent opening size on percentages of backfill soils passing a No. 200 (0.075-mm) sieve.  First option in subparagraph below corresponds to less than 15 percent; second, 15 to 50 percent; and third, greater than 50 percent for Class 2 geotextiles.

b. Apparent Opening Size:  [No. 40 (0.425-mm)] [No. 60 (0.25-mm)] [No. 70 (0.212-mm)] sieve, maximum.

AASHTO M 288 bases selection of permittivity on percentages of backfill soils passing a No. 200 (0.075-mm) sieve.  First option in subparagraph below corresponds to less than 15 percent; second, 15 to 50 percent; and third, greater than 50 percent for Class 2 geotextiles.

c. Permittivity:  [0.5] [0.2] [0.1] per second, minimum.

Woven geotextile type in subparagraph below is sometimes used for deck or plaza applications.  Verify selections with geotextile and waterproofing manufacturers if required.  Woven geotextiles have a range of permeability and opening sizes and may be classified by AASHTO M 288 into subsurface drainage as well as separation applications.

4. Filter Fabric:  Woven geotextile fabric, manufactured for subsurface drainage, made from polyolefins or polyesters; with elongation less than 50 percent; complying with the following properties determined according to AASHTO M 288:

Survivability rates a geotextile's ability to withstand installation stresses and is divided into 3 classes by AASHTO M 288.  Survivability measures grab, seam, tear, puncture, and burst strength.  Class 2 is default class recommended by AASHTO M 288 for subsurface drainage and separation applications.  Select Class 1 in subparagraph below if higher strength is required; select Class 3 if lower strength is sufficient.

a. Survivability:  Class [1] [2] [3].

AASHTO M 288 bases selection of apparent opening size on percentages of backfill soils passing a No. 200 (0.075-mm) sieve.  First option in subparagraph below corresponds to less than 15 percent; second, 15 to 50 percent; and third, greater than 50 percent for Class 2 geotextiles for subsurface applications.  Fourth option corresponds to AASHTO M 288 default value for Class 2 separation rather than subsurface applications.

b. Apparent Opening Size:  [No. 40 (0.425-mm)] [No. 60 (0.25-mm)] [No. 70 (0.212-mm)] [No. 30 (0.6-mm)] sieve, maximum.

AASHTO M 288 bases selection of permittivity on percentages of backfill soils passing a No. 200 (0.075-mm) sieve.  First option in subparagraph below corresponds to less than 15 percent; second, 15 to 50 percent; and third, greater than 50 percent for Class 2 geotextiles for subsurface applications.  Fourth option corresponds to AASHTO M 288 default value for Class 2 separation rather than subsurface applications.

c. Permittivity:  [0.5] [0.2] [0.1] [0.02] per second, minimum.

Retain subparagraph below if drainage panel also acts as protection course on vertical or wall applications.  Soft waterproofing membranes can be damaged by drainage core during backfilling and under permanent soil pressure.

5. Film Backing:  Polymeric film bonded to drainage core surface.

B. Mesh Fabric Drainage Panels:  Prefabricated geocomposite with drainage core faced with geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Colbond Geosynthetics.

b. <Insert manufacturer's name.>

2. Drainage Core:  Open-construction, resilient, approximately 0.4-inch- (10.2-mm-) thick, plastic-filament mesh.

a. Minimum In-Plane Flow Rate:  [2.4 gpm/ft. (30 L/min. per m)] <Insert value> of unit width at hydraulic gradient of [1.0] <Insert value> and normal pressure of 25 psig (172 kPa) when tested according to ASTM D 4716.

3. Filter Fabric:  Nonwoven geotextile of PP or polyester fibers or combination of both.  Flow rates range from 120 to 200 gpm/sq. ft. (81 to 136 L/s per sq. m) when tested according to ASTM D 4491.

C. Net Fabric Drainage Panels:  Prefabricated geocomposite with drainage core faced with geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. GSE Lining Technology, Inc.

b. JDR Enterprises, Inc.

c. Strata Systems, Inc.

d. <Insert manufacturer's name.>

2. Drainage Core:  3-dimensional, PE nonwoven-strand geonet, approximately 0.25-inch- (6-mm-) thick.

a. Minimum In-Plane Flow Rate:  [2.4 gpm/ft. (30 L/min. per m)] [5 gpm/ft. (62 L/min. per m)] <Insert value> of unit width at hydraulic gradient of [1.0] <Insert value> and normal pressure of 25 psig (172 kPa) when tested according to ASTM D 4716.

3. Filter Fabric:  Nonwoven geotextile of PP or polyester fibers or combination of both.  Flow rates range from 120 to 200 gpm/sq. ft. (81 to 136 L/s per sq. m) when tested according to ASTM D 4491.

Drainage panels in paragraph and subparagraphs below require field application of geotextile filter fabric.

D. Ring Fabric Drainage Panels:  Drainage-core panel for field application of geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Invisible Structures, Inc.

b. <Insert manufacturer's name.>

2. Drainage Core:  3-dimensional, HDPE rings in grid pattern, approximately 0.1 inch (25 mm) thick.

a. Minimum In-Plane Flow Rate:  [50 gpm/ft. (625 L/min. per m)] <Insert value> of unit width at hydraulic gradient of [1.0] <Insert value> and normal pressure of 25 psig (172 kPa) when tested according to ASTM D 4716.

Retain paragraph and subparagraphs below for foundation-wall applications if an insulated drainage panel is required.  Edit edge and facing options as applicable.  Shiplap edge and unfaced panels describe Dow Chemical Company's "Perimate." Tongue-and-groove edge and faced panels describe Owens Corning's "Insul-Drain."

E. Fabric-Covered Insulated Drainage Panels:  Extruded PS board insulation complying with ASTM C 578; fabricated with [shiplap] [or] [tongue-and-groove] edges and with one side having grooved drainage channels[; unfaced] [; faced with geotextile filter fabric].

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Dow Chemical Company (The).

b. Owens Corning.

c. T. Clear Corporation.

d. <Insert manufacturer's name.>

Retain one of first two subparagraphs below.  First subparagraph corresponds to Dow's "Perimate" and Owens Corning's "Insul-Drain."

2. Type IV, 1.6-lb/cu. ft. (26-kg/cu. m) minimum density and 25-psig (172-kPa) minimum compressive strength.

3. Type VI, 1.8-lb/cu. ft. (29-kg/cu. m) minimum density and 40-psig (276-kPa) minimum compressive strength.

4. Minimum In-Plane Flow Rate:  [9 gpm/ft. (112 L/min. per m)] <Insert value> of unit width when tested according to ASTM D 4716.

Retain subparagraph below if panels are faced with geotextile filter fabric.

5. Filter Fabric:  Nonwoven geotextile of PP or polyester fibers or combination of both.  Flow rates range from 120 to 200 gpm/sq. ft. (81 to 136 L/s per sq. m) when tested according to ASTM D 4491.

Retain first paragraph and subparagraphs below for plaza deck applications if an unfaced insulation drainage panel with ribbed drainage channels is required.

F. Noncovered Insulated Drainage Panels:  Extruded PS board insulation complying with ASTM C 578; fabricated with rabbeted edges and with one side having ribbed drainage channels.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Dow Chemical Company (The).

b. Owens Corning.

c. <Insert manufacturer's name.>

Retain one of first two subparagraphs below.  First subparagraph corresponds to Dow's "Styrofoam Ribbed Roofmate" and Owens Corning's "Foamular 404 RB"; second corresponds to Owens Corning's "Foamular 604 RB." Type VI insulation is usually limited to intermittent or light pedestrian traffic.  Type VII is used for heavier pedestrian traffic.

2. Type VI, 1.8-lb/cu. ft. (29-kg/cu. m) minimum density and 40-psig (276-kPa) minimum compressive strength.

3. Type VII, 2.2-lb/cu. ft. (35-kg/cu. m) minimum density and 60-psig (414-kPa) minimum compressive strength.

4. Minimum In-Plane Flow Rate:  [9 gpm/ft. (112 L/min. per m)] <Insert value> of unit width when tested according to ASTM D 4716.

G. Expanded PS Insulated Drainage Panels:  PS bead board insulation; panels are 4 inches (102 mm) thick by 48 inches (1220 mm) wide and faced with geotextile filter fabric.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. GeoTech Systems Corporation.

b. <Insert manufacturer's name.>

2. Density:  2 lb/cu. ft. (32 kg/cu. m).

3. Compressive Strength:  800 lbf/sq. ft. (38 kPa).

4. Minimum In-Plane Flow Rate:  [3 gpm/ft. (37 L/min. per m)] <Insert value> of unit width when tested according to ASTM D 4716.

5. Filter Fabric:  Nonwoven geotextile of PP or polyester fibers or combination of both.  Flow rates range from 120 to 200 gpm/sq. ft. (81 to 136 L/s per sq. m) when tested according to ASTM D 4491.

2.9 SOIL MATERIALS

A. Backfill, drainage course, impervious fill, and satisfactory soil materials are specified in Division 31 Section "Earth Moving."

2.10 ROOFING FELTS

Delete this Article if no roofing felts.

A. [ASTM D 226, Type I, asphalt] [or] [ASTM D 227, coal-tar]-saturated roofing felt.

2.11 GEOTEXTILE FILTER FABRICS

A. Description:  Fabric of PP or polyester fibers or combination of both, with flow rate range from 110 to 330 gpm/sq. ft. (4480 to 13 440 L/min. per sq. m) when tested according to ASTM D 4491.

1. Structure Type:  [Nonwoven, needle-punched continuous filament] [or] [woven, monofilament or multifilament].

2. Style(s):  [Flat] [and] [sock].

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine surfaces and areas for suitable conditions where subdrainage systems are to be installed.

Retain first paragraph below if subdrainage system is required for landscaped areas.

B. If subdrainage is required for landscaping, locate and mark existing utilities, underground structures, and aboveground obstructions before beginning installation and avoid disruption and damage of services.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 EARTHWORK

A. Excavating, trenching, and backfilling are specified in Division 31 Section "Earth Moving."

3.3 PIPING APPLICATIONS

Coordinate products retained under each application below with products retained in Part 2 and with pipe sizes indicated on Drawings.

A. Underground Subdrainage Piping:

Retain one or more of three subparagraphs below that specify products suitable for Project applications.  If retaining more than one type of pipe, indicate location of each on Drawings.

1. Perforated PE pipe and fittings, couplings, and coupled joints.

Pipe in first subparagraph below is available in NPS 4 (DN 100) only.

2. Perforated PVC sewer pipe and fittings for loose, bell-and-spigot joints.

3. Perforated clay pipe and fittings, [Standard] [Extra]-Strength class; gaskets; and gasketed joints.

B. Underslab Subdrainage Piping:

Retain one or more of four subparagraphs below that specify products suitable for Project applications.  If retaining more than one type of pipe, indicate location of each on Drawings.

1. Perforated PE pipe and fittings, couplings, and coupled joints.

Pipe in first subparagraph below is available in NPS 4 (DN 100) only.

2. Perforated PVC sewer pipe and fittings and loose, bell-and-spigot joints.

3. Perforated clay pipe and fittings, Extra-Strength class; gaskets; and gasketed joints.

4. Perforated concrete pipe and fittings, gaskets, and gasketed joints.

C. Header Piping:

Retain one or more of four subparagraphs below that specify products suitable for Project applications.  If retaining more than one type of pipe, indicate location of each on Drawings.

1. ABS pipe and fittings[, gaskets, and gasketed] [and solvent-cemented] joints.

2. Cast-iron soil pipe and fittings, [Extra-Heavy] [Service] class; gaskets; and gasketed joints.

3. PE drainage tubing and fittings, couplings, and coupled joints.

4. PVC sewer pipe and fittings, couplings, and coupled joints.

3.4 CLEANOUT APPLICATIONS

Coordinate products retained under each application below with products retained in Part 2.

A. In Underground Subdrainage Piping:

1. At Grade in Earth:  [Cast-iron] [PVC] cleanouts.

2. At Grade in Paved Areas:  Cast-iron cleanouts.

B. In Underslab Subdrainage Piping:

1. In Equipment Rooms and Unfinished Areas:  Cast-iron cleanouts.

2. In Finished Areas:  Copper-alloy cleanouts.

3.5 FOUNDATION DRAINAGE INSTALLATION

A. Place impervious fill material on subgrade adjacent to bottom of footing after concrete footing forms have been removed.  Place and compact impervious fill to dimensions indicated, but not less than 6 inches (150 mm) deep and 12 inches (300 mm) wide.

B. Place impervious fill on subgrade adjacent to bottom of footing and compact to dimensions indicated, but not less than 6 inches (150 mm) deep and 12 inches (300 mm) wide after concrete footing forms have been removed.

C. Lay flat-style geotextile filter fabric in trench and overlap trench sides.

D. Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches (100 mm).

E. Encase pipe with sock-style geotextile filter fabric before installing pipe.  Connect sock sections with [adhesive] [or] [tape].

F. Install drainage piping as indicated in Part 3 "Piping Installation" Article for foundation subdrainage.

G. Add drainage course to width of at least 6 inches (150 mm) on side away from wall and to top of pipe to perform tests.

H. After satisfactory testing, cover drainage piping to width of at least 6 inches (150 mm) on side away from footing and above top of pipe to within 12 inches (300 mm) of finish grade.

I. Install drainage course and wrap top of drainage course with flat-style geotextile filter fabric.

J. Place layer of [flat-style geotextile filter fabric] [roofing felt] over top of drainage course, overlapping edges at least 4 inches (100 mm).

K. Install vertical drainage panels as follows:

1. Coordinate placement with other drainage materials.

2. Lay perforated drainage pipe at base of footing.  Install as indicated in Part 3 "Piping Installation" Article.  Do not install aggregate.

3. Separate 4 inches (100 mm) of fabric at beginning of roll and cut away 4 inches (100 mm) of core.  Wrap fabric around end of remaining core.

Retain first subparagraph below if pipe is used.

4. Wrap bottom of panel around drainage pipe.

5. Attach panel to wall at horizontal mark and at beginning of pipe.  Place core side of panel against wall.  Use concrete nails with washers through product cylinders to attach panel to wall.  Place nails from 2 to 6 inches (50 to 150 mm) below top of panel, approximately 48 inches (1200 mm) apart.[ Construction adhesives, metal stick pins, ordouble- double-sided tape may be used instead of nails.] Do not penetrate waterproofing.  Before using adhesives, discuss with waterproofing manufacturer.

6. If additional panels are required on same row, cut away 4 inches (100 mm) of installed panel core, install new panel against installed panel, and overlap new panel with installed panel fabric.

7. If additional rows of panels are required, overlap lower panel with 4 inches (100 mm) of fabric.

8. Cut panel as necessary to keep top 12 inches (300 mm) below finish grade.

9. For inside corners, bend panel.  For outside corners, cut core to provide 3 inches (75 mm) for overlap.

Coordinate first paragraph below with appropriate Division 07Division 7 waterproofing Sections or delete.  Refer to "Drainage Panel Characteristics" Article in the Evaluations for a discussion.

L. Do not use drainage panels as protection for waterproof membrane unless approved by factory-authorized service representative of waterproofing membrane manufacturer.  Submit approval if so used.

M. Place initial backfill material over compacted drainage course .  Place material in loose-depth layers not exceeding 6 inches (150 mm).  Thoroughly compact each layer.  Final backfill to finish elevations and slope away from building.

3.6 UNDERSLAB DRAINAGE INSTALLATION

A. Excavate for underslab drainage system after subgrade material has been compacted but before drainage course has been placed.  Include horizontal distance of at least 6 inches (150 mm) between drainage pipe and trench walls.  Grade bottom of trench excavations to required slope, and compact to firm, solid bed for drainage system.

B. Lay flat-style geotextile filter fabric in trench and overlap trench sides.

C. Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches (100 mm).

D. Encase pipe with sock-style geotextile filter fabric before installing pipe.  Connect sock sections with [adhesive] [or] [tape].

E. Install drainage piping as indicated in Part 3 "Piping Installation" Article for underslab subdrainage.

F. Add drainage course to width of at least 6 inches (150 mm) on side away from wall and to top of pipe to perform tests.

G. After satisfactory testing, cover drainage piping with drainage course to elevation of bottom of slab, and compact and wrap top of drainage course with flat-style geotextile filter fabric.

H. Install horizontal drainage panels as follows:

1. Coordinate placement with other drainage materials.

2. Lay perforated drainage pipe at inside edge of footings.

3. Place drainage panel over drainage pipe with core side up.  Peel back fabric and wrap fabric around pipe.  Locate top of core at bottom elevation of floor slab.

4. Butt additional panels against other installed panels.  If panels have plastic flanges, overlap installed panel with flange.

3.7 PLAZA DECK DRAINAGE INSTALLATION

A. Horizontal Drainage Panel:  Install between slab and floor cover.  Place core on structural floor.  Install panels to fit tightly around floor drains of building's storm drainage system.  Provide stormwater access into floor drain.

1. Install drainage piping as indicated in Part 3 "Piping Installation" Article for plaza deck subdrainage.

Retain paragraph and subparagraph above or paragraph below.

B. See Division 32 Section "Unit Paving."

3.8 RETAINING-WALL DRAINAGE INSTALLATION

Retain one of first two paragraphs below.

A. Lay flat-style geotextile filter fabric in trench and overlap trench sides.

B. Place supporting layer of drainage course over compacted subgrade to compacted depth of not less than 4 inches (100 mm).

C. Encase pipe with sock-style geotextile filter fabric before installing pipe.  Connect sock sections with [adhesive] [or] [tape].

D. Install drainage piping as indicated in Part 3 "Piping Installation" Article for retaining-wall subdrainage.

E. Add drainage course to width of at least 6 inches (150 mm) on side away from wall and to top of pipe to perform tests.

F. After satisfactory testing, cover drainage piping to width of at least 6 inches (150 mm) on side away from footing and above top of pipe to within 12 inches (300 mm) of finish grade.

G. Place drainage course in layers not exceeding 3 inches (75 mm) in loose depth; compact each layer placed and wrap top of drainage course with flat-style geotextile filter fabric.

H. Place layer of [flat-style geotextile filter fabric] [roofing felt] over top of drainage course, overlapping edges at least 4 inches (100 mm).

I. Install vertical drainage panels as follows:

1. Coordinate placement with other drainage materials.

2. Lay perforated drainage pipe at base of footing as described elsewhere in this Specification.  Do not install aggregate.

Retain subparagraph above or first subparagraph below.

3. If weep holes are used instead of drainage pipe, cut 1/2-inch- (13-mm-) diameter holes on core side at weep-hole locations.  Do not cut fabric.

4. Mark horizontal calk line on wall at a point 6 inches (150 mm) less than panel width above footing bottom.  Before marking wall, subtract footing width.

5. Separate 4 inches (100 mm) of fabric at beginning of roll and cut away 4 inches (100 mm) of core.  Wrap fabric around end of remaining core.

Retain first subparagraph below if pipe is used.

6. Wrap bottom of panel around drainage pipe.

7. Attach panel to wall at horizontal mark and at beginning of wall corner.  Place core side of panel against wall.  Use concrete nails with washers through product.  Place nails from 2 to 6 inches (50 to 150 mm) below top of panel, approximately 48 inches (1200 mm) apart.[ Construction adhesives, metal stick pins, or double-sided tape may be used instead of nails.] Do not penetrate waterproofing.  Before using adhesives, discuss with waterproofing manufacturer.

8. If another panel is required on same row, cut away 4 inches (100 mm) of installed panel core and wrap fabric over new panel.

9. If additional rows of panel are required, overlap lower panel with 4 inches (100 mm) of fabric.

10. Cut panel as necessary to keep top 12 inches (300 mm) below finish grade.

11. For inside corners, bend panel.  For outside corners, cut core to provide 3 inches (75 mm) for overlap.

Coordinate subparagraph below with appropriate Division 07Division 7 waterproofing Sections or delete.  Refer to "Drainage Panel Characteristics" Article in the Evaluations for a discussion.

12. Do not use drainage panels as protection for waterproof membrane unless approved by factory-authorized service representative of waterproofing membrane manufacturer.  Submit approval if so used.

J. Fill to Grade:  Place satisfactory soil fill material over compacted drainage course .  Place material in loose-depth layers not exceeding 6 inches (150 mm).  Thoroughly compact each layer.  Fill to finish grade.

3.9 LANDSCAPING DRAINAGE INSTALLATION

A. Provide trench width to allow installation of drainage conduit.  Grade bottom of trench excavations to required slope, and compact to firm, solid bed for drainage system.

B. Lay flat-style geotextile filter fabric in trench and overlap trench sides.

C. Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches (100 mm).

D. Install drainage conduits as indicated in Part 3 "Piping Installation" Article for landscaping subdrainage with horizontal distance of at least 6 inches (150 mm) between conduit and trench walls.  Wrap drainage conduits without integral geotextile filter fabric with flat-style geotextile filter fabric before installation.  Connect fabric sections with [adhesive] [or] [tape].

E. Add drainage course to top of drainage conduits.

F. After satisfactory testing, cover drainage conduit to within 12 inches (300 mm) of finish grade.

G. Install drainage course and wrap top of drainage course with flat-style geotextile filter fabric.

H. Place layer of [flat-style geotextile filter fabric] [roofing felt] over top of drainage course, overlapping edges at least 4 inches (100 mm).

I. Fill to Grade:  Place satisfactory soil fill material over drainage course.  Place material in loose-depth layers not exceeding 6 inches (150 mm).  Thoroughly compact each layer.  Fill to finish grade.

3.10 PIPING INSTALLATION

Show relationships of piping and other materials on Drawings.

A. Install piping beginning at low points of system, true to grades and alignment indicated, with unbroken continuity of invert.  Bed piping with full bearing in filtering material.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions and other requirements indicated.

Of first five subparagraphs below, retain only those applicable to Project.

Edit first subparagraph below as required for different minimum slope and cover.

1. Foundation Subdrainage:  Install piping pitched down in direction of flow, at a minimum slope of 0.5 percent and with a minimum cover of [36 inches (915 mm)] <Insert dimension>, unless otherwise indicated.

2. Underslab Subdrainage:  Install piping pitched down in direction of flow, at a minimum slope of 0.5 percent.

3. Plaza Deck Subdrainage:  Install piping pitched down in direction of flow, at a minimum slope of 1.0 percent.

4. Retaining-Wall Subdrainage:  When water discharges at end of wall into stormwater piping system, install piping pitched down in direction of flow, at a minimum slope of 0.5 percent and with a minimum cover of [36 inches (915 mm)] <Insert dimension>, unless otherwise indicated.  However, when water discharges through wall weep holes, pipe may be installed with a minimum slope of zero percent.

5. Landscaping Subdrainage:  Install piping pitched down in direction of flow, at a minimum slope of 0.5 percent and with a minimum cover of [36 inches (915 mm)] <Insert dimension>, unless otherwise indicated.

6. Lay perforated pipe with perforations down.

Revise subparagraph below to suit Project or delete.

7. Excavate recesses in trench bottom for bell ends of pipe.  Lay pipe with bells facing upslope and with spigot end entered fully into adjacent bell.

B. Use increasers, reducers, and couplings made for different sizes or materials of pipes and fittings being connected.  Reduction of pipe size in direction of flow is prohibited.

C. Install ABS piping according to ASTM D 2321.

D. Install PE piping according to ASTM D 2321.

E. Install PVC piping according to ASTM D 2321.

F. Install clay piping according to ASTM C 12 and NCPI's "Clay Pipe Engineering Manual."

G. Install concrete piping according to ACPA's "Concrete Pipe Handbook."

3.11 PIPE JOINT CONSTRUCTION

A. Cast-Iron Soil Pipe and Fittings:  Hub and spigot, with rubber compression gaskets according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook." Use gaskets that match class of pipe and fittings.

B. Join ABS pipe and fittings according to ASTM D 2751.

C. Join PE pipe, tubing, and fittings with couplings for soil-tight joints according to AASHTO's "Standard Specifications for Highway Bridges," Division II, Section 26.4.2.4, "Joint Properties."

D. Join perforated, PE pipe and fittings with couplings for soil-tight joints according to AASHTO's "Standard Specifications for Highway Bridges," Division II, Section 26.4.2.4, "Joint Properties"; or according to ASTM D 2321.

E. Join PVC pipe and fittings according to ASTM D 3034 with elastomeric seal gaskets according to ASTM D 2321.

F. Join perforated PVC pipe and fittings according to ASTM D 2729, with loose bell-and-spigot joints.

G. Join perforated clay pipe and fittings with gaskets according to ASTM C 425.

H. Join perforated concrete pipe and fittings with gaskets according to ASTM C 443 (ASTM C 443M).

I. Special Pipe Couplings:  Join piping made of different materials and dimensions with special couplings made for this application.  Use couplings that are compatible with and fit materials and dimensions of both pipes.

3.12 CLEANOUT INSTALLATION

A. Cleanouts for [Foundation] [Retaining-Wall] [and] [Landscaping] Subdrainage:

1. Install cleanouts from piping to grade.  Locate cleanouts at beginning of piping run and at changes in direction.  Install fittings so cleanouts open in direction of flow in piping.

2. In vehicular-traffic areas, use NPS 4 (DN 100) cast-iron soil pipe and fittings for piping branch fittings and riser extensions to cleanout.  Set cleanout frames and covers in a cast-in-place concrete anchor, 18 by 18 by 12 inches (450 by 450 by 300 mm) in depth.  Set top of cleanout flush with grade.  Cast-iron pipe may also be used for cleanouts in nonvehicular-traffic areas.

3. In nonvehicular-traffic areas, use NPS 4 (DN 100) [cast-iron] [PVC] pipe and fittings for piping branch fittings and riser extensions to cleanout.  Set cleanout frames and covers in a cast-in-place concrete anchor, 12 by 12 by 4 inches (300 by 300 by 100 mm) in depth.  Set top of cleanout plug 1 inch (25 mm) above grade.

B. Cleanouts for Underslab Subdrainage:

1. Install cleanouts and riser extensions from piping to top of slab.  Locate cleanouts at beginning of piping run and at changes in direction.  Install fittings so cleanouts open in direction of flow in piping.

2. Use NPS 4 (DN 100) cast-iron soil pipe and fittings for piping branch fittings and riser extensions to cleanout flush with top of slab.

3.13 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

Retain option in paragraph below if connection will be to building's storm drainage system.

B. Connect low elevations of subdrainage system to[ building's] solid-wall-piping storm drainage system.

Retain paragraph below if gravity discharge is not possible.

C. Where required, connect low elevations of [foundation] [underslab] subdrainage to stormwater sump pumps.

3.14 IDENTIFICATION

Retain this Article for landscaping subdrainage only.

A. Materials and their installation are specified in Division 31 Section "Earth Moving." Arrange for installation of green warning tapes directly over piping.

1. Install PE warning tape or detectable warning tape over ferrous piping.

2. Install detectable warning tape over nonferrous piping and over edges of underground structures.

3.15 FIELD QUALITY CONTROL

Insert specific test requirements in paragraph below to comply with authorities having jurisdiction.

A. Testing:  After installing drainage course to top of piping, test drain piping with water to ensure free flow before backfilling.  Remove obstructions, replace damaged components, and repeat test until results are satisfactory.

3.16 CLEANING

A. Clear interior of installed piping and structures of dirt and other superfluous material as work progresses.  Maintain swab or drag in piping and pull past each joint as it is completed.  Place plugs in ends of uncompleted pipe at end of each day or when work stops.

END OF SECTION 334600

	SUBDRAINAGE
	334600 - 1



