Elevator Checklist:

1. Hoistway enclosure to be fire rated.

2. Hoistway to be vented.

3. Provide convenience outlet (GFI) and light in pit.

4. Provide pit ladder.

5. Provide lighting and HVAC for elevator equipment room. Verify CFM, temperature and dehumidification requirements.

6. Provide fused disconnect or circuit breaker for each elevator, inside equipment room adjacent to door.

7. Provide dedicated circuits for elevator car lights and fan.

8. Provide convenience outlet (GFI) and telephone outlet near control panels in equipment room.

9. Provide ABC type fire extinguisher near equipment room door.

10.  Provide sump pit no larger than 18” x 18” at rear center of elevator pit. Sump pump must drain to collection device, not environment.

11.  Pit must be waterproof to storm or ground water.

12.  Elevator equipment rooms are recommended to have soundproofing.

13.  Verify requirements for temporary hoist beam. An 8” steel beam with a 5,000# capacity is typical.

14.  Pit reactions from jack or buffer can exceed 10,000#’s.

15.  Typical minimum dimensions for the equipment room are 5’-2” x 6’-6”.

