4.22
MOTOR STARTERS
4.22.1
Combination Full Voltage Non-Reversing Starter
4.22.1.1
General

Full voltage non-reversing (FVNR) motor starters shall be combination type with magnetic only circuit breakers or fusible disconnect switches.

4.22.1.2
Ratings


The motor starter shall be rated for 480 V, three phase, 60 Hz service. All combination starters units shall have a minimum interrupting rating of 22,000 ARMS, symmetrical. Each motor starter shall carry the Underwriters Laboratory (UL) label.

4.22.1.3
Control


Motor starter control voltage shall be 120 V unless otherwise noted.  Each starter shall have a separate control circuit transformer, and fused grounded secondary. Internal starter wiring, wire and terminal numbers shall conform to the schematic wiring diagrams on the drawings.

4.22.1.4
Overloads


Each starter shall be provided with three manual reset overload relays with a bimetallic or eutectic alloy heater elements.

4.22.2
Combination Type Solid-State Reduced Voltage Starter
4.22.2.1
Ratings

The general specifications for the solid-state reduced voltage (SSRV) starter shall be as follows:


SYMBOL 183 \f "Symbol" \s 10 \h
Size
NEMA size 7


SYMBOL 183 \f "Symbol" \s 10 \h
Voltage
480 V + 10%, 3-phase


SYMBOL 183 \f "Symbol" \s 10 \h
Current
Continuous-current rating is 115% of 520 FLA.  Starting current is 300% of FLA for 30 seconds, standard duty.


SYMBOL 183 \f "Symbol" \s 10 \h
Frequency
47-63 Hz


SYMBOL 183 \f "Symbol" \s 10 \h
Temperature
Operating range  0° to 50°C


SYMBOL 183 \f "Symbol" \s 10 \h
Packaging
NEMA Type 3R, vented

4.22.2.2
Components

The SSRV starter shall consist of a power section, printed circuit logic board(s) and a field wiring interface terminal board as specified below.  The SSRV starter shall have a  built-in electronic overload protection.  The SSRV starter is used to reduce starting current and high starting torque.  The starter's load sensing circuit shall also reduce the voltage to lightly loaded motors to save energy.

4.22.2.3
Enclosure

4.22.2.3.1
General


The enclosure shall be a NEMA 3R (outdoor weatherproof). All enclosures shall be constructed of 16 gauge minimum thickness steel of welded construction with gasketed heat sink, ventilation louvers and exterior doors. The approximate dimensions shall be 90"H X 30"W X 21"D.  The structure shall be provided with adequate lifting means and shall be capable of being rolled or lifted into the installation position and bolted to the floor.

4.22.2.3.2
Doors


Inner doors shall include a factory-mounted and wired operator devices. Interlock provisions shall prevent unauthorized opening of the starter exterior door with the switchgear breaker in the on position.  A door switch shall be provided to trip with the breaker in the switchgear.  The door switch shall be capable of being bypassed by a door key.

4.22.2.3.3
Operator Devices


The following door-mounted operator devices shall be provided:


SYMBOL 183 \f "Symbol" \s 10 \h
Start-Stop pushbuttons


SYMBOL 183 \f "Symbol" \s 10 \h
Reset pushbutton


SYMBOL 183 \f "Symbol" \s 10 \h
White pilot light, 120 V (power on)


SYMBOL 183 \f "Symbol" \s 10 \h
Amber pilot light, 120 V (motor on)


SYMBOL 183 \f "Symbol" \s 10 \h
Red pilot light, 120 V (alarm tripped)


SYMBOL 183 \f "Symbol" \s 10 \h
Ammeter, single phase

4.22.2.3.4
Space Heater


A thermostat controlled space heater shall be provided to prevent condensation in the enclosure.  A 120V, single pole, 15A breaker shall be connected to the space heater to be fed 120V power from an outside source.

4.22.2.3
Power System
4.22.2.3.1
General


The power section shall be rated for 450 hp, 480 V, threephase, 60 Hz.  It shall consist of three sets of back-to-back silicon controlled rectifiers (SCR's).

4.22.2.3.2
Silicon Controlled Rectifiers


The power section shall have surge suppressors across the SCR's rated ten percent above rated volts and not less than 660 joules.  They shall be metal oxide varistor (MOV) type.  Resistor/Capacitor snubber networks shall be used to prevent false firing of SCR's due to dv/dt characteristics of the electrical system.  The SCR's shall be rated with peak inverse voltage at least 2.5 times rated line-to-line voltage.  The SCR's shall be protected by an electronic fuse in the logic board.  The SCR's heat sink shall be adequately sized and mounted for dissipating the heat effectively.  The SCR's shall be shunted by a magnetic bypass contactor when the motor approaches full speed and full load.

4.22.2.3.3
Terminations


Power terminations shall consist of pressure type terminals for top or bottom entrance.

4.22.2.3.4
Ground Lugs


Two ground lugs shall be furnished, one for incoming and one for outgoing ground connections.

4.22.2.4
Logic Circuitry
4.22.2.4.1
General


The logic board(s) shall be mounted for easy testing, service and replacement.  Three-phase current sensing is required.  The logic board soldering shall be treated with a conformal protective coating system.  The logic board shall be identical from five through 1000 hp with DIP (Dual Inline Package) switches to set-up for various ampere ratings.

4.22.2.4.2
Connectors


The logic board(s) shall use quick disconnect, plug-in connectors for current transformer inputs, line and load voltage inputs and SCR gate firing output circuits.

4.22.2.4.3
Sensing Circuitry


The logic board shall include, as standard, current and motor slip sensing circuitry that continually monitor motor load and regulate motor voltage to minimize motor kwh energy consumption.

4.22.2.4.4
Customer Interface


All customer interface wiring shall connect to a common barrier terminal strip rated 1000 volts or greater.  The customer interface circuitry shall include relay logic interface capability.  Tripped functions shall be designed to be cleared by interrupting customer control power from the solid state logic board.

4.22.2.4.5
Standard Features


The logic circuitry shall include the following standard features as a minimum:


SYMBOL 183 \f "Symbol" \s 10 \h
Single-phase protection


SYMBOL 183 \f "Symbol" \s 10 \h
Under-voltage protection


SYMBOL 183 \f "Symbol" \s 10 \h
Short circuit "electronic fuse" overcurrent protection (Trip time shall not exceed 1/2 cycle or eight milliseconds.)


SYMBOL 183 \f "Symbol" \s 10 \h
Inverse-time running overcurrent protection


SYMBOL 183 \f "Symbol" \s 10 \h
Heat sink over temperature protection


SYMBOL 183 \f "Symbol" \s 10 \h
Auxiliary trip circuitry


SYMBOL 183 \f "Symbol" \s 10 \h
Gate firing circuit lockout protection on trip


SYMBOL 183 \f "Symbol" \s 10 \h
Fault relay lockout protection


SYMBOL 183 \f "Symbol" \s 10 \h
100% - 130% full-load running current adjustment


SYMBOL 183 \f "Symbol" \s 10 \h
200% - 350% current limit adjustment


SYMBOL 183 \f "Symbol" \s 10 \h
Local and remote control station start-stop capability


SYMBOL 183 \f "Symbol" \s 10 \h
Manual reset


SYMBOL 183 \f "Symbol" \s 10 \h
Dwell time at current limit with ramp continuation after acceleration


SYMBOL 183 \f "Symbol" \s 10 \h
Green run light-emitting diode (LED)


SYMBOL 183 \f "Symbol" \s 10 \h
Red over-current trip LED


SYMBOL 183 \f "Symbol" \s 10 \h
Red phase loss trip LED


SYMBOL 183 \f "Symbol" \s 10 \h
Red auxiliary trip LED


SYMBOL 183 \f "Symbol" \s 10 \h
Minimum voltage adjustment


SYMBOL 183 \f "Symbol" \s 10 \h
Maximum voltage adjustment


SYMBOL 183 \f "Symbol" \s 10 \h
Voltage stability adjustment

4.22.2.4.6
Auxilliary Devices


The auxiliary devices and logic boards, such as voltage ramp, smooth stop, shorted SCR detector and relay output dry contacts shall add to the basic unit inside the original enclosure.  An explanatory cover plate shall be included with the equipment.  The following auxiliary equipment shall be provided:


SYMBOL 183 \f "Symbol" \s 10 \h
Two auxiliary contacts, (DPDT)


SYMBOL 183 \f "Symbol" \s 10 \h
Time delay relay and interposing relays


SYMBOL 183 \f "Symbol" \s 10 \h
200 VA control transformer


SYMBOL 183 \f "Symbol" \s 10 \h
Voltage ramp controller.


SYMBOL 183 \f "Symbol" \s 10 \h
Shorted SCR detector


SYMBOL 183 \f "Symbol" \s 10 \h
Trip relay with 3PDT alarm contacts


SYMBOL 183 \f "Symbol" \s 10 \h
Smooth stop


SYMBOL 183 \f "Symbol" \s 10 \h
Up-to-speed contacts for bypass contactor


SYMBOL 183 \f "Symbol" \s 10 \h
Current transducer, 4-20 mA DC signal output

4.22.2.4.7
Control and Status Signals


The following control and status signal terminals shall be provided as minimum to interface with a customer's remote station:


SYMBOL 183 \f "Symbol" \s 10 \h
Breaker interlock by door switch and trip contact


SYMBOL 183 \f "Symbol" \s 10 \h
Start-stop remote control


SYMBOL 183 \f "Symbol" \s 10 \h
Power-on, motor on and motor trip indications


SYMBOL 183 \f "Symbol" \s 10 \h
Four 20 mA motor current signal

4.22.2.4.8
Cover


A  transparent cover shall be mounted above the logic board to provide (a) an insulating safety barrier and (b) silk-screened with information to aid in starting and set-up of DIP Switches.  Identified holes will be located above adjustment pots so that screwdriver adjustments can be made without removing the transparent cover.

STD SPEC
4.22 - 4

